## BuildingSummary
Building Summary Sit Down Restaurant new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Sit Down Restaurant
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Service
Form |  |  | Time Saver Standards; Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991 for all Form parameters
| Total Floor Area (m2) | 511.15
| Building Shape | Rectangle
| Aspect Ratio | 1
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.28
| East | 0.224
| North | 0
| West | 0.224
| Total | 0.182
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 2 zones plus attic
| Floor to Ceiling Height (m) | 3.048
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 275.72
| Net Dimensions - Total Area (m2) | 225.54
| Wall to Skin Ratio | 0.326
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 569.52
| Net Dimensions - Total Area (m2) | 569.52
| Roof to Skin Ratio | 0.674
| Window Dimensions (m2) |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991
| South | 19.3
| East | 15.44
| North | 0
| West | 15.44
| Total Area (m2) | 50.18
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab-on-grade
| Dimensions - Total Area (m2) | 511.15
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 68.93
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.31
| Thermal diffusivity (m2/s) | 1.84e-07
| Air Barrier System |  | See Benchmark Technical Report
| Infiltration (ACH) | 0.55
HVAC |  |  | 2003 CBECS
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas | Standard 90.1-2004
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 140
| Water Consumption (m3 ) | 1375.88

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Dining | Yes | 1 | 371.75 | 1133.39 | 3.0488 | 169.19 | 47.17 | 1.3935 | 266.7653 | 22.596 | 60.256 | 0 | 0 | 3.8 | 0.9 | 1348.2832 | 0 | 0.51945
Kitchen | Yes | 1 | 139.41 | 425.02 | 3.0487 | 106.53 | 0 | 18.5806 | 7.503 | 12.912 | 376.6 | 1796.92 | 503.4582 | 0 | 0 | 0 | 2831.682 | 0.62979
Attic | No | 1 | 511.15 | 856.26 | 1.6752 | 0 | 0 | [10 empty] | 1
Total Conditioned Zones |  |  | 511.16 | 1558.41 |  | 275.72 | 47.17 |  | 274.2683
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.262 | 0.262 | 0.262 | 0.391 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.39 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor | Mass floor
| Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_COOLC DXCOIL | 72.8324 | 74.9662 | 78.0873 | 75.4899 | 52.5042 | 76.3797 | 44.1839 | 75.1103 | 57.4178 | 55.7876 | 73.9271 | 55.5513 | 74.2077 | 52.7026 | 70.3096 | 44.1839
| PSZ-AC_2:2_COOLC DXCOIL | 70.3174 | 70.3174 | 53.753 | 70.3174 | 46.8744 | 46.8744 | 46.8744 | 70.3174 | 46.8744 | 46.8744 | 70.3174 | 46.8744 | 70.3174 | 46.8744 | 54.9558 | 46.8744
Heating (kW)
| PSZ-AC_1:1_HEATC | 34.0657 | 46.2889 | 40.6797 | 50.2826 | 34.4877 | 43.8319 | 35.6392 | 55.6922 | 50.7449 | 44.6342 | 64.0351 | 58.6056 | 69.4658 | 67.4396 | 67.3685 | 78.6456
| PSZ-AC_2:2_HEATC | 32.8893 | 43.4184 | 36.6319 | 46.8373 | 34.2063 | 39.6001 | 37.8093 | 52.1383 | 41.4268 | 45.0897 | 60.9083 | 49.4517 | 65.824 | 59.9816 | 67.3759 | 83.4344
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_COOLC DXCOIL | 3.12 | 3.12 | 3.12 | 3.12 | 3.38 | 3.13 | 3.47 | 3.12 | 3.47 | 3.32 | 3.12 | 3.47 | 3.12 | 3.47 | 3.12 | 3.47
| PSZ-AC_2:2_COOLC DXCOIL | 3.12 | 3.12 | 3.35 | 3.12 | 3.47 | 3.47 | 3.47 | 3.12 | 3.47 | 3.47 | 3.12 | 3.47 | 3.12 | 3.47 | 3.34 | 3.47
Heating Efficiency (%)
| PSZ-AC_1:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| DINING EXHAUST FAN | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
| KITCHEN EXHAUST FAN | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| PSZ-AC_1:1_FAN | 2.93 | 3.02 | 3.14 | 3.04 | 2.85 | 3.13 | 2.67 | 3.02 | 3.47 | 2.8 | 2.98 | 3.36 | 2.99 | 3.18 | 2.83 | 2.67
| PSZ-AC_2:2_FAN | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.076283 | 0.10718 | 0.095028 | 0.10341 | 0.1238 | 0.093616 | 0.14438 | 0.066407 | 0.037501 | 0.07223 | 0.052095 | 0.037519 | 0.052051 | 0.067405 | 0.050674 | 0.086071
| Total Cost ($/m2) | 66.62 | 85.17 | 72.36 | 74.05 | 76.6 | 66.85 | 86.47 | 45.68 | 24.65 | 43.74 | 33.8 | 23.91 | 33.49 | 41.86 | 30.94 | 51.52
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011469 | 0.0081953 | 0.0085951 | 0.010702 | 0.0084089 | 0.0081438 | 0.0084195 | 0.01003 | 0.0071764 | 0.0083053 | 0.008814 | 0.0071655 | 0.0079431 | 0.0086483 | 0.0079373 | 0.0041839
| Total Cost ($/m2) | 29.99 | 24.71 | 24.87 | 36.37 | 24.6 | 25.35 | 28.94 | 39.69 | 25.62 | 32.8 | 39.01 | 28.56 | 38.87 | 39.88 | 43.14 | 28.62
Total Utility Costs
| Cost Intensity ($/m2) | 96.62 | 109.88 | 97.23 | 110.42 | 101.19 | 92.19 | 115.41 | 85.37 | 50.27 | 76.54 | 72.81 | 52.47 | 72.36 | 81.74 | 74.08 | 80.14
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 136575 | 97047.2222 | 79666.6667 | 57555.5556 | 9702.7778 | 56069.4444 | 2344.4444 | 43891.6667 | 24863.8889 | 4755.5556 | 24652.7778 | 15858.3333 | 21683.3333 | 9272.2222 | 6802.7778 | 2055.5556
| Interior Lighting | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333 | 51558.3333
| Exterior Lighting | 6483.3333 | 6480.5556 | 6480.5556 | 6480.5556 | 6475 | 6472.2222 | 6477.7778 | 6472.2222 | 6475 | 6461.1111 | 6475 | 6469.4444 | 6469.4444 | 6466.6667 | 6463.8889 | 6425
| Interior Equipment | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200 | 181200
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 51855.5556 | 51397.2222 | 52050 | 50952.7778 | 48925 | 51588.8889 | 46416.6667 | 50427.7778 | 53891.6667 | 47544.4444 | 49880.5556 | 52638.8889 | 50191.6667 | 51158.3333 | 48544.4444 | 47641.6667
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 18744.4444 | 18527.7778 | 18269.4444 | 18275 | 18408.3333 | 18094.4444 | 18136.1111 | 18041.6667 | 18050 | 17991.6667 | 17925 | 17955.5556 | 17758.3333 | 17786.1111 | 17544.4444 | 17105.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 446419.4444 | 406211.1111 | 389225 | 366025 | 316269.4444 | 364986.1111 | 306130.5556 | 351588.8889 | 336038.8889 | 309511.1111 | 331691.6667 | 325680.5556 | 328861.1111 | 317441.6667 | 312116.6667 | 305986.1111
Gas (MJ)
| Heating | 14120 | 187430 | 143250 | 353780 | 117260 | 233440 | 353600 | 615840 | 422180 | 599240 | 834500 | 610830 | 1055670 | 908140 | 1302820 | 1985660
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410 | 1201410
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 121280 | 152320 | 134470 | 182230 | 176430 | 155960 | 202030 | 205750 | 201280 | 217980 | 226380 | 225310 | 244220 | 247460 | 273640 | 309230
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1336810 | 1541160 | 1479130 | 1737420 | 1495090 | 1590810 | 1757040 | 2023000 | 1824880 | 2018640 | 2262290 | 2037550 | 2501300 | 2357010 | 2777870 | 3496310
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2943920 | 3003530 | 2880330 | 3055110 | 2633660 | 2904760 | 2859110 | 3288720 | 3034620 | 3132880 | 3456370 | 3210000 | 3685190 | 3499800 | 3901480 | 4597860
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 961.8899 | 683.498 | 561.0877 | 405.3605 | 68.3361 | 394.8939 | 16.5118 | 309.1265 | 175.1149 | 33.4931 | 173.6281 | 111.6893 | 152.7145 | 65.3037 | 47.9116 | 14.4772
| Interior Lighting (elec) | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224 | 363.1224
| Exterior Lighting (elec) | 45.6617 | 45.6422 | 45.6422 | 45.6422 | 45.6031 | 45.5835 | 45.6226 | 45.5835 | 45.6031 | 45.5052 | 45.6031 | 45.5639 | 45.5639 | 45.5444 | 45.5248 | 45.2509
| Interior Equipment (elec) | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812 | 1276.1812
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 365.2157 | 361.9877 | 366.5852 | 358.8575 | 344.576 | 363.3376 | 326.9099 | 355.1599 | 379.5559 | 334.8528 | 351.3059 | 370.7327 | 353.497 | 360.3052 | 341.8957 | 335.5375
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 132.016 | 130.4901 | 128.6706 | 128.7098 | 129.6488 | 127.4381 | 127.7316 | 127.0664 | 127.1251 | 126.7143 | 126.2447 | 126.4599 | 125.0709 | 125.2666 | 123.5645 | 120.4734
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3144.1064 | 2860.9215 | 2741.2892 | 2577.893 | 2227.4675 | 2570.5762 | 2156.0599 | 2476.2203 | 2366.7025 | 2179.8689 | 2336.0853 | 2293.7494 | 2316.1499 | 2235.7234 | 2198.2197 | 2155.0426
Gas (MJ/m2)
| Heating (gas) | 27.624 | 366.683 | 280.2504 | 692.1256 | 229.4043 | 456.6957 | 691.7735 | 1204.8127 | 825.9415 | 1172.3369 | 1632.5932 | 1195.0112 | 2065.2842 | 1776.6605 | 2548.8017 | 3884.6914
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059 | 2350.4059
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 237.2689 | 297.9947 | 263.0735 | 356.5098 | 345.1629 | 305.1159 | 395.246 | 402.5237 | 393.7787 | 426.4502 | 442.8837 | 440.7904 | 477.7854 | 484.124 | 535.3419 | 604.9692
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2615.2988 | 3015.0836 | 2893.7298 | 3399.0414 | 2924.9535 | 3112.2175 | 3437.4254 | 3957.7423 | 3570.1457 | 3949.2126 | 4425.8828 | 3986.2076 | 4893.4755 | 4611.1905 | 5434.5495 | 6840.0861
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 5759.4053 | 5876.0247 | 5634.9995 | 5976.9344 | 5152.421 | 5682.7937 | 5593.4853 | 6433.9626 | 5936.8483 | 6129.0815 | 6761.9485 | 6279.957 | 7209.6058 | 6846.9138 | 7632.7497 | 8995.1286
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 69.9425 | 66.6222 | 51.5331 | 47.4185 | 55.3744 | 44.0268 | 43.2978 | 43.6427 | 44.1474 | 43.4206 | 43.5872 | 44.0214 | 43.6541 | 43.82 | 43.3768 | 44.2766
| Feb | 70.6944 | 62.002 | 55.976 | 48.9047 | 54.4971 | 46.1387 | 45.7044 | 43.6523 | 44.8577 | 43.4186 | 43.5964 | 44.0277 | 43.5839 | 43.8502 | 43.4166 | 43.206
| Mar | 71.1675 | 68.0974 | 64.1524 | 56.1948 | 53.1442 | 52.9 | 43.3026 | 58.057 | 46.5726 | 43.6319 | 45.3419 | 49.8483 | 43.6517 | 46.0106 | 43.4321 | 43.2222
| Apr | 73.8918 | 71.9689 | 66.8781 | 64.7722 | 56.646 | 64.7537 | 47.5573 | 58.0043 | 56.4182 | 45.2811 | 46.4222 | 52.0979 | 52.6643 | 44.8831 | 43.4515 | 43.1738
| May | 76.418 | 78.0718 | 76.3943 | 72.9969 | 55.2384 | 69.9577 | 51.4395 | 68.8694 | 61.1263 | 51.8346 | 67.6747 | 57.9542 | 73.6105 | 54.5185 | 50.631 | 44.8088
| Jun | 81.1868 | 78.2061 | 87.7706 | 75.0329 | 55.275 | 81.0915 | 54.0774 | 81.0327 | 64.4925 | 56.0002 | 77.6135 | 63.4262 | 75.5845 | 63.5292 | 65.0363 | 55.8285
| Jul | 79.0648 | 84.0963 | 87.4579 | 80.2232 | 58.3405 | 79.258 | 59.2387 | 83.1409 | 66.0313 | 59.678 | 78.5916 | 64.7777 | 78.6364 | 63.4939 | 69.6705 | 58.1376
| Aug | 79.3341 | 81.3959 | 86.5614 | 77.168 | 63.037 | 78.0868 | 56.6434 | 82.6988 | 65.9401 | 59.4591 | 79.1532 | 65.1298 | 77.2606 | 62.3347 | 67.6206 | 55.1545
| Sep | 76.939 | 79.7655 | 78.9902 | 72.1515 | 62.1724 | 74.0492 | 59.5177 | 69.7451 | 60.8694 | 65.3238 | 68.3134 | 60.4473 | 63.7906 | 59.5803 | 55.4007 | 43.2739
| Oct | 76.4832 | 74.2332 | 67.2631 | 66.004 | 59.5054 | 64.685 | 51.0687 | 65.4612 | 56.0675 | 46.6244 | 57.4974 | 55.8891 | 56.2586 | 50.3532 | 51.7651 | 43.2608
| Nov | 73.0736 | 71.0688 | 61.2917 | 54.168 | 55.8227 | 47.8791 | 43.321 | 59.9493 | 44.1579 | 43.457 | 56.9847 | 47.2943 | 43.6374 | 43.8305 | 43.4686 | 43.213
| Dec | 69.3262 | 70.498 | 50.2192 | 49.3074 | 55.9237 | 47.8827 | 43.2946 | 43.6455 | 44.1435 | 43.4212 | 43.595 | 44.0231 | 43.623 | 43.8177 | 43.4306 | 44.3925
Time of Peak Electrical Demand
| Jan | 06-JAN-12:09 | 03-JAN-12:09 | 28-JAN-14:00 | 23-JAN-18:19 | 26-JAN-12:00 | 18-JAN-13:00 | 05-JAN-19:10 | 09-JAN-19:10 | 26-JAN-19:10 | 28-JAN-19:10 | 28-JAN-19:30 | 21-JAN-19:10 | 28-JAN-19:19 | 14-JAN-19:10 | 21-JAN-19:10 | 03-JAN-11:09
| Feb | 23-FEB-12:09 | 23-FEB-13:00 | 28-FEB-18:19 | 18-FEB-13:00 | 13-FEB-11:00 | 08-FEB-13:00 | 14-FEB-12:00 | 15-FEB-19:10 | 14-FEB-14:00 | 22-FEB-19:10 | 18-FEB-19:10 | 25-FEB-19:10 | 27-FEB-19:10 | 02-FEB-19:10 | 23-FEB-19:10 | 27-FEB-19:10
| Mar | 14-MAR-10:39 | 25-MAR-18:10 | 17-MAR-17:19 | 28-MAR-17:19 | 04-MAR-11:00 | 31-MAR-16:10 | 30-MAR-18:30 | 09-MAR-13:00 | 02-MAR-13:00 | 29-MAR-16:10 | 31-MAR-14:00 | 30-MAR-17:10 | 25-MAR-18:00 | 30-MAR-17:10 | 30-MAR-18:30 | 09-MAR-19:10
| Apr | 01-APR-18:40 | 29-APR-18:10 | 01-APR-17:10 | 15-APR-18:10 | 11-APR-17:10 | 21-APR-17:10 | 29-APR-12:00 | 04-APR-17:10 | 21-APR-17:10 | 29-APR-17:10 | 07-APR-13:00 | 24-APR-11:00 | 01-APR-17:10 | 06-APR-17:10 | 08-APR-18:49 | 05-APR-19:49
| May | 23-MAY-10:00 | 18-MAY-17:30 | 27-MAY-17:10 | 31-MAY-17:00 | 30-MAY-11:09 | 31-MAY-17:10 | 17-MAY-13:00 | 15-MAY-17:10 | 31-MAY-17:10 | 05-MAY-16:10 | 30-MAY-17:10 | 23-MAY-17:10 | 27-MAY-17:19 | 16-MAY-17:10 | 31-MAY-17:10 | 30-MAY-17:10
| Jun | 27-JUN-17:00 | 13-JUN-17:19 | 28-JUN-17:49 | 08-JUN-18:00 | 28-JUN-12:00 | 27-JUN-16:19 | 16-JUN-11:09 | 30-JUN-17:19 | 20-JUN-17:10 | 28-JUN-12:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-17:19 | 30-JUN-12:00 | 14-JUN-17:19 | 20-JUN-17:00
| Jul | 13-JUL-11:00 | 18-JUL-11:00 | 19-JUL-17:19 | 03-JUL-17:00 | 29-JUL-10:39 | 24-JUL-16:19 | 02-JUL-12:00 | 25-JUL-11:00 | 31-JUL-17:19 | 31-JUL-17:19 | 14-JUL-10:00 | 19-JUL-12:00 | 13-JUL-17:00 | 21-JUL-17:19 | 06-JUL-17:00 | 29-JUL-18:10
| Aug | 21-AUG-17:00 | 31-AUG-10:00 | 01-AUG-17:19 | 17-AUG-11:00 | 08-AUG-10:39 | 04-AUG-16:19 | 15-AUG-11:00 | 09-AUG-17:49 | 01-AUG-17:19 | 18-AUG-17:40 | 04-AUG-17:19 | 30-AUG-11:00 | 25-AUG-17:19 | 09-AUG-17:10 | 11-AUG-17:49 | 15-AUG-17:10
| Sep | 06-SEP-11:00 | 16-SEP-18:30 | 12-SEP-17:19 | 01-SEP-17:49 | 24-SEP-10:00 | 01-SEP-14:00 | 28-SEP-16:10 | 05-SEP-11:00 | 02-SEP-17:10 | 02-SEP-16:10 | 06-SEP-11:09 | 01-SEP-17:10 | 14-SEP-11:00 | 01-SEP-17:10 | 07-SEP-14:00 | 20-SEP-18:00
| Oct | 06-OCT-18:10 | 30-OCT-18:19 | 13-OCT-17:00 | 21-OCT-18:10 | 19-OCT-10:00 | 06-OCT-12:00 | 30-OCT-12:00 | 03-OCT-11:09 | 11-OCT-16:19 | 17-OCT-17:19 | 31-OCT-12:00 | 05-OCT-12:00 | 08-OCT-14:00 | 06-OCT-17:10 | 07-OCT-14:00 | 02-OCT-18:19
| Nov | 01-NOV-18:10 | 27-NOV-18:19 | 13-NOV-13:00 | 22-NOV-12:00 | 20-NOV-12:00 | 10-NOV-12:00 | 16-NOV-19:10 | 04-NOV-11:00 | 15-NOV-19:00 | 04-NOV-19:10 | 02-NOV-12:09 | 10-NOV-13:00 | 02-NOV-19:10 | 20-NOV-19:10 | 08-NOV-19:10 | 13-NOV-19:10
| Dec | 15-DEC-18:10 | 02-DEC-19:10 | 09-DEC-15:00 | 13-DEC-13:00 | 19-DEC-12:00 | 05-DEC-13:00 | 14-DEC-19:10 | 02-DEC-19:10 | 07-DEC-19:10 | 23-DEC-19:19 | 11-DEC-19:10 | 21-DEC-19:10 | 05-DEC-18:30 | 02-DEC-19:10 | 04-DEC-18:30 | 18-DEC-11:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88
| Total Building | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88 | 1375.88
Emissions
| Carbon Equivalent (kg) | 146536.797 | 163287.9016 | 144169.9206 | 144079.2476 | 63921.5535 | 151787.338 | 67460.4861 | 131358.6039 | 170179.0965 | 58944.5338 | 217635.6421 | 169782.8649 | 157671.7679 | 158508.7112 | 156927.4933 | 149148.5382
| CO2 (kg) | 353142.1848 | 420294.2651 | 353380.5839 | 346414.4165 | 176573.899 | 374446.7628 | 187058.4326 | 318166.3402 | 414932.2606 | 158721.5255 | 525884.0674 | 416153.1747 | 389827.8475 | 392613.7183 | 391023.6076 | 397841.1399
| NOX (kg) | 563.2033 | 519.7955 | 536.9851 | 576.3124 | 155.1654 | 553.3917 | 164.8487 | 521.0976 | 647.5167 | 181.5234 | 849.9661 | 640.2775 | 591.8703 | 590.4313 | 580.8397 | 435.5856
| SO2 (kg) | 1911.2127 | 1938.0455 | 1565.545 | 1285.2093 | 920.7034 | 2008.1416 | 891.2759 | 1283.9864 | 1467.9081 | 239.7688 | 2235.9344 | 1422.7329 | 776.8336 | 848.2417 | 737.3875 | 1558.5292
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0089 | 0.0056 | 0.0044 | 0.0049 | 0.0006 | 0.0039 | 0.0006 | 0.0054 | 0.0059 | 0.0012 | 0.007 | 0.0058 | 0.0059 | 0.0061 | 0.0057 | 0.0057
| Water for Electricity (m3) | 236.4943 | 660.955 | 11561.7 | 2285.31 | 5552.96 | 10013 | 5374.98 | 79.8242 | 1525.89 | 3162.22 | 514.5978 | 1478.86 | 510.2073 | 20108.1 | 484.2288 | 312.62

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2943.92 | 5759.37 | 5759.37
Net Site Energy | 2943.92 | 5759.37 | 5759.37
Total Source Energy | 6790.58 | 13284.83 | 13284.83
Net Source Energy | 6790.58 | 13284.83 | 13284.83
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14.12 | 0 | 0 | 0 | 0
Cooling | 491.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 186.68 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 121.28 | 0 | 0 | 0 | 1375.88
Refrigeration | 67.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1607.11 | 1336.81 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 72832.38 | 49240.75 | 23591.63 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70317.36 | 47540.39 | 22776.97 | 0.68 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 34065.69 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 32889.34 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.93 | 3207.56 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26991.6676 | 42.2628 | 139.9051 | 0 | 0.0007 | 17311.19 | 11121.6216
February | 24545.358 | 38.5753 | 128.3497 | 0 | 0.0006 | 15881.5257 | 10127.9628
March | 27787.6462 | 43.8291 | 146.55 | 0 | 0.0007 | 18133.7161 | 11481.6673
April | 28363.27 | 45.1559 | 152.8821 | 0 | 0.0007 | 18917.628 | 11761.4753
May | 31257.7689 | 50.1497 | 171.519 | 0 | 0.0008 | 21224.1196 | 13000.3852
June | 31261.2731 | 50.3445 | 173.0273 | 0 | 0.0008 | 21410.9294 | 13020.7994
July | 33260.1302 | 53.7271 | 185.3775 | 0 | 0.0009 | 22939.3266 | 13869.7354
August | 33012.1816 | 53.2771 | 183.6068 | 0 | 0.0008 | 22720.1773 | 13761.3907
September | 31446.4493 | 50.6523 | 174.1275 | 0 | 0.0008 | 21547.0843 | 13098.8868
October | 30708.1712 | 49.1526 | 167.5953 | 0 | 0.0008 | 20738.4909 | 12760.2444
November | 27768.0435 | 44.0735 | 148.6132 | 0 | 0.0007 | 18389.2766 | 11501.1503
December | 26740.2254 | 42.0034 | 139.6591 | 0 | 0.0006 | 17280.8815 | 11031.4779
Annual Sum or Average | 353142.1848 | 563.2033 | 1911.2127 | 0 | 0.0089 | 236494.346 | 146536.797
Minimum of Months | 24545.358 | 38.5753 | 128.3497 | 0 | 0.0006 | 15881.5257 | 10127.9628
Maximum of Months | 33260.1302 | 53.7271 | 185.3775 | 0 | 0.0009 | 22939.3266 | 13869.7354
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 117639000000 | 69942.463 | 06-JAN-12:09 | 9181.105 | 24042.957 | 6639.075 | 0 | 27758.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2320.789 | 0 | 0
February | 107924000000 | 70694.401 | 23-FEB-12:09 | 9181.105 | 24042.957 | 6639.075 | 0 | 28500.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2330.3 | 0 | 0
March | 123229000000 | 71167.469 | 14-MAR-10:39 | 9181.105 | 24042.957 | 6639.075 | 0 | 28372.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.837 | 0 | 0
April | 128556000000 | 73891.811 | 01-APR-18:40 | 9181.105 | 24042.957 | 6639.075 | 0 | 30270.777 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2274.404 | 0 | 0
May | 144230000000 | 76417.982 | 23-MAY-10:00 | 9181.105 | 24042.957 | 6639.075 | 0 | 33623.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.782 | 0 | 0
June | 145499000000 | 81186.811 | 27-JUN-17:00 | 9181.105 | 24042.957 | 6639.075 | 0 | 39185.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2138.116 | 0 | 0
July | 155885000000 | 79064.833 | 13-JUL-11:00 | 9181.105 | 24042.957 | 6639.075 | 0 | 37063.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2138.057 | 0 | 0
August | 154396000000 | 79334.086 | 21-AUG-17:00 | 9181.105 | 24042.957 | 6639.075 | 0 | 37333.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.644 | 0 | 0
September | 146424000000 | 76939.016 | 06-SEP-11:00 | 9181.105 | 24042.957 | 6639.075 | 0 | 34938.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.229 | 0 | 0
October | 140930000000 | 76483.216 | 06-OCT-18:10 | 9181.105 | 24042.957 | 6639.075 | 0 | 32999.296 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.29 | 0 | 0
November | 124965000000 | 73073.648 | 01-NOV-18:10 | 9181.105 | 24042.957 | 6639.075 | 0 | 29590.137 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2136.882 | 0 | 0
December | 117433000000 | 69326.17 | 15-DEC-18:10 | 9181.105 | 24042.957 | 6639.075 | 0 | 25865.186 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2114.354 | 0 | 0
Annual Sum or Average | 1607110000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 107924000000 | 69326.17 |  | 9181.105 | 24042.957 | 6639.075 | 0 | 25865.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2114.354 | 0 | 0
Maximum of Months | 155885000000 | 81186.811 |  | 9181.105 | 24042.957 | 6639.075 | 0 | 39185.558 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.837 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34054.25 | 15331.42 | 0 | 49385.67
Cost per Total Building Area ($/m2) | 66.62 | 29.99 | 0 | 96.62
Cost per Net Conditioned Building Area ($/m2) | 66.62 | 29.99 | 0 | 96.62

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3003.53 | 5875.98 | 5875.98
Net Site Energy | 3003.53 | 5875.98 | 5875.98
Total Source Energy | 1682.95 | 3292.46 | 3292.46
Net Source Energy | 1682.95 | 3292.46 | 3292.46
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 187.43 | 0 | 0 | 0 | 0
Cooling | 349.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.33 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 185.03 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 152.32 | 0 | 0 | 0 | 1375.88
Refrigeration | 66.7 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1462.36 | 1541.16 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74966.21 | 50683.4 | 24282.81 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70317.36 | 47540.39 | 22776.97 | 0.68 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 46288.95 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 43418.44 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.02 | 3301.54 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32328.8915 | 38.9724 | 134.9263 | 0 | 0.0004 | 46010.135 | 12429.8439
February | 28716.4137 | 34.4784 | 117.9013 | 0 | 0.0003 | 40203.7668 | 11022.9856
March | 31510.6684 | 38.5195 | 138.9836 | 0 | 0.0004 | 47396.8549 | 12184.0232
April | 32678.0262 | 40.4991 | 151.8717 | 0 | 0.0004 | 51795.0787 | 12706.6249
May | 37244.3197 | 46.5212 | 178.1761 | 0 | 0.0005 | 60767.9831 | 14528.9727
June | 38922.0742 | 48.8516 | 189.4908 | 0 | 0.0005 | 64628.1514 | 15213.7277
July | 42119.9659 | 52.9966 | 206.8983 | 0 | 0.0006 | 70565.8253 | 16480.63
August | 41366.5117 | 52.001 | 202.5305 | 0 | 0.0006 | 69075.902 | 16179.6839
September | 37453.0072 | 46.9147 | 181.0356 | 0 | 0.0005 | 61743.911 | 14627.5103
October | 34877.1472 | 43.3428 | 163.7484 | 0 | 0.0005 | 55846.2015 | 13576.9812
November | 31242.3279 | 38.3695 | 140.2933 | 0 | 0.0004 | 47844.4668 | 12103.2117
December | 31834.9115 | 38.3287 | 132.1897 | 0 | 0.0004 | 45076.6759 | 12233.7065
Annual Sum or Average | 420294.2651 | 519.7955 | 1938.0455 | 0 | 0.0056 | 660954.9523 | 163287.9016
Minimum of Months | 28716.4137 | 34.4784 | 117.9013 | 0 | 0.0003 | 40203.7668 | 11022.9856
Maximum of Months | 42119.9659 | 52.9966 | 206.8983 | 0 | 0.0006 | 70565.8253 | 16480.63
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 101798000000 | 66622.175 | 03-JAN-12:09 | 9181.105 | 24042.957 | 6733.05 | 0 | 24356.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2308.403 | 0 | 0
February | 88950900000 | 62002.009 | 23-FEB-13:00 | 9181.105 | 24042.957 | 6733.05 | 0 | 19910.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2134.732 | 0 | 0
March | 104866000000 | 68097.354 | 25-MAR-18:10 | 9181.105 | 24042.957 | 6733.05 | 0 | 25869.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2270.872 | 0 | 0
April | 114597000000 | 71968.865 | 29-APR-18:10 | 9181.105 | 24042.957 | 6733.05 | 0 | 29737.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2274.177 | 0 | 0
May | 134449000000 | 78071.791 | 18-MAY-17:30 | 9181.105 | 24042.957 | 6733.05 | 0 | 35977.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.642 | 0 | 0
June | 142990000000 | 78206.089 | 13-JUN-17:19 | 9181.105 | 24042.957 | 6733.05 | 0 | 36122.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.948 | 0 | 0
July | 156127000000 | 84096.298 | 18-JUL-11:00 | 9181.105 | 24042.957 | 6733.05 | 0 | 42000.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2138.617 | 0 | 0
August | 152831000000 | 81395.869 | 31-AUG-10:00 | 9181.105 | 24042.957 | 6733.05 | 0 | 38507.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.67 | 0 | 0
September | 136609000000 | 79765.482 | 16-SEP-18:30 | 9181.105 | 24042.957 | 6733.05 | 0 | 35993.548 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2331.329 | 0 | 0
October | 123560000000 | 74233.242 | 30-OCT-18:19 | 9181.105 | 24042.957 | 6733.05 | 0 | 30655.248 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.39 | 0 | 0
November | 105856000000 | 71068.755 | 27-NOV-18:19 | 9181.105 | 24042.957 | 6733.05 | 0 | 27490.967 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.183 | 0 | 0
December | 99732200000 | 70497.996 | 02-DEC-19:10 | 9181.105 | 24042.957 | 6733.05 | 0 | 26726.518 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2330.874 | 0 | 0
Annual Sum or Average | 1462360000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 88950900000 | 62002.009 |  | 9181.105 | 24042.957 | 6733.05 | 0 | 19910.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.948 | 0 | 0
Maximum of Months | 156127000000 | 84096.298 |  | 9181.105 | 24042.957 | 6733.05 | 0 | 42000.569 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.67 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43536.7 | 12630.25 | 0 | 56166.94
Cost per Total Building Area ($/m2) | 85.17 | 24.71 | 0 | 109.88
Cost per Net Conditioned Building Area ($/m2) | 85.17 | 24.71 | 0 | 109.88

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2880.33 | 5634.97 | 5634.97
Net Site Energy | 2880.33 | 5634.97 | 5634.97
Total Source Energy | 6047.23 | 11830.55 | 11830.55
Net Source Energy | 6047.23 | 11830.55 | 11830.55
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 143.25 | 0 | 0 | 0 | 0
Cooling | 286.8 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.33 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 187.38 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 134.47 | 0 | 0 | 0 | 1375.88
Refrigeration | 65.77 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1401.21 | 1479.13 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 6.49 | 0.25 | 0.25 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 6.49 | 0.25 | 0.25
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 78087.3 | 52793.51 | 25293.79 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53752.99 | 40401.14 | 13351.85 | 0.75 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 40679.69 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 36631.93 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.14 | 3438.99 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26729.5261 | 38.9022 | 106.0103 | 0 | 0.0003 | 782788.1351 | 10731.5104
February | 24082.9555 | 35.1295 | 96.0861 | 0 | 0.0003 | 709512.3597 | 9676.9495
March | 27068.3629 | 40.5204 | 115.4927 | 0 | 0.0003 | 852884.6349 | 10981.3137
April | 27462.4038 | 41.7186 | 121.5745 | 0 | 0.0003 | 897836.6932 | 11202.6855
May | 30266.0552 | 46.554 | 138.1555 | 0 | 0.0004 | 1020320 | 12404.6553
June | 33135.3369 | 51.6667 | 156.3114 | 0 | 0.0004 | 1154450 | 13651.3517
July | 35862.5215 | 56.1723 | 171.0085 | 0 | 0.0005 | 1263020 | 14800.5265
August | 35131.1993 | 54.9188 | 166.7396 | 0 | 0.0005 | 1231480 | 14487.7832
September | 32031.0834 | 49.7664 | 149.811 | 0 | 0.0004 | 1106430 | 13178.363
October | 28795.0469 | 43.9468 | 128.948 | 0 | 0.0004 | 952302.6518 | 11766.911
November | 25790.205 | 38.5201 | 109.4102 | 0 | 0.0003 | 807960.9619 | 10453.9873
December | 27025.8874 | 39.1693 | 105.9974 | 0 | 0.0003 | 782680.9856 | 10833.8836
Annual Sum or Average | 353380.5839 | 536.9851 | 1565.545 | 0 | 0.0044 | 11561700 | 144169.9206
Minimum of Months | 24082.9555 | 35.1295 | 96.0861 | 0 | 0.0003 | 709512.3597 | 9676.9495
Maximum of Months | 35862.5215 | 56.1723 | 171.0085 | 0 | 0.0005 | 1263020 | 14800.5265
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94869400000 | 51533.069 | 28-JAN-14:00 | 8160.982 | 24042.957 | 6870.503 | 0 | 10383.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2075.026 | 0 | 0
February | 85988800000 | 55976.013 | 28-FEB-18:19 | 9181.105 | 24042.957 | 6870.503 | 0 | 12380.171 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2017.784 | 0 | 0
March | 103365000000 | 64152.43 | 17-MAR-17:19 | 9181.105 | 24042.957 | 6870.503 | 0 | 22028.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2029.813 | 0 | 0
April | 108813000000 | 66878.111 | 01-APR-17:10 | 9181.105 | 24042.957 | 6870.503 | 0 | 24750.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2032.576 | 0 | 0
May | 123657000000 | 76394.335 | 27-MAY-17:10 | 9181.105 | 24042.957 | 6870.503 | 0 | 34274.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2025.201 | 0 | 0
June | 139913000000 | 87770.563 | 28-JUN-17:49 | 9181.105 | 24042.957 | 6870.503 | 0 | 45623.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2052.226 | 0 | 0
July | 153070000000 | 87457.916 | 19-JUL-17:19 | 9181.105 | 24042.957 | 6870.503 | 0 | 45297.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2065.885 | 0 | 0
August | 149248000000 | 86561.388 | 01-AUG-17:19 | 9181.105 | 24042.957 | 6870.503 | 0 | 44415.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2051.21 | 0 | 0
September | 134093000000 | 78990.227 | 12-SEP-17:19 | 9181.105 | 24042.957 | 6870.503 | 0 | 36842.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2053.359 | 0 | 0
October | 115414000000 | 67263.076 | 13-OCT-17:00 | 9181.105 | 24042.957 | 6870.503 | 0 | 23631.817 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2053.201 | 0 | 0
November | 97920200000 | 61291.681 | 13-NOV-13:00 | 9181.105 | 24042.957 | 6870.503 | 0 | 19094.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2102.778 | 0 | 0
December | 94856400000 | 50219.245 | 09-DEC-15:00 | 8160.982 | 24042.957 | 6870.503 | 0 | 9080.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2064.261 | 0 | 0
Annual Sum or Average | 1401210000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 85988800000 | 50219.245 |  | 8160.982 | 24042.957 | 6870.503 | 0 | 9080.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017.784 | 0 | 0
Maximum of Months | 153070000000 | 87770.563 |  | 9181.105 | 24042.957 | 6870.503 | 0 | 45623.771 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2102.778 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 36987.14 | 12713.3 | 0 | 49700.44
Cost per Total Building Area ($/m2) | 72.36 | 24.87 | 0 | 97.23
Cost per Net Conditioned Building Area ($/m2) | 72.36 | 24.87 | 0 | 97.23

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3055.11 | 5976.9 | 5976.9
Net Site Energy | 3055.11 | 5976.9 | 5976.9
Total Source Energy | 6329.96 | 12383.69 | 12383.69
Net Source Energy | 6329.96 | 12383.69 | 12383.69
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 353.78 | 0 | 0 | 0 | 0
Cooling | 207.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.33 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 183.43 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 182.23 | 0 | 0 | 0 | 1375.88
Refrigeration | 65.79 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1317.69 | 1737.42 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75489.87 | 51037.43 | 24452.44 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70317.36 | 47540.39 | 22776.97 | 0.68 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 50282.64 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 46837.31 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.04 | 3324.6 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29302.2273 | 45.2948 | 91.7812 | 0 | 0.0004 | 163159.6782 | 11868.2867
February | 25841.3021 | 40.4592 | 83.4616 | 0 | 0.0003 | 148377.2623 | 10513.9981
March | 27128.7903 | 43.8207 | 94.2165 | 0 | 0.0004 | 167516.0529 | 11162.114
April | 26556.545 | 44.1968 | 98.6041 | 0 | 0.0004 | 175333.9106 | 11046.7652
May | 29103.4638 | 49.8682 | 115.084 | 0 | 0.0004 | 204655.0727 | 12238.5244
June | 30530.5903 | 53.0015 | 124.0997 | 0 | 0.0005 | 220695.7144 | 12902.1923
July | 33230.8761 | 58.0793 | 136.9876 | 0 | 0.0005 | 243619.4798 | 14079.3482
August | 32731.0693 | 57.1146 | 134.4807 | 0 | 0.0005 | 239160.228 | 13859.1762
September | 30022.6807 | 52.0356 | 121.6226 | 0 | 0.0005 | 216289.571 | 12679.7777
October | 27193.4666 | 45.58 | 102.5535 | 0 | 0.0004 | 182360.4928 | 11341.5581
November | 26222.6243 | 42.1852 | 90.2274 | 0 | 0.0003 | 160421.1819 | 10773.4084
December | 28550.7807 | 44.6765 | 92.0905 | 0 | 0.0004 | 163717.359 | 11614.0984
Annual Sum or Average | 346414.4165 | 576.3124 | 1285.2093 | 0 | 0.0049 | 2285310 | 144079.2476
Minimum of Months | 25841.3021 | 40.4592 | 83.4616 | 0 | 0.0003 | 148377.2623 | 10513.9981
Maximum of Months | 33230.8761 | 58.0793 | 136.9876 | 0 | 0.0005 | 243619.4798 | 14079.3482
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94076300000 | 47418.547 | 23-JAN-18:19 | 9181.105 | 24042.957 | 6756.111 | 0 | 3904.397 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2050.484 | 0 | 0
February | 85552900000 | 48904.698 | 18-FEB-13:00 | 8160.982 | 24042.957 | 6756.111 | 0 | 7843.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2100.828 | 0 | 0
March | 96588200000 | 56194.821 | 28-MAR-17:19 | 9181.105 | 24042.957 | 6756.111 | 0 | 14174.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2039.704 | 0 | 0
April | 101096000000 | 64772.174 | 15-APR-18:10 | 9181.105 | 24042.957 | 6756.111 | 0 | 22537.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2254.589 | 0 | 0
May | 118002000000 | 72996.893 | 31-MAY-17:00 | 9181.105 | 24042.957 | 6756.111 | 0 | 30940.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2075.771 | 0 | 0
June | 127251000000 | 75032.929 | 08-JUN-18:00 | 9181.105 | 24042.957 | 6756.111 | 0 | 32779.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2272.775 | 0 | 0
July | 140469000000 | 80223.204 | 03-JUL-17:00 | 9181.105 | 24042.957 | 6756.111 | 0 | 38164.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2078.2 | 0 | 0
August | 137898000000 | 77168.04 | 17-AUG-11:00 | 9181.105 | 24042.957 | 6756.111 | 0 | 35050.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.048 | 0 | 0
September | 124711000000 | 72151.503 | 01-SEP-17:49 | 9181.105 | 24042.957 | 6756.111 | 0 | 30040.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2130.569 | 0 | 0
October | 105147000000 | 66004.028 | 21-OCT-18:10 | 9181.105 | 24042.957 | 6756.111 | 0 | 22274.393 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2265.968 | 0 | 0
November | 92497300000 | 54167.996 | 22-NOV-12:00 | 9181.105 | 24042.957 | 6756.111 | 0 | 12071.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2116.158 | 0 | 0
December | 94397900000 | 49307.354 | 13-DEC-13:00 | 9181.105 | 24042.957 | 6756.111 | 0 | 7193.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2133.601 | 0 | 0
Annual Sum or Average | 1317690000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 85552900000 | 47418.547 |  | 8160.982 | 24042.957 | 6756.111 | 0 | 3904.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2039.704 | 0 | 0
Maximum of Months | 140469000000 | 80223.204 |  | 9181.105 | 24042.957 | 6756.111 | 0 | 38164.829 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2272.775 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37849.45 | 18593.17 | 0 | 56442.61
Cost per Total Building Area ($/m2) | 74.05 | 36.37 | 0 | 110.42
Cost per Net Conditioned Building Area ($/m2) | 74.05 | 36.37 | 0 | 110.42

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2633.66 | 5152.39 | 5152.39
Net Site Energy | 2633.66 | 5152.39 | 5152.39
Total Source Energy | 5156.5 | 10087.98 | 10087.98
Net Source Energy | 5156.5 | 10087.98 | 10087.98
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 117.26 | 0 | 0 | 0 | 0
Cooling | 34.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 176.13 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 176.43 | 0 | 0 | 0 | 1375.88
Refrigeration | 66.27 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1138.57 | 1495.09 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 52504.22 | 40004.7 | 12499.52 | 0.76 | 3.38
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 34487.73 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 34206.32 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.85 | 3122.28 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15631.3355 | 13.7659 | 76.1777 | 0 | 0 | 459412.2844 | 5642.4466
February | 14077.5674 | 12.3971 | 68.6844 | 0 | 0 | 414222.3821 | 5081.8232
March | 15155.5817 | 13.3341 | 76.1574 | 0 | 0 | 459304.7541 | 5477.7256
April | 14431.9148 | 12.6905 | 73.7558 | 0 | 0 | 444828.5134 | 5219.9361
May | 14609.5961 | 12.8351 | 76.7469 | 0 | 0 | 462880.5949 | 5290.5576
June | 14019.9261 | 12.311 | 74.738 | 0 | 0 | 450770.8411 | 5080.3427
July | 14796.8906 | 12.9783 | 81.5549 | 0 | 0 | 491901.773 | 5370.0497
August | 15093.3335 | 13.2322 | 84.2753 | 0 | 0.0001 | 508315.5878 | 5480.9486
September | 14435.2637 | 12.6597 | 79.8076 | 0 | 0 | 481363.7937 | 5239.5588
October | 14594.8405 | 12.8138 | 78.1617 | 0 | 0 | 471422.2728 | 5289.767
November | 14371.3372 | 12.6334 | 74.1223 | 0 | 0 | 447043.0191 | 5200.0883
December | 15356.312 | 13.5143 | 76.5214 | 0 | 0 | 461496.1435 | 5548.3093
Annual Sum or Average | 176573.899 | 155.1654 | 920.7034 | 0 | 0.0006 | 5552960 | 63921.5535
Minimum of Months | 14019.9261 | 12.311 | 68.6844 | 0 | 0 | 414222.3821 | 5080.3427
Maximum of Months | 15631.3355 | 13.7659 | 84.2753 | 0 | 0.0001 | 508315.5878 | 5642.4466
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94196800000 | 55374.36 | 26-JAN-12:00 | 9181.105 | 24042.957 | 6553.789 | 0 | 13518.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2078.291 | 0 | 0
February | 84931100000 | 54497.055 | 13-FEB-11:00 | 9181.105 | 24042.957 | 6553.789 | 0 | 11833.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2885.966 | 0 | 0
March | 94174700000 | 53144.156 | 04-MAR-11:00 | 8160.982 | 24042.957 | 6553.789 | 0 | 11532.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2853.53 | 0 | 0
April | 91206600000 | 56646.034 | 11-APR-17:10 | 9181.105 | 24042.957 | 6553.789 | 0 | 14855.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2013.11 | 0 | 0
May | 94907900000 | 55238.424 | 30-MAY-11:09 | 9181.105 | 24042.957 | 6553.789 | 0 | 13124.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2336.138 | 0 | 0
June | 92425000000 | 55275.023 | 28-JUN-12:00 | 9181.105 | 24042.957 | 6553.789 | 0 | 13361.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2135.328 | 0 | 0
July | 100858000000 | 58340.458 | 29-JUL-10:39 | 8160.982 | 24042.957 | 6553.789 | 0 | 16669.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.728 | 0 | 0
August | 104224000000 | 63037.045 | 08-AUG-10:39 | 9181.105 | 24042.957 | 6553.789 | 0 | 20327.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.85 | 0 | 0
September | 98697700000 | 62172.37 | 24-SEP-10:00 | 7140.86 | 24042.957 | 6553.789 | 0 | 21600.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2834.039 | 0 | 0
October | 96659300000 | 59505.446 | 19-OCT-10:00 | 9181.105 | 24042.957 | 6553.789 | 0 | 16848.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2878.971 | 0 | 0
November | 91660600000 | 55822.666 | 20-NOV-12:00 | 9181.105 | 24042.957 | 6553.789 | 0 | 13947.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2097.044 | 0 | 0
December | 94624000000 | 55923.685 | 19-DEC-12:00 | 9181.105 | 24042.957 | 6553.789 | 0 | 14071.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2074.646 | 0 | 0
Annual Sum or Average | 1138570000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84931100000 | 53144.156 |  | 7140.86 | 24042.957 | 6553.789 | 0 | 11532.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2013.11 | 0 | 0
Maximum of Months | 104224000000 | 63037.045 |  | 9181.105 | 24042.957 | 6553.789 | 0 | 21600.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.85 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 39153.46 | 12572.01 | 0 | 51725.47
Cost per Total Building Area ($/m2) | 76.6 | 24.6 | 0 | 101.19
Cost per Net Conditioned Building Area ($/m2) | 76.6 | 24.6 | 0 | 101.19

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2904.76 | 5682.76 | 5682.76
Net Site Energy | 2904.76 | 5682.76 | 5682.76
Total Source Energy | 6437.17 | 12593.41 | 12593.41
Net Source Energy | 6437.17 | 12593.41 | 12593.41
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 233.44 | 0 | 0 | 0 | 0
Cooling | 201.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 185.72 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 155.96 | 0 | 0 | 0 | 1375.88
Refrigeration | 65.14 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1313.95 | 1590.81 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.262 | 0.318 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.262 | 0.318
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76379.66 | 51994.91 | 24384.75 | 0.68 | 3.13
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 43831.94 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 39600.07 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.13 | 3427.74 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 30651.7617 | 43.1178 | 143.8732 | 0 | 0.0003 | 717284.5613 | 12198.3191
February | 26171.1511 | 37.5817 | 130.0491 | 0 | 0.0003 | 648403.5384 | 10494.8895
March | 28980.7415 | 41.6925 | 144.7267 | 0 | 0.0003 | 721587.1097 | 11629.4826
April | 28471.9447 | 42.1608 | 153.4679 | 0 | 0.0003 | 765227.4804 | 11550.0686
May | 31144.6437 | 46.621 | 172.5977 | 0 | 0.0003 | 860636.125 | 12686.523
June | 34497.2929 | 52.4449 | 198.7454 | 0 | 0.0004 | 991053.2252 | 14135.8846
July | 37424.8198 | 57.1588 | 218.0868 | 0 | 0.0004 | 1087510 | 15362.8633
August | 37062.6136 | 56.5556 | 215.5058 | 0 | 0.0004 | 1074640 | 15208.9778
September | 32879.7428 | 49.7813 | 187.5049 | 0 | 0.0004 | 934993.3171 | 13451.8163
October | 29480.8513 | 43.7684 | 159.9737 | 0 | 0.0003 | 797672.0457 | 11971.1527
November | 27555.5557 | 39.8562 | 139.6215 | 0 | 0.0003 | 696143.8453 | 11079.8291
December | 30125.6442 | 42.6528 | 143.989 | 0 | 0.0003 | 717876.1348 | 12017.5314
Annual Sum or Average | 374446.7628 | 553.3917 | 2008.1416 | 0 | 0.0039 | 10013000 | 151787.338
Minimum of Months | 26171.1511 | 37.5817 | 130.0491 | 0 | 0.0003 | 648403.5384 | 10494.8895
Maximum of Months | 37424.8198 | 57.1588 | 218.0868 | 0 | 0.0004 | 1087510 | 15362.8633
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94125000000 | 44026.789 | 18-JAN-13:00 | 9181.105 | 24042.957 | 6859.252 | 0 | 1848.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2094.964 | 0 | 0
February | 85086100000 | 46138.66 | 08-FEB-13:00 | 9181.105 | 24042.957 | 6859.252 | 0 | 3964.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2091.254 | 0 | 0
March | 94689600000 | 52900.016 | 31-MAR-16:10 | 9181.105 | 24042.957 | 6859.252 | 0 | 10795.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021.544 | 0 | 0
April | 100416000000 | 64753.719 | 21-APR-17:10 | 9181.105 | 24042.957 | 6859.252 | 0 | 22634.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2035.536 | 0 | 0
May | 112936000000 | 69957.715 | 31-MAY-17:10 | 9181.105 | 24042.957 | 6859.252 | 0 | 27847.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026.447 | 0 | 0
June | 130050000000 | 81091.453 | 27-JUN-16:19 | 9181.105 | 24042.957 | 6859.252 | 0 | 38983.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024.58 | 0 | 0
July | 142708000000 | 79257.98 | 24-JUL-16:19 | 9181.105 | 24042.957 | 6859.252 | 0 | 37147.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027.269 | 0 | 0
August | 141018000000 | 78086.829 | 04-AUG-16:19 | 9181.105 | 24042.957 | 6859.252 | 0 | 35955.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2047.599 | 0 | 0
September | 122694000000 | 74049.221 | 01-SEP-14:00 | 9181.105 | 24042.957 | 6859.252 | 0 | 31850.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.574 | 0 | 0
October | 104674000000 | 64684.954 | 06-OCT-12:00 | 9181.105 | 24042.957 | 6859.252 | 0 | 22472.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2129.5 | 0 | 0
November | 91350800000 | 47879.127 | 10-NOV-12:00 | 9181.105 | 24042.957 | 6859.252 | 0 | 5732.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2063.726 | 0 | 0
December | 94202600000 | 47882.717 | 05-DEC-13:00 | 9181.105 | 24042.957 | 6859.252 | 0 | 5708.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2090.941 | 0 | 0
Annual Sum or Average | 1313950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 85086100000 | 44026.789 |  | 9181.105 | 24042.957 | 6859.252 | 0 | 1848.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021.544 | 0 | 0
Maximum of Months | 142708000000 | 81091.453 |  | 9181.105 | 24042.957 | 6859.252 | 0 | 38983.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2129.5 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34168.63 | 12955.19 | 0 | 47123.82
Cost per Total Building Area ($/m2) | 66.85 | 25.35 | 0 | 92.19
Cost per Net Conditioned Building Area ($/m2) | 66.85 | 25.35 | 0 | 92.19

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2859.11 | 5593.46 | 5593.46
Net Site Energy | 2859.11 | 5593.46 | 5593.46
Total Source Energy | 5329.6 | 10426.62 | 10426.62
Net Source Energy | 5329.6 | 10426.62 | 10426.62
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 353.6 | 0 | 0 | 0 | 0
Cooling | 8.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 167.1 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 202.03 | 0 | 0 | 0 | 1375.88
Refrigeration | 65.29 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1102.07 | 1757.04 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 6.49 | 0.391 | 0.39 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 6.49 | 0.391 | 0.39 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 6.49 | 0.391 | 0.39 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 6.49 | 0.391 | 0.39
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 6.49 | 0.391 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44183.93 | 35287.73 | 8896.2 | 0.8 | 3.47
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 35639.17 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 37809.29 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.67 | 2919.05 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17535.182 | 15.4995 | 75.2617 | 0 | 0.0001 | 453823.589 | 6298.5766
February | 14896.9032 | 13.1448 | 67.9974 | 0 | 0 | 410049.6539 | 5363.3008
March | 16613.6321 | 14.663 | 75.2363 | 0 | 0.0001 | 453698.8071 | 5979.5491
April | 15532.5897 | 13.6955 | 72.736 | 0 | 0 | 438637.6812 | 5597.7702
May | 15439.847 | 13.5967 | 75.3435 | 0 | 0 | 454382.0991 | 5573.627
June | 14675.6987 | 12.9149 | 73.2083 | 0 | 0 | 441515.1066 | 5302.6395
July | 14921.8656 | 13.1207 | 76.3778 | 0 | 0 | 460642.7522 | 5397.5086
August | 14938.564 | 13.1361 | 76.3263 | 0 | 0 | 460331.2071 | 5403.1307
September | 14484.3591 | 12.7325 | 74.7677 | 0 | 0 | 450935.695 | 5241.1744
October | 15184.0876 | 13.3617 | 75.8557 | 0 | 0 | 457482.2511 | 5486.6709
November | 15386.3194 | 13.5619 | 72.8694 | 0 | 0 | 439447.5637 | 5547.5529
December | 17449.3843 | 15.4214 | 75.2956 | 0 | 0.0001 | 454030.8218 | 6268.9853
Annual Sum or Average | 187058.4326 | 164.8487 | 891.2759 | 0 | 0.0006 | 5374980 | 67460.4861
Minimum of Months | 14484.3591 | 12.7325 | 67.9974 | 0 | 0 | 410049.6539 | 5241.1744
Maximum of Months | 17535.182 | 15.4995 | 76.3778 | 0 | 0.0001 | 460642.7522 | 6298.5766
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 93050900000 | 43297.826 | 05-JAN-19:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2239.704 | 0 | 0
February | 84075600000 | 45704.361 | 14-FEB-12:00 | 9181.105 | 24042.957 | 6350.567 | 0 | 4045.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2084.316 | 0 | 0
March | 93025300000 | 43302.589 | 30-MAR-18:30 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2244.467 | 0 | 0
April | 89937200000 | 47557.292 | 29-APR-12:00 | 8160.982 | 24042.957 | 6350.567 | 0 | 6908.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2094.666 | 0 | 0
May | 93165400000 | 51439.506 | 17-MAY-13:00 | 9181.105 | 24042.957 | 6350.567 | 0 | 9732.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2132.708 | 0 | 0
June | 90527200000 | 54077.447 | 16-JUN-11:09 | 9181.105 | 24042.957 | 6350.567 | 0 | 12152.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2350.287 | 0 | 0
July | 94449100000 | 59238.704 | 02-JUL-12:00 | 7140.86 | 24042.957 | 6350.567 | 0 | 19616.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2088.209 | 0 | 0
August | 94385200000 | 56643.367 | 15-AUG-11:00 | 9181.105 | 24042.957 | 6350.567 | 0 | 14949.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2118.85 | 0 | 0
September | 92458800000 | 59517.684 | 28-SEP-16:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 17897.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2045.533 | 0 | 0
October | 93801000000 | 51068.717 | 30-OCT-12:00 | 9181.105 | 24042.957 | 6350.567 | 0 | 9423.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2070.614 | 0 | 0
November | 90103300000 | 43320.979 | 16-NOV-19:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2262.858 | 0 | 0
December | 93093400000 | 43294.643 | 14-DEC-19:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2236.521 | 0 | 0
Annual Sum or Average | 1102070000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84075600000 | 43294.643 |  | 7140.86 | 24042.957 | 6350.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2045.533 | 0 | 0
Maximum of Months | 94449100000 | 59517.684 |  | 9181.105 | 24042.957 | 6350.567 | 0 | 19616.111 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2350.287 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 44198.02 | 14793.4 | 0 | 58991.42
Cost per Total Building Area ($/m2) | 86.47 | 28.94 | 0 | 115.41
Cost per Net Conditioned Building Area ($/m2) | 86.47 | 28.94 | 0 | 115.41

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3288.72 | 6433.92 | 6433.92
Net Site Energy | 3288.72 | 6433.92 | 6433.92
Total Source Energy | 6735.34 | 13176.75 | 13176.75
Net Source Energy | 6735.34 | 13176.75 | 13176.75
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 615.84 | 0 | 0 | 0 | 0
Cooling | 158.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 181.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 205.75 | 0 | 0 | 0 | 1375.88
Refrigeration | 64.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1265.72 | 2023 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75110.31 | 50780.82 | 24329.49 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70317.36 | 47540.39 | 22776.97 | 0.68 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 55692.16 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 52138.32 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.02 | 3307.88 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29381.5099 | 43.9242 | 95.396 | 0 | 0.0004 | 5928.8357 | 11746.7057
February | 26159.6118 | 39.3001 | 85.9981 | 0 | 0.0004 | 5344.8617 | 10476.1955
March | 26608.7327 | 41.5974 | 96.4338 | 0 | 0.0004 | 5994.3238 | 10804.4211
April | 23695.9401 | 38.3868 | 93.2926 | 0 | 0.0004 | 5799.7217 | 9744.4828
May | 24529.4819 | 41.5624 | 106.6527 | 0 | 0.0004 | 6631.0981 | 10254.158
June | 26536.5792 | 46.5215 | 123.984 | 0 | 0.0005 | 7709.3017 | 11235.6849
July | 29007.7309 | 51.3821 | 138.447 | 0 | 0.0006 | 8608.808 | 12330.2901
August | 29096.4388 | 51.5567 | 138.9666 | 0 | 0.0006 | 8641.1266 | 12369.5912
September | 24700.234 | 42.7663 | 112.4451 | 0 | 0.0005 | 6991.6142 | 10409.1668
October | 24708.3946 | 41.0511 | 102.9336 | 0 | 0.0004 | 6399.5367 | 10254.4803
November | 25020.5676 | 39.7322 | 94.088 | 0 | 0.0004 | 5848.8099 | 10216.0184
December | 28721.1186 | 43.3167 | 95.3489 | 0 | 0.0004 | 5926.1151 | 11517.409
Annual Sum or Average | 318166.3402 | 521.0976 | 1283.9864 | 0 | 0.0054 | 79824.1531 | 131358.6039
Minimum of Months | 23695.9401 | 38.3868 | 85.9981 | 0 | 0.0004 | 5344.8617 | 9744.4828
Maximum of Months | 29381.5099 | 51.5567 | 138.9666 | 0 | 0.0006 | 8641.1266 | 12369.5912
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94010000000 | 43642.687 | 09-JAN-19:10 | 9181.105 | 24042.957 | 6739.396 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2195.736 | 0 | 0
February | 84750300000 | 43652.341 | 15-FEB-19:10 | 9181.105 | 24042.957 | 6739.396 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2205.391 | 0 | 0
March | 95048400000 | 58057.027 | 09-MAR-13:00 | 9181.105 | 24042.957 | 6739.396 | 0 | 15958.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2135.468 | 0 | 0
April | 91962700000 | 58004.32 | 04-APR-17:10 | 9181.105 | 24042.957 | 6739.396 | 0 | 15983.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2057.7 | 0 | 0
May | 105145000000 | 68869.394 | 15-MAY-17:10 | 9181.105 | 24042.957 | 6739.396 | 0 | 26769.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2136.78 | 0 | 0
June | 122242000000 | 81032.745 | 30-JUN-17:19 | 9181.105 | 24042.957 | 6739.396 | 0 | 38931.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.381 | 0 | 0
July | 136505000000 | 83140.865 | 25-JUL-11:00 | 9181.105 | 24042.957 | 6739.396 | 0 | 41039.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.772 | 0 | 0
August | 137017000000 | 82698.808 | 09-AUG-17:49 | 9181.105 | 24042.957 | 6739.396 | 0 | 40596.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2138.746 | 0 | 0
September | 110862000000 | 69745.083 | 05-SEP-11:00 | 9181.105 | 24042.957 | 6739.396 | 0 | 27645.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2136.235 | 0 | 0
October | 101474000000 | 65461.188 | 03-OCT-11:09 | 9181.105 | 24042.957 | 6739.396 | 0 | 23181.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2316.475 | 0 | 0
November | 92741100000 | 59949.261 | 04-NOV-11:00 | 8160.982 | 24042.957 | 6739.396 | 0 | 18092.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.702 | 0 | 0
December | 93966900000 | 43645.534 | 02-DEC-19:10 | 9181.105 | 24042.957 | 6739.396 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2198.583 | 0 | 0
Annual Sum or Average | 1265720000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84750300000 | 43642.687 |  | 8160.982 | 24042.957 | 6739.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2057.7 | 0 | 0
Maximum of Months | 137017000000 | 83140.865 |  | 9181.105 | 24042.957 | 6739.396 | 0 | 41039.635 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2913.702 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 23347.96 | 20290.11 | 0 | 43638.07
Cost per Total Building Area ($/m2) | 45.68 | 39.69 | 0 | 85.37
Cost per Net Conditioned Building Area ($/m2) | 45.68 | 39.69 | 0 | 85.37

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3034.62 | 5936.81 | 5936.81
Net Site Energy | 3034.62 | 5936.81 | 5936.81
Total Source Energy | 6006.69 | 11751.26 | 11751.26
Net Source Energy | 6006.69 | 11751.26 | 11751.26
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 422.18 | 0 | 0 | 0 | 0
Cooling | 89.51 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 194.01 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 201.28 | 0 | 0 | 0 | 1375.88
Refrigeration | 64.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1209.74 | 1824.88 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 57417.8 | 45857.03 | 11560.77 | 0.8 | 3.47
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 50744.87 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 41426.76 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.47 | 3793.36 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 36192.4467 | 54.1086 | 115.2053 | 0 | 0.0005 | 119736.4151 | 14611.2961
February | 31902.5793 | 48.1538 | 104.0324 | 0 | 0.0004 | 108128.2639 | 12924.4151
March | 34394.1325 | 52.5025 | 115.3395 | 0 | 0.0005 | 119885.7776 | 13991.4685
April | 32114.6492 | 50.1388 | 113.7351 | 0 | 0.0005 | 118227.7488 | 13173.6355
May | 34252.0945 | 54.5406 | 127.0682 | 0 | 0.0005 | 132096.1999 | 14154.8749
June | 34958.4201 | 56.288 | 133.0587 | 0 | 0.0005 | 138328.652 | 14507.8456
July | 37927.3543 | 61.4407 | 146.3737 | 0 | 0.0006 | 152173.864 | 15776.4732
August | 36840.4504 | 59.5284 | 141.359 | 0 | 0.0006 | 146959.3293 | 15309.4983
September | 33578.4537 | 53.8814 | 126.8064 | 0 | 0.0005 | 131827.3338 | 13917.0355
October | 33072.5223 | 51.8361 | 118.2202 | 0 | 0.0005 | 122891.632 | 13586.3644
November | 33369.5539 | 50.8644 | 111.5028 | 0 | 0.0005 | 115897.2019 | 13567.4079
December | 36329.6037 | 54.2333 | 115.2067 | 0 | 0.0005 | 119737.1494 | 14658.7813
Annual Sum or Average | 414932.2606 | 647.5167 | 1467.9081 | 0 | 0.0059 | 1525890 | 170179.0965
Minimum of Months | 31902.5793 | 48.1538 | 104.0324 | 0 | 0.0004 | 108128.2639 | 12924.4151
Maximum of Months | 37927.3543 | 61.4407 | 146.3737 | 0 | 0.0006 | 152173.864 | 15776.4732
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94928500000 | 44147.42 | 26-JAN-19:10 | 9181.105 | 24042.957 | 7224.875 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2214.99 | 0 | 0
February | 85725400000 | 44857.727 | 14-FEB-14:00 | 9181.105 | 24042.957 | 7224.875 | 0 | 2308.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2100.364 | 0 | 0
March | 95046900000 | 46572.635 | 02-MAR-13:00 | 9181.105 | 24042.957 | 7224.875 | 0 | 4032.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2091.066 | 0 | 0
April | 93732400000 | 56418.215 | 21-APR-17:10 | 9181.105 | 24042.957 | 7224.875 | 0 | 13959.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2010.066 | 0 | 0
May | 104727000000 | 61126.337 | 31-MAY-17:10 | 9181.105 | 24042.957 | 7224.875 | 0 | 18647.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2029.578 | 0 | 0
June | 109669000000 | 64492.548 | 20-JUN-17:10 | 9181.105 | 24042.957 | 7224.875 | 0 | 22025.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018.434 | 0 | 0
July | 120645000000 | 66031.284 | 31-JUL-17:19 | 9181.105 | 24042.957 | 7224.875 | 0 | 23562.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2019.44 | 0 | 0
August | 116511000000 | 65940.069 | 01-AUG-17:19 | 9181.105 | 24042.957 | 7224.875 | 0 | 23427.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2063.399 | 0 | 0
September | 104514000000 | 60869.445 | 02-SEP-17:10 | 9181.105 | 24042.957 | 7224.875 | 0 | 18379.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2041.405 | 0 | 0
October | 97430000000 | 56067.5 | 11-OCT-16:19 | 9181.105 | 24042.957 | 7224.875 | 0 | 13571.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2047.535 | 0 | 0
November | 91884700000 | 44157.933 | 15-NOV-19:00 | 9181.105 | 24042.957 | 7224.875 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2225.503 | 0 | 0
December | 94929100000 | 44143.452 | 07-DEC-19:10 | 9181.105 | 24042.957 | 7224.875 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2211.022 | 0 | 0
Annual Sum or Average | 1209740000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 85725400000 | 44143.452 |  | 9181.105 | 24042.957 | 7224.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2010.066 | 0 | 0
Maximum of Months | 120645000000 | 66031.284 |  | 9181.105 | 24042.957 | 7224.875 | 0 | 23562.907 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2225.503 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12601.8 | 13096.06 | 0 | 25697.86
Cost per Total Building Area ($/m2) | 24.65 | 25.62 | 0 | 50.27
Cost per Net Conditioned Building Area ($/m2) | 24.65 | 25.62 | 0 | 50.27

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3132.88 | 6129.04 | 6129.04
Net Site Energy | 3132.88 | 6129.04 | 6129.04
Total Source Energy | 4145.36 | 8109.82 | 8109.82
Net Source Energy | 4145.36 | 8109.82 | 8109.82
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 599.24 | 0 | 0 | 0 | 0
Cooling | 17.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 171.16 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 217.98 | 0 | 0 | 0 | 1375.88
Refrigeration | 64.77 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1114.24 | 2018.64 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55787.65 | 41103.98 | 14683.67 | 0.74 | 3.32
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 44634.23 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 45089.74 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.8 | 3065.52 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16167.0625 | 17.8174 | 20.1302 | 0 | 0.0001 | 265296.6424 | 5931.9768
February | 13738.5413 | 15.3047 | 18.1519 | 0 | 0.0001 | 239280.5958 | 5058.4469
March | 14852.1792 | 16.6179 | 20.087 | 0 | 0.0001 | 264814.2294 | 5476.2614
April | 13240.9764 | 15.0415 | 19.3533 | 0 | 0.0001 | 255214.363 | 4906.4278
May | 12292.9277 | 14.3091 | 20.1673 | 0 | 0.0001 | 266051.4028 | 4592.0281
June | 11249.3451 | 13.2951 | 19.7373 | 0 | 0.0001 | 260431.486 | 4223.7025
July | 11260.1644 | 13.5149 | 21.0778 | 0 | 0.0001 | 278170.8229 | 4249.9327
August | 11198.3655 | 13.4727 | 21.166 | 0 | 0.0001 | 279341.5774 | 4230.027
September | 11443.0054 | 13.5418 | 20.1905 | 0 | 0.0001 | 266415.4997 | 4298.3167
October | 12846.3041 | 14.8 | 20.0967 | 0 | 0.0001 | 265079.3986 | 4782.3292
November | 14431.1325 | 16.1396 | 19.4718 | 0 | 0.0001 | 256700.7455 | 5320.2456
December | 16001.5213 | 17.6686 | 20.1389 | 0 | 0.0001 | 265422.0602 | 5874.8391
Annual Sum or Average | 158721.5255 | 181.5234 | 239.7688 | 0 | 0.0012 | 3162220 | 58944.5338
Minimum of Months | 11198.3655 | 13.2951 | 18.1519 | 0 | 0.0001 | 239280.5958 | 4223.7025
Maximum of Months | 16167.0625 | 17.8174 | 21.166 | 0 | 0.0001 | 279341.5774 | 5931.9768
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 93480100000 | 43420.561 | 28-JAN-19:10 | 9181.105 | 24042.957 | 6497.027 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2215.979 | 0 | 0
February | 84313100000 | 43418.553 | 22-FEB-19:10 | 9181.105 | 24042.957 | 6497.027 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2213.97 | 0 | 0
March | 93310200000 | 43631.897 | 29-MAR-16:10 | 9181.105 | 24042.957 | 6497.027 | 0 | 1886.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024.18 | 0 | 0
April | 89927500000 | 45281.101 | 29-APR-17:10 | 9181.105 | 24042.957 | 6497.027 | 0 | 3503.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2056.363 | 0 | 0
May | 93746100000 | 51834.608 | 05-MAY-16:10 | 9181.105 | 24042.957 | 6497.027 | 0 | 10058.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2054.622 | 0 | 0
June | 91765900000 | 56000.193 | 28-JUN-12:00 | 9181.105 | 24042.957 | 6497.027 | 0 | 14145.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2134.085 | 0 | 0
July | 98016500000 | 59678.015 | 31-JUL-17:19 | 9181.105 | 24042.957 | 6497.027 | 0 | 17891.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2065.536 | 0 | 0
August | 98429000000 | 59459.083 | 18-AUG-17:40 | 9181.105 | 24042.957 | 6497.027 | 0 | 17670.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2067.047 | 0 | 0
September | 93874400000 | 65323.821 | 02-SEP-16:10 | 9181.105 | 24042.957 | 6497.027 | 0 | 23553.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2049.403 | 0 | 0
October | 93403600000 | 46624.417 | 17-OCT-17:19 | 9181.105 | 24042.957 | 6497.027 | 0 | 3393.217 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2026.618 | 0 | 0
November | 90451300000 | 43456.983 | 04-NOV-19:10 | 9181.105 | 24042.957 | 6497.027 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2252.401 | 0 | 0
December | 93524300000 | 43421.225 | 23-DEC-19:19 | 9181.105 | 24042.957 | 6497.027 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2216.642 | 0 | 0
Annual Sum or Average | 1114240000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84313100000 | 43418.553 |  | 9181.105 | 24042.957 | 6497.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024.18 | 0 | 0
Maximum of Months | 98429000000 | 65323.821 |  | 9181.105 | 24042.957 | 6497.027 | 0 | 23553.328 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2252.401 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22356.07 | 16765.5 | 0 | 39121.57
Cost per Total Building Area ($/m2) | 43.74 | 32.8 | 0 | 76.54
Cost per Net Conditioned Building Area ($/m2) | 43.74 | 32.8 | 0 | 76.54

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3456.37 | 6761.91 | 6761.91
Net Site Energy | 3456.37 | 6761.91 | 6761.91
Total Source Energy | 6704.64 | 13116.7 | 13116.7
Net Source Energy | 6704.64 | 13116.7 | 13116.7
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 834.5 | 0 | 0 | 0 | 0
Cooling | 88.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 179.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 226.38 | 0 | 0 | 0 | 1375.88
Refrigeration | 64.53 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1194.09 | 2262.29 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 73927.13 | 49980.89 | 23946.24 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70317.36 | 47540.39 | 22776.97 | 0.68 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 64035.08 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 60908.32 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.98 | 3255.78 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47527.0472 | 72.457 | 175.9416 | 0 | 0.0006 | 40485.4907 | 19252.1511
February | 42227.7104 | 64.7721 | 158.6868 | 0 | 0.0005 | 36515.7872 | 17143.1945
March | 45087.3032 | 70.1695 | 175.4944 | 0 | 0.0006 | 40385.3367 | 18400.7811
April | 40338.4492 | 64.8271 | 169.2893 | 0 | 0.0005 | 38961.1223 | 16658.5428
May | 41179.4788 | 68.2612 | 185.3028 | 0 | 0.0006 | 42650.0792 | 17204.9699
June | 43828.1812 | 74.1715 | 206.3316 | 0 | 0.0006 | 47492.5674 | 18456.906
July | 48531.3839 | 82.7344 | 232.0916 | 0 | 0.0007 | 53422.8055 | 20495.2291
August | 46613.513 | 79.2316 | 221.5213 | 0 | 0.0007 | 50989.383 | 19662.9907
September | 40466.4585 | 67.9168 | 187.115 | 0 | 0.0006 | 43068.5098 | 16987.143
October | 40861.2232 | 66.7356 | 177.8876 | 0 | 0.0006 | 40941.8036 | 16976.5774
November | 42566.9138 | 67.0624 | 170.5725 | 0 | 0.0005 | 39254.1772 | 17450.137
December | 46656.4048 | 71.6269 | 175.6997 | 0 | 0.0006 | 40430.7741 | 18947.0194
Annual Sum or Average | 525884.0674 | 849.9661 | 2235.9344 | 0 | 0.007 | 514597.8368 | 217635.6421
Minimum of Months | 40338.4492 | 64.7721 | 158.6868 | 0 | 0.0005 | 36515.7872 | 16658.5428
Maximum of Months | 48531.3839 | 82.7344 | 232.0916 | 0 | 0.0007 | 53422.8055 | 20495.2291
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 93943500000 | 43587.208 | 28-JAN-19:30 | 9181.105 | 24042.957 | 6687.288 | 0 | 164.206 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2028.159 | 0 | 0
February | 84732100000 | 43596.369 | 18-FEB-19:10 | 9181.105 | 24042.957 | 6687.288 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2201.526 | 0 | 0
March | 93711100000 | 45341.88 | 31-MAR-14:00 | 9181.105 | 24042.957 | 6687.288 | 0 | 3326.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2103.905 | 0 | 0
April | 90406300000 | 46422.238 | 07-APR-13:00 | 9181.105 | 24042.957 | 6687.288 | 0 | 4384.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2126.183 | 0 | 0
May | 98966300000 | 67674.693 | 30-MAY-17:10 | 9181.105 | 24042.957 | 6687.288 | 0 | 25627.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2136.127 | 0 | 0
June | 110203000000 | 77613.52 | 08-JUN-12:00 | 9181.105 | 24042.957 | 6687.288 | 0 | 35564.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.345 | 0 | 0
July | 123964000000 | 78591.625 | 14-JUL-10:00 | 9181.105 | 24042.957 | 6687.288 | 0 | 35748.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.763 | 0 | 0
August | 118317000000 | 79153.228 | 04-AUG-17:19 | 9181.105 | 24042.957 | 6687.288 | 0 | 37104.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.679 | 0 | 0
September | 99937200000 | 68313.418 | 06-SEP-11:09 | 9181.105 | 24042.957 | 6687.288 | 0 | 26073.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2328.202 | 0 | 0
October | 95002400000 | 57497.433 | 31-OCT-12:00 | 9181.105 | 24042.957 | 6687.288 | 0 | 15450.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2135.541 | 0 | 0
November | 91086400000 | 56984.744 | 02-NOV-12:09 | 9181.105 | 24042.957 | 6687.288 | 0 | 14752.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2320.863 | 0 | 0
December | 93816600000 | 43594.968 | 11-DEC-19:10 | 9181.105 | 24042.957 | 6687.288 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2200.125 | 0 | 0
Annual Sum or Average | 1194090000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84732100000 | 43587.208 |  | 9181.105 | 24042.957 | 6687.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2028.159 | 0 | 0
Maximum of Months | 123964000000 | 79153.228 |  | 9181.105 | 24042.957 | 6687.288 | 0 | 37104.198 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2931.763 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17279.47 | 19939.73 | 0 | 37219.19
Cost per Total Building Area ($/m2) | 33.8 | 39.01 | 0 | 72.81
Cost per Net Conditioned Building Area ($/m2) | 33.8 | 39.01 | 0 | 72.81

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3210 | 6279.92 | 6279.92
Net Site Energy | 3210 | 6279.92 | 6279.92
Total Source Energy | 6115.21 | 11963.55 | 11963.55
Net Source Energy | 6115.21 | 11963.55 | 11963.55
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 610.83 | 0 | 0 | 0 | 0
Cooling | 57.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 189.5 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 225.31 | 0 | 0 | 0 | 1375.88
Refrigeration | 64.64 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1172.45 | 2037.55 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55551.26 | 44366.3 | 11184.95 | 0.8 | 3.47
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 58605.63 | 0.8
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 49451.65 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.36 | 3670.05 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37345.5353 | 55.1278 | 115.0612 | 0 | 0.0005 | 119580.2631 | 15007.6817
February | 33315.9078 | 49.3928 | 103.801 | 0 | 0.0004 | 107879.8415 | 13409.2679
March | 35834.4345 | 53.8035 | 115.3111 | 0 | 0.0005 | 119848.4724 | 14489.3327
April | 32828.4905 | 50.4352 | 111.8354 | 0 | 0.0005 | 116246.3301 | 13386.2144
May | 33404.4723 | 52.2281 | 118.712 | 0 | 0.0005 | 123401.9029 | 13710.1413
June | 33008.4766 | 52.4715 | 121.9735 | 0 | 0.0005 | 126799.2813 | 13632.2244
July | 36292.4051 | 58.4467 | 138.1943 | 0 | 0.0006 | 143667.748 | 15062.508
August | 35380.6072 | 56.805 | 133.7845 | 0 | 0.0005 | 139081.999 | 14667.0868
September | 32826.7715 | 51.9853 | 120.2337 | 0 | 0.0005 | 124989.1103 | 13537.8203
October | 33771.2256 | 52.3187 | 117.4022 | 0 | 0.0005 | 122036.3733 | 13813.3088
November | 34551.6638 | 51.8994 | 111.3018 | 0 | 0.0005 | 115681.5738 | 13972.8029
December | 37593.1846 | 55.3636 | 115.122 | 0 | 0.0005 | 119642.2105 | 15094.4759
Annual Sum or Average | 416153.1747 | 640.2775 | 1422.7329 | 0 | 0.0058 | 1478860 | 169782.8649
Minimum of Months | 32826.7715 | 49.3928 | 103.801 | 0 | 0.0004 | 107879.8415 | 13386.2144
Maximum of Months | 37593.1846 | 58.4467 | 138.1943 | 0 | 0.0006 | 143667.748 | 15094.4759
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94804700000 | 44021.406 | 21-JAN-19:10 | 9181.105 | 24042.957 | 7101.56 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2212.291 | 0 | 0
February | 85528400000 | 44027.686 | 25-FEB-19:10 | 9181.105 | 24042.957 | 7101.56 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2218.571 | 0 | 0
March | 95017300000 | 49848.295 | 30-MAR-17:10 | 9181.105 | 24042.957 | 7101.56 | 0 | 7513.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2008.818 | 0 | 0
April | 92161500000 | 52097.922 | 24-APR-11:00 | 9181.105 | 24042.957 | 7101.56 | 0 | 9707.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2064.853 | 0 | 0
May | 97834500000 | 57954.221 | 23-MAY-17:10 | 9181.105 | 24042.957 | 7101.56 | 0 | 15601.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027.384 | 0 | 0
June | 100528000000 | 63426.243 | 28-JUN-11:00 | 9181.105 | 24042.957 | 7101.56 | 0 | 21026.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2074.269 | 0 | 0
July | 113902000000 | 64777.716 | 19-JUL-12:00 | 9181.105 | 24042.957 | 7101.56 | 0 | 22324.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2127.665 | 0 | 0
August | 110266000000 | 65129.811 | 30-AUG-11:00 | 9181.105 | 24042.957 | 7101.56 | 0 | 22710.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2093.379 | 0 | 0
September | 99092900000 | 60447.286 | 01-SEP-17:10 | 9181.105 | 24042.957 | 7101.56 | 0 | 18085.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2035.82 | 0 | 0
October | 96751900000 | 55889.129 | 05-OCT-12:00 | 9181.105 | 24042.957 | 7101.56 | 0 | 13463.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2099.978 | 0 | 0
November | 91713700000 | 47294.273 | 10-NOV-13:00 | 9181.105 | 24042.957 | 7101.56 | 0 | 4878.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2090.506 | 0 | 0
December | 94853800000 | 44023.091 | 21-DEC-19:10 | 9181.105 | 24042.957 | 7101.56 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2213.975 | 0 | 0
Annual Sum or Average | 1172450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 85528400000 | 44021.406 |  | 9181.105 | 24042.957 | 7101.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2008.818 | 0 | 0
Maximum of Months | 113902000000 | 65129.811 |  | 9181.105 | 24042.957 | 7101.56 | 0 | 22710.809 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2218.571 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12219.29 | 14600.02 | 0 | 26819.31
Cost per Total Building Area ($/m2) | 23.91 | 28.56 | 0 | 52.47
Cost per Net Conditioned Building Area ($/m2) | 23.91 | 28.56 | 0 | 52.47

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3685.19 | 7209.56 | 7209.56
Net Site Energy | 3685.19 | 7209.56 | 7209.56
Total Source Energy | 6800.47 | 13304.17 | 13304.17
Net Source Energy | 6800.47 | 13304.17 | 13304.17
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1055.67 | 0 | 0 | 0 | 0
Cooling | 78.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 180.69 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 244.22 | 0 | 0 | 0 | 1375.88
Refrigeration | 63.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1183.9 | 2501.3 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74207.74 | 50170.6 | 24037.13 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70317.36 | 47540.39 | 22776.97 | 0.68 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 69465.76 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 65823.99 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.99 | 3268.13 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39258.3179 | 54.5937 | 61.9137 | 0 | 0.0005 | 40635.8124 | 15399.5731
February | 34148.9616 | 48.0576 | 55.709 | 0 | 0.0004 | 36567.4543 | 13449.7644
March | 34270.9769 | 49.9489 | 61.5071 | 0 | 0.0005 | 40384.9588 | 13662.1843
April | 29568.8143 | 45.1041 | 59.6078 | 0 | 0.0005 | 39150.2407 | 11979.6391
May | 29645.6374 | 47.2703 | 66.4348 | 0 | 0.0005 | 43645.4318 | 12206.6292
June | 29988.4371 | 48.9805 | 70.9919 | 0 | 0.0005 | 46645.0045 | 12459.0022
July | 32392.9659 | 53.3577 | 78.1488 | 0 | 0.0006 | 51349.5538 | 13500.9851
August | 32005.9515 | 52.6746 | 77.0665 | 0 | 0.0006 | 50638.1696 | 13335.3185
September | 27425.8434 | 43.9418 | 62.1473 | 0 | 0.0005 | 40829.7348 | 11312.7932
October | 30376.582 | 46.5631 | 61.9748 | 0 | 0.0005 | 40706.1383 | 12328.5851
November | 32955.6516 | 48.1662 | 59.5839 | 0 | 0.0005 | 39123.0316 | 13150.6694
December | 37789.7079 | 53.2119 | 61.7482 | 0 | 0.0005 | 40531.7935 | 14886.6243
Annual Sum or Average | 389827.8475 | 591.8703 | 776.8336 | 0 | 0.0059 | 510207.3241 | 157671.7679
Minimum of Months | 27425.8434 | 43.9418 | 55.709 | 0 | 0.0004 | 36567.4543 | 11312.7932
Maximum of Months | 39258.3179 | 54.5937 | 78.1488 | 0 | 0.0006 | 51349.5538 | 15399.5731
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94292300000 | 43654.088 | 28-JAN-19:19 | 9181.105 | 24042.957 | 6699.646 | 0 | 143.401 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2103.486 | 0 | 0
February | 84852000000 | 43583.939 | 27-FEB-19:10 | 9181.105 | 24042.957 | 6699.646 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2176.738 | 0 | 0
March | 93710300000 | 43651.663 | 25-MAR-18:00 | 9181.105 | 24042.957 | 6699.646 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2244.462 | 0 | 0
April | 90845200000 | 52664.309 | 01-APR-17:10 | 9181.105 | 24042.957 | 6699.646 | 0 | 10674.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2066.19 | 0 | 0
May | 101276000000 | 73610.494 | 27-MAY-17:19 | 9181.105 | 24042.957 | 6699.646 | 0 | 31612.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2074.315 | 0 | 0
June | 108236000000 | 75584.493 | 29-JUN-17:19 | 9181.105 | 24042.957 | 6699.646 | 0 | 33559.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2101.038 | 0 | 0
July | 119153000000 | 78636.352 | 13-JUL-17:00 | 9181.105 | 24042.957 | 6699.646 | 0 | 36575.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.543 | 0 | 0
August | 117502000000 | 77260.551 | 25-AUG-17:19 | 9181.105 | 24042.957 | 6699.646 | 0 | 35199.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2137.212 | 0 | 0
September | 94742300000 | 63790.604 | 14-SEP-11:00 | 9181.105 | 24042.957 | 6699.646 | 0 | 21751.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.825 | 0 | 0
October | 94455500000 | 56258.589 | 08-OCT-14:00 | 7140.86 | 24042.957 | 6699.646 | 0 | 16295.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2079.588 | 0 | 0
November | 90782000000 | 43637.37 | 02-NOV-19:10 | 9181.105 | 24042.957 | 6699.646 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2230.169 | 0 | 0
December | 94051000000 | 43622.963 | 05-DEC-18:30 | 9181.105 | 24042.957 | 6699.646 | 0 | 286.66 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 1929.103 | 0 | 0
Annual Sum or Average | 1183900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84852000000 | 43583.939 |  | 7140.86 | 24042.957 | 6699.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1929.103 | 0 | 0
Maximum of Months | 119153000000 | 78636.352 |  | 9181.105 | 24042.957 | 6699.646 | 0 | 36575.1 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2244.462 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17117.49 | 19868.14 | 0 | 36985.63
Cost per Total Building Area ($/m2) | 33.49 | 38.87 | 0 | 72.36
Cost per Net Conditioned Building Area ($/m2) | 33.49 | 38.87 | 0 | 72.36

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3499.8 | 6846.87 | 6846.87
Net Site Energy | 3499.8 | 6846.87 | 6846.87
Total Source Energy | 6546.2 | 12806.73 | 12806.73
Net Source Energy | 6546.2 | 12806.73 | 12806.73
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 908.14 | 0 | 0 | 0 | 0
Cooling | 33.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 184.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 247.46 | 0 | 0 | 0 | 1375.88
Refrigeration | 64.03 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1142.79 | 2357.01 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.402 | 0.495 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 52702.64 | 42091.24 | 10611.4 | 0.8 | 3.47
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 67439.63 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 59981.61 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.18 | 3481.85 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37993.4336 | 53.8546 | 70.2164 | 0 | 0.0005 | 1663860 | 15021.7466
February | 33385.8907 | 47.7748 | 63.333 | 0 | 0.0005 | 1500850 | 13243.6459
March | 34178.9105 | 50.3368 | 69.9987 | 0 | 0.0005 | 1659150 | 13696.1785
April | 31540.0679 | 47.2216 | 67.3832 | 0 | 0.0005 | 1597320 | 12713.2826
May | 30714.3976 | 47.2427 | 70.1664 | 0 | 0.0005 | 1663560 | 12502.0085
June | 30075.1007 | 47.4222 | 72.9113 | 0 | 0.0005 | 1728860 | 12354.1935
July | 31648.6328 | 50.5913 | 79.2138 | 0 | 0.0006 | 1878430 | 13067.0585
August | 31008.4466 | 49.3418 | 76.7937 | 0 | 0.0005 | 1821000 | 12780.8833
September | 29472.3372 | 46.1183 | 70.1717 | 0 | 0.0005 | 1663840 | 12072.4234
October | 31704.4382 | 48.1083 | 70.0514 | 0 | 0.0005 | 1660700 | 12841.4687
November | 33478.5227 | 49.0901 | 67.786 | 0 | 0.0005 | 1606660 | 13394.7174
December | 37413.5399 | 53.3289 | 70.216 | 0 | 0.0005 | 1663920 | 14821.1042
Annual Sum or Average | 392613.7183 | 590.4313 | 848.2417 | 0 | 0.0061 | 20108100 | 158508.7112
Minimum of Months | 29472.3372 | 46.1183 | 63.333 | 0 | 0.0005 | 1500850 | 12072.4234
Maximum of Months | 37993.4336 | 53.8546 | 79.2138 | 0 | 0.0006 | 1878430 | 15021.7466
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94560900000 | 43819.956 | 14-JAN-19:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2199.037 | 0 | 0
February | 85297100000 | 43850.21 | 02-FEB-19:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2229.292 | 0 | 0
March | 94293400000 | 46010.615 | 30-MAR-17:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 3863.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2010.08 | 0 | 0
April | 90779500000 | 44883.066 | 06-APR-17:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 2735.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2009.72 | 0 | 0
May | 94543900000 | 54518.519 | 16-MAY-17:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 12353.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2027.861 | 0 | 0
June | 98255300000 | 63529.22 | 30-JUN-12:00 | 9181.105 | 24042.957 | 6913.364 | 0 | 21257.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2134.376 | 0 | 0
July | 106756000000 | 63493.874 | 21-JUL-17:19 | 9181.105 | 24042.957 | 6913.364 | 0 | 21324.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2031.956 | 0 | 0
August | 103492000000 | 62334.719 | 09-AUG-17:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 20162.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2034.421 | 0 | 0
September | 94559700000 | 59580.254 | 01-SEP-17:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 17406.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2036.627 | 0 | 0
October | 94381700000 | 50353.245 | 06-OCT-17:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 8197.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018.018 | 0 | 0
November | 91310100000 | 43830.53 | 20-NOV-19:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2209.612 | 0 | 0
December | 94564400000 | 43817.74 | 02-DEC-19:10 | 9181.105 | 24042.957 | 6913.364 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2196.821 | 0 | 0
Annual Sum or Average | 1142790000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 85297100000 | 43817.74 |  | 9181.105 | 24042.957 | 6913.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2009.72 | 0 | 0
Maximum of Months | 106756000000 | 63529.22 |  | 9181.105 | 24042.957 | 6913.364 | 0 | 21324.492 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2229.292 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21397.05 | 20384.14 | 0 | 41781.18
Cost per Total Building Area ($/m2) | 41.86 | 39.88 | 0 | 81.74
Cost per Net Conditioned Building Area ($/m2) | 41.86 | 39.88 | 0 | 81.74

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3901.48 | 7632.71 | 7632.71
Net Site Energy | 3901.48 | 7632.71 | 7632.71
Total Source Energy | 6895.3 | 13489.69 | 13489.69
Net Source Energy | 6895.3 | 13489.69 | 13489.69
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1302.82 | 0 | 0 | 0 | 0
Cooling | 24.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 174.76 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 273.64 | 0 | 0 | 0 | 1375.88
Refrigeration | 63.16 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1123.62 | 2777.87 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 3.18 | 0.501 | 0.49 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 3.18 | 0.501 | 0.49 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 3.18 | 0.501 | 0.49 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 3.18 | 0.501 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 70309.64 | 47535.17 | 22774.47 | 0.68 | 3.12
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54955.8 | 40919.55 | 14036.25 | 0.74 | 3.34
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 67368.47 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 67375.87 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.46 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39230.6572 | 54.476 | 61.6119 | 0 | 0.0005 | 40437.1844 | 15381.1442
February | 34871.3556 | 48.6782 | 55.5978 | 0 | 0.0004 | 36491.8345 | 13696.4263
March | 36502.8075 | 51.9292 | 61.3692 | 0 | 0.0005 | 40286.5957 | 14430.2746
April | 31897.4794 | 47.0242 | 58.9882 | 0 | 0.0005 | 38734.4002 | 12767.092
May | 29853.6936 | 45.8182 | 61.0926 | 0 | 0.0005 | 40126.9937 | 12121.7855
June | 27544.8145 | 43.8415 | 61.4695 | 0 | 0.0005 | 40383.0071 | 11334.0556
July | 29714.2174 | 48.08 | 68.8689 | 0 | 0.0005 | 45248.0086 | 12301.8105
August | 29192.9333 | 46.7855 | 66.1922 | 0 | 0.0005 | 43487.211 | 12042.8868
September | 28170.1862 | 43.8822 | 59.7565 | 0 | 0.0005 | 39252.9321 | 11500.1277
October | 31539.9139 | 47.4197 | 61.3312 | 0 | 0.0005 | 40278.42 | 12712.1663
November | 33934.1716 | 49.0109 | 59.4469 | 0 | 0.0005 | 39029.55 | 13485.1846
December | 38571.3775 | 53.894 | 61.6624 | 0 | 0.0005 | 40472.7002 | 15154.5393
Annual Sum or Average | 391023.6076 | 580.8397 | 737.3875 | 0 | 0.0057 | 484228.8376 | 156927.4933
Minimum of Months | 27544.8145 | 43.8415 | 55.5978 | 0 | 0.0004 | 36491.8345 | 11334.0556
Maximum of Months | 39230.6572 | 54.476 | 68.8689 | 0 | 0.0005 | 45248.0086 | 15381.1442
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 93831400000 | 43376.811 | 21-JAN-19:10 | 9181.105 | 24042.957 | 6527.972 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2141.284 | 0 | 0
February | 84676600000 | 43416.572 | 23-FEB-19:10 | 9181.105 | 24042.957 | 6527.972 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2181.045 | 0 | 0
March | 93482000000 | 43432.088 | 30-MAR-18:30 | 9181.105 | 24042.957 | 6527.972 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2196.56 | 0 | 0
April | 89880300000 | 43451.48 | 08-APR-18:49 | 9181.105 | 24042.957 | 6527.972 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2215.952 | 0 | 0
May | 93111700000 | 50631.036 | 31-MAY-17:10 | 9181.105 | 24042.957 | 6527.972 | 0 | 8861.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2017.784 | 0 | 0
June | 93705700000 | 65036.341 | 14-JUN-17:19 | 9181.105 | 24042.957 | 6527.972 | 0 | 23213.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2071.167 | 0 | 0
July | 104995000000 | 69670.453 | 06-JUL-17:00 | 9181.105 | 24042.957 | 6527.972 | 0 | 27845.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2073.19 | 0 | 0
August | 100909000000 | 67620.583 | 11-AUG-17:49 | 9181.105 | 24042.957 | 6527.972 | 0 | 25792.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2076.482 | 0 | 0
September | 91083500000 | 55400.694 | 07-SEP-14:00 | 9181.105 | 24042.957 | 6527.972 | 0 | 13512.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2135.879 | 0 | 0
October | 93463000000 | 51765.119 | 07-OCT-14:00 | 8160.982 | 24042.957 | 6527.972 | 0 | 10938.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2094.482 | 0 | 0
November | 90565100000 | 43468.649 | 08-NOV-19:10 | 9181.105 | 24042.957 | 6527.972 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2233.121 | 0 | 0
December | 93913900000 | 43430.552 | 04-DEC-18:30 | 9181.105 | 24042.957 | 6527.972 | 0 | 264.592 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 1930.432 | 0 | 0
Annual Sum or Average | 1123620000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84676600000 | 43376.811 |  | 8160.982 | 24042.957 | 6527.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1930.432 | 0 | 0
Maximum of Months | 104995000000 | 69670.453 |  | 9181.105 | 24042.957 | 6527.972 | 0 | 27845.227 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2233.121 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15816.35 | 22048.81 | 0 | 37865.16
Cost per Total Building Area ($/m2) | 30.94 | 43.14 | 0 | 74.08
Cost per Net Conditioned Building Area ($/m2) | 30.94 | 43.14 | 0 | 74.08

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4597.86 | 8995.06 | 8995.06
Net Site Energy | 4597.86 | 8995.06 | 8995.06
Total Source Energy | 7752.7 | 15167.08 | 15167.08
Net Source Energy | 7752.7 | 15167.08 | 15167.08
Area [m2]
Total Building Area | 511.15
Net Conditioned Building Area | 511.15
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1985.66 | 0 | 0 | 0 | 0
Cooling | 7.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 185.61 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 652.32 | 1201.41 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 171.51 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 309.23 | 0 | 0 | 0 | 1375.88
Refrigeration | 61.58 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1101.55 | 3496.31 | 0 | 0 | 0 | 1375.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
DINING | 371.75 | Yes | 1133.39 | 1 | 169.19 | 47.17 | 22.6 | 1.39 | 60.26
KITCHEN | 139.41 | Yes | 425.02 | 1 | 106.53 | 0 | 12.91 | 18.52 | 2184.78
ATTIC | 511.15 | No | 856.26 | 1 | 0 | 0 | 0 |  | 0
Total | 1022.31 |  | 2414.66 |  | 275.72 | 47.17 | 9.9786 | 3.73 | 319.8368
Conditioned Total | 511.15 |  | 1558.4 |  | 275.72 | 47.17 | 19.9573 | 1.86 | 639.6737
Unconditioned Total | 511.15 |  | 856.26 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
DINING_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 50.13 | 90 | 90 | E
DINING_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 68.93 | 180 | 90 | S
DINING_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 50.13 | 270 | 90 | W
DINING_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 371.75 | 0 | 180
KITCHEN_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 68.93 | 0 | 90 | N
KITCHEN_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 18.8 | 90 | 90 | E
KITCHEN_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 18.8 | 270 | 90 | W
KITCHEN_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 139.41 | 0 | 180
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 180 | 45
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 60.26 | 0 | 45
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 270 | 18.44
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 224.5 | 90 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_WALL_EAST_WINDOW | WINDOW_EAST | 13.94 | 13.94 | 2.58 | 0.504 | 0.49 | No | DINING_WALL_EAST | 90 | E
DINING_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 19.3 | 19.3 | 2.58 | 0.504 | 0.49 | No | DINING_WALL_SOUTH | 180 | S
DINING_WALL_WEST_WINDOW | WINDOW_WEST | 13.94 | 13.94 | 2.58 | 0.504 | 0.49 | No | DINING_WALL_WEST | 270 | W
Total or Average |  |  | 47.17 | 2.58 | 0.504 | 0.49
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 47.17 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44183.93 | 35287.73 | 8896.2 | 0.8 | 3.47
PSZ-AC_2:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46874.36 | 37436.45 | 9437.91 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_1:1_HEATC | Coil:Heating:Gas | 78645.59 | 0.78
PSZ-AC_2:2_HEATC | Coil:Heating:Gas | 83434.45 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.67 | 333.46 | 1 | Zone Exhaust Fans
KITCHEN EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0.01 | 1.25 | 1 | Zone Exhaust Fans
PSZ-AC_1:1_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.67 | 2919.05 | 1 | Fan Energy
PSZ-AC_2:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.83 | 3096.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.2 | 845000 | 0.8 | 3.42 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42528.2584 | 44.9789 | 133.461 | 0 | 0.0005 | 26761.7486 | 15699.8412
February | 37678.4135 | 39.9294 | 119.9102 | 0 | 0.0004 | 24045.0752 | 13921.7353
March | 38050.9726 | 40.8448 | 131.9873 | 0 | 0.0005 | 26470.3664 | 14139.5037
April | 32340.3217 | 35.3928 | 126.3634 | 0 | 0.0005 | 25346.7211 | 12121.7979
May | 27783.6041 | 31.4274 | 129.9278 | 0 | 0.0005 | 26067.3289 | 10571.029
June | 25383.6196 | 29.1798 | 128.4766 | 0 | 0.0005 | 25778.3375 | 9729.7691
July | 26113.5605 | 30.1722 | 135.3793 | 0 | 0.0005 | 27163.9995 | 10033.1602
August | 26473.9146 | 30.3475 | 132.2044 | 0 | 0.0005 | 26525.9293 | 10134.5176
September | 28144.554 | 31.6049 | 126.7858 | 0 | 0.0005 | 25435.8819 | 10672.8351
October | 34044.9562 | 37.1963 | 131.7251 | 0 | 0.0005 | 26421.8586 | 12751.1754
November | 38034.3423 | 40.6695 | 128.6367 | 0 | 0.0005 | 25797.4255 | 14109.1032
December | 41264.6224 | 43.8421 | 133.6715 | 0 | 0.0005 | 26805.3203 | 15264.0705
Annual Sum or Average | 397841.1399 | 435.5856 | 1558.5292 | 0 | 0.0057 | 312619.9927 | 149148.5382
Minimum of Months | 25383.6196 | 29.1798 | 119.9102 | 0 | 0.0004 | 24045.0752 | 9729.7691
Maximum of Months | 42528.2584 | 44.9789 | 135.3793 | 0 | 0.0005 | 27163.9995 | 15699.8412
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94297900000 | 44276.641 | 03-JAN-11:09 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 3218.519 | 0 | 0
February | 84725400000 | 43206.037 | 27-FEB-19:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2147.915 | 0 | 0
March | 93271200000 | 43222.24 | 09-MAR-19:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2164.119 | 0 | 0
April | 89311900000 | 43173.834 | 05-APR-19:49 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2115.712 | 0 | 0
May | 91851100000 | 44808.774 | 30-MAY-17:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 3207.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026.246 | 0 | 0
June | 90832800000 | 55828.528 | 20-JUN-17:00 | 9181.105 | 24042.957 | 6350.567 | 0 | 14214.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2039.268 | 0 | 0
July | 95715300000 | 58137.567 | 29-JUL-18:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 16307.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2255.01 | 0 | 0
August | 93467000000 | 55154.455 | 15-AUG-17:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 13529.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2050.731 | 0 | 0
September | 89626100000 | 43273.906 | 20-SEP-18:00 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2215.784 | 0 | 0
October | 93100300000 | 43260.809 | 02-OCT-18:19 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2202.687 | 0 | 0
November | 90900000000 | 43212.964 | 13-NOV-19:10 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 2154.842 | 0 | 0
December | 94451400000 | 44392.474 | 18-DEC-11:09 | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 3334.353 | 0 | 0
Annual Sum or Average | 1101550000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 84725400000 | 43173.834 |  | 9181.105 | 24042.957 | 6350.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2026.246 | 0 | 0
Maximum of Months | 95715300000 | 58137.567 |  | 9181.105 | 24042.957 | 6350.567 | 0 | 16307.928 | 1483.493 | 0 | 0 | 0 | 0 | 0 | 0 | 3334.353 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26336.64 | 14628.38 | 0 | 40965.02
Cost per Total Building Area ($/m2) | 51.52 | 28.62 | 0 | 80.14
Cost per Net Conditioned Building Area ($/m2) | 51.52 | 28.62 | 0 | 80.14

## Picture
DOE Commercial Building Benchmark - Sit Down Restaurant

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 14.55 | 53.9 | 2810.5
|  |  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 13.65
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 11.15
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 6.25 | 25 | 1303.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 6.25
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 6.25
FF_GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.05 | 3.05 | 18.3 | 954.21
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.05 | 3.05
Rest_GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | 8.4 | 56.8 | 2961.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | 8.25
|  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | 6.55
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35 | 1825
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5 | 101.5 | 5292.5
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 7.75 | 52.65 | 2745.32
|  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 7.45
|  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 6.45
Hours_of_operation | On/Off | Through 12/31 | Weekday, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 80 | 4171.43
|  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | Weekday, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 80 | 4171.43
|  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Kitchen_Exhaust_SCH | On/Off | Through 12/31 | Weekday, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 72 | 3754.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477 | 3339 | 174105
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 606 | 4248 | 221502.86
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 606
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 612
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4 | 3096.8 | 161476
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
|  |  | Sun, Hol, Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640 | 4480 | 233600
|  |  | Sat | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 133 | 6935
|  |  | Sat | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_SDKitch_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.08 | 7.56 | 394.2
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.08
|  |  | WinterDesign | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.44
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 1.08
MinOA_FFKitch_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 11.7 | 81.9 | 4270.5
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 11.7
|  |  | WinterDesign | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 15.6
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 11.7
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720