## BuildingSummary
Building Summary Hospital new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Hospital
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, inpatient
Form
| Total Floor Area (m2) | 22422.1768 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3142
| Number of Floors | 5 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.1334
| East | 0.121
| North | 0.117
| West | 0.2315
| Total | 0.1461
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures and zone summary
| Floor to Ceiling Height (m) | 4.27
| Floor to Floor Height (m) | 4.27
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 5184.32
| Net Dimensions - Total Area (m2) | 4338.78
| Wall to Skin Ratio | 0.41902
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3739.134
| Net Dimensions - Total Area (m2) | 3739.134
| Roof to Skin Ratio | 0.58098
Window Dimensions (m2)
| South | 220.72
| East | 144.86
| North | 186.18
| West | 293.66
| Total Area (m2) | 845.42
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab
| Dimensions - Total Area (m2) | 3739.134
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15534.17
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 44872.35
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.11 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Boiler | 2003 CBECS
| Cooling Type | Chiller, water cooled | 2003 CBECS
| Fan Control | CAV, VAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 4037.86

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 10.76 | 8.07 |  |  | 10 | 0 | 1006.2497 |  | 0
ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
ER_Exam2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.1785
ER_Exam4_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
ER_Exam5_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 13.935 | 2 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.94 | 1 | 11.836 | 8.07 |  |  | 10 | 0 | 10 |  | 0.23798
Lobby_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.78 | 62.63 | 18.5806 | 79.3735 | 13.988 | 8.07 |  |  | 10 | 0 | 793.7354 |  | 0.070849
Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.07 | 0 | 92.9031 | 6.125 | 10.76 | 0 |  |  | 0 | 0.25 | 142.2575 |  | 0.040809
ER_NurseStat_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.58 | 30.42 | 46.4516 | 26.6 | 10.76 | 8.07 |  |  |  |  | 2929.97 |  | 0.02282
OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.05 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.29758
OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.11903
OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.17855
OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 23.672 | 53.8 |  | 22.7124 |  |  | 793.0845 |  | 0
IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 10.45 | 2 | 8.608 | 32.28 |  |  |  |  | 49.5596 |  | 0.23803
IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 13.935 | 2 | 8.608 | 32.28 |  |  |  |  | 66.0874 |  | 0.41656
IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 10.45 | 2 | 8.608 | 32.28 |  |  |  |  | 49.5596 |  | 0.23803
ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.68 | 25.03 | 46.4516 | 13.3033 | 8.608 | 32.28 |  |  |  |  | 1465.3525 |  | 0.088583
ICU_NurseSat_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 10.76 | 8.07 |  |  | 10 | 0 | 359.9287 |  | 0
Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.07 | 0 | 92.9031 | 6.125 | 10.76 | 0 |  |  | 0 | 0.25 | 142.2575 |  | 0.040809
OR_NurseSat_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.14 | 35.76 | 18.5806 | 54.4998 | 10.76 | 8.07 |  |  | 10 | 0 | 544.9978 |  | 0.045864
PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 4.6452 | 104.9997 | 9.684 | 16.14 |  | 3.7854 | 8 | 0 | 839.9975 |  | 0
PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
NurseSat_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 18.5806 | 48.7497 | 10.76 | 8.07 |  |  | 10 | 0 | 487.497 |  | 0
Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 3.7161 | 71.2489 | 15.064 | 32.28 |  | 7.5708 | 10 | 0 | 712.4895 |  | 0
Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 23.2267 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 13.9333 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 4.304 | 53.8 |  | 3.7854 | 8 | 0 | 209.9994 |  | 0
PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 13.4733 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.58 | 1.5 | 7.532 | 8.07 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
NurseSat_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 18.5806 | 48.7497 | 10.76 | 8.07 |  |  | 10 | 0 | 487.497 |  | 0
Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 3.7161 | 71.2489 | 15.064 | 32.28 |  | 7.5708 | 10 | 0 | 712.4895 |  | 0
Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.67 | 35.76 | 1.3935 | 499.9995 | 9.684 | 2.69 |  |  | 10 | 0 | 4999.9952 |  | 0.33831
NurseSat_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.08 | 0 | 18.5806 | 55.9999 | 10.76 | 8.07 |  |  | 10 | 0 | 559.9995 |  | 0.28049
Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2 | 0 | 23.2258 | 39.9999 | 12.912 | 80.7001 | 457.3006 | 567.81 | 8 | 0 | 319.9996 | 3775.576 | 0.32641
Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.56 | 17.98 | 18.5806 | 3.7512 | 11.836 | 8.07 |  |  | 10 | 0 | 37.5122 |  | 0.51678
Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 18.5806 | 3.7501 | 11.836 | 8.07 |  |  | 10 | 0 | 37.5014 |  | 0.37399
Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.55 | 17.98 | 18.5806 | 3.7501 | 11.836 | 8.07 |  |  | 10 | 0 | 37.5014 |  | 0.51682
Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.94 | 1 | 11.836 | 8.07 |  |  | 10 | 0 | 10 |  | 0.49297
Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.06 | 0 | 92.9031 | 5.4 | 10.76 | 0 |  |  | 0 | 0.25 | 125.42 |  | 0.29466
Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.32 | 845.54 |  | 1572.9423 |  |  |  | 1052.3412
4338.78
Data Source |  |  | 1.3142 | 8923.454 |  |  |  | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
|  |  | 3739.134 | 0.41902 | 0.58098
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.692 | 1.9531 | 1.9531 | 1.9531 | 1.9531 | 2.2026 | 2.4752
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.391 | 0.391 | 0.402 | 0.402 | 0.402 | 0.61 | 0.402 | 0.402 | 0.402 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.39 | 0.39 | 0.495 | 0.495 | 0.495 | 0.61 | 0.495 | 0.495 | 0.495 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
| R-value (m2·K / W) | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 2643.4806 | 2581.1908 | 2083.8689 | 2420.0742 | 1629 | 1855.5942 | 1571.4468 | 2408.9105 | 1468.4289 | 1657.9639 | 2419.9066 | 1495.6699 | 2292.0454 | 1475.0488 | 1969.9432 | 1298.8668
Heating (kW)
| HEATSYS1 BOILER | 3845.1393 | 4337.5966 | 4263.2693 | 4372.2517 | 3906.7911 | 4219.9288 | 4190.5536 | 4557.9151 | 4029.2059 | 4240.7068 | 4906.6943 | 4351.6232 | 5074.718 | 4781.1584 | 5031.723 | 5632.4677
HVAC Efficiency
| Air Conditioning (COP) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
| Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_ER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_OR_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_ICU_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_PATRMS_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 16.39 | 17.15 | 18.18 | 17.26 | 16.46 | 18.23 | 17.04 | 16.55 | 19.02 | 16.3 | 17.02 | 19.34 | 17.2 | 18.69 | 17.11 | 16.93
| CAV_ER_FAN | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55 | 5.55
| CAV_OR_FAN | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9
| CAV_ICU_FAN | 6.3 | 6.61 | 6.91 | 6.59 | 6.41 | 6.81 | 6.65 | 6.52 | 6.8 | 6.38 | 6.7 | 6.94 | 6.7 | 6.84 | 6.64 | 6.56
| CAV_PATRMS_FAN | 13.57 | 14.78 | 16.91 | 14.76 | 14.11 | 16.25 | 16.24 | 14.47 | 15.91 | 14.27 | 15.46 | 16.95 | 15.75 | 16.88 | 15.33 | 15.89
| VAV_2_FAN | 50.49 | 52.32 | 56.85 | 53.17 | 49.66 | 57.61 | 49.17 | 51.24 | 61.57 | 49.7 | 51.87 | 60.75 | 51.96 | 57.64 | 51.79 | 48.63
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.075159 | 0.098029 | 0.068732 | 0.098585 | 0.044536 | 0.088456 | 0.13224 | 0.05612 | 0.036969 | 0.066596 | 0.096461 | 0.03697 | 0.053374 | 0.070423 | 0.053771 | 0.089102
| Total Cost ($/m2) | 22.08 | 27.36 | 16.99 | 25.12 | 10.19 | 20.38 | 27.53 | 13.82 | 7.79 | 13.29 | 21.29 | 7.59 | 11.59 | 13.99 | 10.75 | 16.85
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011455 | 0.0081874 | 0.008574 | 0.01075 | 0.0084126 | 0.0081238 | 0.0084134 | 0.010066 | 0.0071529 | 0.0082967 | 0.0088575 | 0.0071557 | 0.0079571 | 0.0086466 | 0.0079505 | 0.0041777
| Total Cost ($/m2) | 8.03 | 6.57 | 6.46 | 9.02 | 6.01 | 6.04 | 7.47 | 9.64 | 5.23 | 7.6 | 9.3 | 6.06 | 9.1 | 8.64 | 9.72 | 6.6
Total Utility Costs
| Cost Intensity ($/m2) | 30.11 | 33.93 | 23.45 | 34.15 | 16.2 | 26.42 | 35.01 | 23.47 | 13.02 | 20.89 | 30.59 | 13.64 | 20.69 | 22.63 | 20.47 | 23.45
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 2063266.6667 | 1748050 | 1139633.3333 | 1276408.3333 | 885866.6667 | 853113.8889 | 473255.5556 | 1133075 | 529675 | 362777.7778 | 652311.1111 | 412869.4444 | 593758.3333 | 303722.2222 | 315644.4444 | 181841.6667
| Interior Lighting | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111 | 1119436.1111
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111 | 1944536.1111
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 698075 | 721452.7778 | 769380.5556 | 722130.5556 | 702955.5556 | 760425 | 735813.8889 | 710425 | 764250 | 701311.1111 | 729655.5556 | 779713.8889 | 734286.1111 | 767652.7778 | 726238.8889 | 726802.7778
| Pumps | 420991.6667 | 399141.6667 | 307619.4444 | 359816.6667 | 250244.4444 | 267072.2222 | 201886.1111 | 349263.8889 | 207280.5556 | 190519.4444 | 313358.3333 | 202352.7778 | 299980.5556 | 192922.2222 | 243744.4444 | 170975
| Heat Rejection | 282950 | 267894.4444 | 202841.6667 | 236050 | 170025 | 159986.1111 | 139705.5556 | 211408.3333 | 98177.7778 | 101113.8889 | 133338.8889 | 84066.6667 | 120105.5556 | 68913.8889 | 76844.4444 | 41675
| Humidification | 16.6667 | 302.7778 | 2561.1111 | 1005.5556 | 775 | 6550 | 347.2222 | 1600 | 6511.1111 | 958.3333 | 2772.2222 | 6000 | 3052.7778 | 5219.4444 | 3755.5556 | 4566.6667
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 58761.1111 | 56677.7778 | 57163.8889 | 54902.7778 | 55113.8889 | 55875 | 53441.6667 | 53583.3333 | 53819.4444 | 52488.8889 | 52727.7778 | 52736.1111 | 52355.5556 | 51755.5556 | 51058.3333 | 50383.3333
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 6588038.8889 | 6257494.4444 | 5543177.7778 | 5714286.1111 | 5128952.7778 | 5166997.2222 | 4668425 | 5523330.5556 | 4723686.1111 | 4473144.4444 | 4948136.1111 | 4601713.8889 | 4867511.1111 | 4454158.3333 | 4481261.1111 | 4240216.6667
Gas (MJ)
| Heating | 3673472.2222 | 4281536.1111 | 3987238.8889 | 4485558.3333 | 3711383.3333 | 3909230.5556 | 4773755.5556 | 5205455.5556 | 3795822.2222 | 4936450 | 5760969.4444 | 4494736.1111 | 6330175 | 5430100 | 6801108.3333 | 8995805.5556
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000 | 566000
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 126833.3333 | 152127.7778 | 137580.5556 | 176513.8889 | 171786.1111 | 155111.1111 | 192655.5556 | 195683.3333 | 192047.2222 | 205658.3333 | 212505.5556 | 211625 | 227041.6667 | 229686.1111 | 251025 | 280047.2222
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4366305.5556 | 4999663.8889 | 4690819.4444 | 5228072.2222 | 4449169.4444 | 4630338.8889 | 5532411.1111 | 5967138.8889 | 4553869.4444 | 5708108.3333 | 6539475 | 5272361.1111 | 7123219.4444 | 6225786.1111 | 7618133.3333 | 9841852.7778
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 39435640 | 1807390 | 1643120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 331.2675 | 280.658 | 182.9737 | 204.9336 | 142.2302 | 136.9716 | 75.9835 | 181.9207 | 85.0419 | 58.2457 | 104.7317 | 66.2882 | 95.3308 | 48.7641 | 50.6783 | 29.1956
| Interior Lighting (elec) | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309 | 179.7309
| Exterior Lighting (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (elec) | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048 | 312.2048
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 112.0793 | 115.8328 | 123.5278 | 115.9416 | 112.8629 | 122.0899 | 118.1385 | 114.0622 | 122.7041 | 112.5989 | 117.1498 | 125.1869 | 117.8932 | 123.2504 | 116.6012 | 116.6917
| Pumps (elec) | 67.5923 | 64.0841 | 49.3898 | 57.7703 | 40.178 | 42.8797 | 32.4138 | 56.076 | 33.2799 | 30.5888 | 50.3112 | 32.4887 | 48.1633 | 30.9746 | 39.1344 | 27.4509
| Heat Rejection (elec) | 45.429 | 43.0118 | 32.5672 | 37.899 | 27.2983 | 25.6866 | 22.4304 | 33.9426 | 15.7629 | 16.2343 | 21.4082 | 13.4973 | 19.2835 | 11.0645 | 12.3378 | 6.6911
| Humidification (elec) | 0.0026759 | 0.048612 | 0.4112 | 0.16145 | 0.12443 | 1.0516 | 0.055748 | 0.25689 | 1.0454 | 0.15387 | 0.44509 | 0.96333 | 0.49014 | 0.83801 | 0.60297 | 0.7332
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 9.4344 | 9.0999 | 9.1779 | 8.8149 | 8.8488 | 8.971 | 8.5803 | 8.6031 | 8.641 | 8.4273 | 8.4657 | 8.467 | 8.4059 | 8.3096 | 8.1977 | 8.0893
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1057.7418 | 1004.6713 | 889.9842 | 917.4565 | 823.4784 | 829.5866 | 749.5384 | 886.7977 | 758.4108 | 718.1852 | 794.4474 | 738.8276 | 781.5027 | 715.1368 | 719.4883 | 680.7875
Gas (MJ/m2)
| Heating (gas) | 589.7939 | 687.4215 | 640.1707 | 720.1783 | 595.8807 | 627.646 | 766.4497 | 835.7613 | 609.4378 | 792.5711 | 924.9517 | 721.6518 | 1016.3405 | 871.829 | 1091.9511 | 1444.3205
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741 | 90.8741
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.3637 | 24.4249 | 22.0892 | 28.3402 | 27.5811 | 24.9038 | 30.9318 | 31.4179 | 30.8341 | 33.0194 | 34.1188 | 33.9774 | 36.4526 | 36.8772 | 40.3033 | 44.9629
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 701.0317 | 802.7204 | 753.1339 | 839.3925 | 714.3359 | 743.4235 | 888.2556 | 958.0533 | 731.146 | 916.4646 | 1049.9446 | 846.5033 | 1143.6676 | 999.5803 | 1223.1285 | 1580.1575
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1758.7734 | 1807.3917 | 1643.1182 | 1756.849 | 1537.8142 | 1573.0105 | 1637.794 | 1844.8509 | 1489.5568 | 1634.6502 | 1844.392 | 1585.3313 | 1925.1703 | 1714.7172 | 1942.6168 | 2260.9449
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1072.3144 | 1047.2788 | 936.6327 | 939.8937 | 911.8526 | 894.6489 | 846.383 | 899.9257 | 841.6234 | 776.7034 | 784.1356 | 863.1006 | 738.6965 | 734.0385 | 733.6877 | 729.1592
| Feb | 1074.825 | 1009.8349 | 947.8757 | 930.6181 | 896.6612 | 909.7996 | 902.2314 | 898.5365 | 883.6702 | 848.03 | 790.3698 | 842.2186 | 739.0168 | 852.7928 | 737.6929 | 727.4489
| Mar | 1095.9339 | 1036.9094 | 972.7679 | 967.2276 | 903.5882 | 924.5702 | 865.8799 | 977.4623 | 887.6778 | 877.8791 | 932.5832 | 900.5122 | 884.4704 | 883.0955 | 736.1637 | 730.7551
| Apr | 1108.3842 | 1069.9671 | 976.1852 | 995.7764 | 933.6015 | 960.8684 | 899.7755 | 965.8914 | 913.4699 | 862.082 | 956.1314 | 908.2502 | 925.087 | 877.5596 | 872.7734 | 771.4784
| May | 1174.8484 | 1169.4594 | 996.8465 | 1047.5574 | 953.0275 | 976.0573 | 923.1705 | 1068.7257 | 924.7898 | 921.4523 | 1023.864 | 921.1048 | 1005.7195 | 902.9275 | 917.573 | 873.86
| Jun | 1237.5592 | 1161.3404 | 1072.502 | 1116.3604 | 950.0231 | 1020.7654 | 920.2431 | 1164.0074 | 949.0588 | 924.1448 | 1172.8592 | 945.3109 | 1121.4612 | 957.9144 | 1033.8099 | 910.5528
| Jul | 1204.7106 | 1249.9839 | 1114.2756 | 1146.4666 | 975.0756 | 1027.0378 | 941.6474 | 1200.834 | 951.1138 | 948.3134 | 1156.7217 | 970.7679 | 1152.3895 | 948.9659 | 1050.0024 | 908.184
| Aug | 1214.328 | 1211.4448 | 1102.4254 | 1145.384 | 1009.5833 | 1065.3163 | 936.7294 | 1216.8101 | 965.1137 | 944.3443 | 1201.1104 | 953.1624 | 1130.3656 | 937.1402 | 1038.1336 | 903.1336
| Sep | 1173.1762 | 1230.1098 | 1063.6553 | 1093.8511 | 961.0715 | 1003.0226 | 959.1328 | 1061.3169 | 932.754 | 949.9304 | 1046.2098 | 934.2841 | 1028.7322 | 921.1511 | 1007.0099 | 824.0992
| Oct | 1157.9677 | 1131.6614 | 1007.0995 | 1008.7398 | 946.8449 | 960.0581 | 913.9342 | 1022.1445 | 908.7794 | 885.6229 | 1004.7547 | 923.6017 | 934.4724 | 895.308 | 884.5217 | 792.4838
| Nov | 1115.4615 | 1080.1189 | 957.1782 | 951.6512 | 922.1628 | 911.4718 | 896.6096 | 984.6086 | 873.5727 | 868.2662 | 1011.768 | 887.063 | 905.128 | 827.5218 | 839.7418 | 724.4253
| Dec | 1070.2312 | 1044.0072 | 930.6726 | 948.8627 | 908.8631 | 908.7115 | 847.3388 | 870.5347 | 832.6145 | 742.5089 | 795.4132 | 832.6567 | 738.6037 | 736.6875 | 733.7341 | 727.7032
Time of Peak Electrical Demand
| Jan | 06-JAN-11:00 | 03-JAN-11:50 | 26-JAN-15:00 | 24-JAN-15:00 | 26-JAN-13:00 | 18-JAN-14:00 | 06-JAN-15:00 | 09-JAN-13:09 | 26-JAN-15:00 | 27-JAN-15:00 | 17-JAN-14:09 | 24-JAN-13:00 | 04-JAN-11:39 | 25-JAN-11:39 | 26-JAN-11:39 | 10-JAN-11:39
| Feb | 23-FEB-11:39 | 15-FEB-14:00 | 28-FEB-15:00 | 21-FEB-13:00 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-15:00 | 15-FEB-15:00 | 14-FEB-15:00 | 21-FEB-13:00 | 28-FEB-11:50 | 07-FEB-14:00 | 03-FEB-11:39 | 02-FEB-14:00 | 28-FEB-15:00 | 02-FEB-11:39
| Mar | 14-MAR-10:39 | 24-MAR-12:09 | 17-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 31-MAR-14:00 | 01-MAR-13:09 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 21-MAR-14:00 | 31-MAR-14:00
| Apr | 05-APR-12:00 | 10-APR-12:00 | 26-APR-14:00 | 13-APR-14:00 | 11-APR-13:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-14:00 | 21-APR-14:00 | 14-APR-14:00 | 03-APR-13:50 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 25-APR-14:00
| May | 19-MAY-14:00 | 18-MAY-14:09 | 19-MAY-14:00 | 31-MAY-14:00 | 30-MAY-13:30 | 31-MAY-14:00 | 25-MAY-12:09 | 31-MAY-14:00 | 19-MAY-14:00 | 05-MAY-14:00 | 30-MAY-09:00 | 23-MAY-14:00 | 31-MAY-12:20 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 29-JUN-14:00 | 30-JUN-12:00 | 08-JUN-14:00 | 28-JUN-13:00 | 27-JUN-14:00 | 15-JUN-12:00 | 30-JUN-14:00 | 29-JUN-14:00 | 28-JUN-12:00 | 08-JUN-12:00 | 30-JUN-10:09 | 29-JUN-14:00 | 30-JUN-12:00 | 14-JUN-14:00 | 21-JUN-14:00
| Jul | 13-JUL-14:00 | 18-JUL-12:50 | 18-JUL-14:00 | 03-JUL-12:09 | 20-JUL-14:00 | 11-JUL-14:00 | 03-JUL-12:00 | 25-JUL-10:39 | 25-JUL-14:09 | 24-JUL-14:00 | 13-JUL-12:00 | 25-JUL-13:20 | 13-JUL-14:00 | 21-JUL-14:00 | 31-JUL-14:00 | 19-JUL-12:00
| Aug | 21-AUG-14:30 | 03-AUG-14:00 | 11-AUG-14:00 | 17-AUG-14:00 | 09-AUG-14:00 | 07-AUG-14:20 | 15-AUG-12:09 | 09-AUG-14:00 | 01-AUG-14:00 | 18-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-14:00 | 09-AUG-14:00 | 11-AUG-14:00 | 15-AUG-14:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 12-SEP-14:00 | 01-SEP-14:20 | 08-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 27-SEP-14:00 | 05-SEP-12:50 | 01-SEP-14:00 | 07-SEP-13:09 | 06-SEP-14:00 | 22-SEP-12:30 | 12-SEP-14:30 | 08-SEP-13:20 | 07-SEP-14:00
| Oct | 06-OCT-14:00 | 30-OCT-14:09 | 03-OCT-08:39 | 20-OCT-14:00 | 17-OCT-14:09 | 03-OCT-14:00 | 17-OCT-12:00 | 03-OCT-10:39 | 13-OCT-14:00 | 17-OCT-14:00 | 30-OCT-10:50 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 27-OCT-14:00 | 03-OCT-14:00
| Nov | 03-NOV-14:00 | 27-NOV-14:00 | 13-NOV-15:00 | 22-NOV-11:39 | 07-NOV-13:09 | 10-NOV-15:00 | 16-NOV-15:00 | 03-NOV-13:00 | 08-NOV-15:00 | 03-NOV-13:00 | 02-NOV-09:20 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:39 | 09-NOV-11:39 | 15-NOV-11:39
| Dec | 15-DEC-15:00 | 06-DEC-14:00 | 08-DEC-14:00 | 26-DEC-14:30 | 19-DEC-13:09 | 05-DEC-14:00 | 14-DEC-14:00 | 08-DEC-11:09 | 05-DEC-14:00 | 06-DEC-11:20 | 12-DEC-13:09 | 29-DEC-14:00 | 29-DEC-11:39 | 01-DEC-14:00 | 29-DEC-11:39 | 28-DEC-11:39
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 30953.83 | 25183.49 | 27036.04 | 19565.23 | 13517.54 | 22330.14 | 7402.52 | 16731.2 | 12406.64 | 6242.73 | 11291.71 | 9649.06 | 10164.86 | 6960.81 | 5497.96 | 3341.37
| Water Systems | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86 | 4037.86
| Total Building | 34997.72 | 29330.54 | 31995.73 | 23965.31 | 17834.12 | 28725.8 | 11565.26 | 21344.82 | 18788.97 | 10625.7 | 16327.51 | 15847.42 | 15302.14 | 12877.66 | 10887.48 | 9023.19
Emissions
| Carbon Equivalent (kg) | 2090220 | 2411820 | 1977870 | 2099600 | 888229.4014 | 2043290 | 904730.9997 | 1877870 | 2225240 | 696355.295 | 3062620 | 2222060 | 2128540 | 2031880 | 2028460 | 1832050
| CO2 (kg) | 5002610 | 6175260 | 4815020 | 4975550 | 2434780 | 4996070 | 2494260 | 4461690 | 5350320 | 1844540 | 7313350 | 5368980 | 5177080 | 4953570 | 4965110 | 4834780
| NOX (kg) | 8121.8337 | 7735.5878 | 7449.8999 | 8604.5219 | 2127.0965 | 7557.4278 | 2188.5843 | 7699.0926 | 8664.1789 | 2215.4755 | 12196.9734 | 8582.826 | 8222.1594 | 7780.3837 | 7750.2311 | 5420.3212
| SO2 (kg) | 28203.6512 | 29853.0711 | 22294.7487 | 20062.1865 | 14928.9302 | 28427.0875 | 13589.8914 | 20168.12 | 20631.7897 | 3462.8907 | 33352.7964 | 20099.8562 | 11494.9802 | 11899.1454 | 10583.8425 | 21593.8939
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1302 | 0.0858 | 0.0623 | 0.0752 | 0.0084 | 0.0551 | 0.0083 | 0.0836 | 0.0821 | 0.0157 | 0.1031 | 0.0803 | 0.0866 | 0.0849 | 0.0801 | 0.0769
| Water for Electricity (m3) | 3490.07 | 10181.7 | 164657 | 35677.7 | 90052.9 | 141751 | 81967.1 | 1254 | 21449.3 | 45701.2 | 7676.74 | 20895.5 | 7551.65 | 282145 | 6952.41 | 4332.14

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 39435.64 | 1758.77 | 1758.77
Net Site Energy | 39435.64 | 1758.77 | 1758.77
Total Source Energy | 95833.9 | 4274.06 | 4274.06
Net Source Energy | 95833.9 | 4274.06 | 4274.06
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13224.5 | 0 | 0 | 0 | 0
Cooling | 7427.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2513.07 | 0 | 0 | 0 | 0 | 0
Pumps | 1515.57 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1018.62 | 0 | 0 | 0 | 0 | 30953.83
Humidification | 0.06 | 0 | 0 | 0 | 0 | 6.04
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 456.6 | 0 | 0 | 0 | 4037.86
Refrigeration | 211.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 23716.94 | 15718.7 | 0 | 0 | 0 | 34997.72
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 6.49 | 0.25 | 0.25 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 6.49 | 0.25 | 0.25 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 6.49 | 0.25 | 0.25 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 6.49 | 0.25 | 0.25 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 6.49 | 0.25 | 0.25 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.25 | 0.25 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.25 | 0.25 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.25 | 0.25 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.25 | 0.25 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.25 | 0.25 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.25 | 0.25 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.25 | 0.25 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.25 | 0.25 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 6.49 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.25 | 0.25 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 6.49 | 0.25 | 0.25 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 6.49 | 0.61 | 0.61 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.25 | 0.25 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 6.49 | 0.61 | 0.61 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 6.49 | 0.329 | 0.329
North Total or Average |  |  | 186.18 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 659.24 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2643480.62 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3845139.3 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2461470.48
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.39 | 37409.81 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.3 | 11816.15 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.57 | 22851.28 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 50.49 | 113514.1 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21365.45 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24223.84 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 34740.22 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 402611.2256 | 643.4724 | 2189.7559 | 0 | 0.0101 | 270962.6925 | 167201.7321
February | 363064.499 | 582.0858 | 1988.9819 | 0 | 0.0092 | 246120.382 | 150960.4977
March | 407879.1443 | 656.8833 | 2257.6937 | 0 | 0.0104 | 279373.9821 | 169889.6075
April | 396869.7383 | 642.2467 | 2221.1052 | 0 | 0.0103 | 274849.2153 | 165613.9811
May | 436743.7123 | 713.1846 | 2494.7186 | 0 | 0.0115 | 308713.0667 | 182895.7636
June | 430733.2542 | 706.2829 | 2483.3141 | 0 | 0.0114 | 307304.3641 | 180670.6456
July | 452868.7069 | 744.9444 | 2629.5505 | 0 | 0.0121 | 325402.8376 | 190192.3681
August | 454031.7881 | 747.2643 | 2639.5048 | 0 | 0.0122 | 326635.0109 | 190721.58
September | 433176.0055 | 709.9656 | 2494.8576 | 0 | 0.0115 | 308732.5652 | 181662.9224
October | 429918.2186 | 699.7134 | 2437.4274 | 0 | 0.0112 | 301621.4305 | 179804.4254
November | 398049.0308 | 641.6672 | 2208.1234 | 0 | 0.0102 | 273240.5636 | 165856.8089
December | 396666.6763 | 634.1232 | 2158.6182 | 0 | 0.01 | 267109.8164 | 164748.2012
Annual Sum or Average | 5002610 | 8121.8337 | 28203.6512 | 0 | 0.1302 | 3490070 | 2090220
Minimum of Months | 363064.499 | 582.0858 | 1988.9819 | 0 | 0.0092 | 246120.382 | 150960.4977
Maximum of Months | 454031.7881 | 747.2643 | 2639.5048 | 0 | 0.0122 | 326635.0109 | 190721.58
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1841340000000 | 1072314.376 | 06-JAN-11:00 | 228236.782 | 379607.201 | 84902.165 | 0 | 289198.138 | 0 | 50721.697 | 32306.8 | 0 | 0 | 0 | 0 | 7341.594 | 0 | 0
February | 1672520000000 | 1074824.986 | 23-FEB-11:39 | 228236.782 | 379607.201 | 85757.056 | 0 | 286789.693 | 0 | 50739.748 | 32306.8 | 0 | 0 | 0 | 0 | 11387.707 | 0 | 0
March | 1898500000000 | 1095933.945 | 14-MAR-10:39 | 228236.782 | 379607.201 | 84929.23 | 0 | 308473.095 | 0 | 51095.284 | 32306.8 | 0 | 0 | 0 | 0 | 11285.553 | 0 | 0
April | 1867750000000 | 1108384.151 | 05-APR-12:00 | 228236.782 | 379607.201 | 87579.926 | 0 | 321586.832 | 0 | 51554.023 | 32306.8 | 0 | 0 | 0 | 0 | 7512.587 | 0 | 0
May | 2097880000000 | 1174848.366 | 19-MAY-14:00 | 228236.782 | 379607.201 | 91684.927 | 0 | 382436.825 | 0 | 52974.555 | 32306.8 | 0 | 0 | 0 | 0 | 7601.277 | 0 | 0
June | 2088300000000 | 1237559.171 | 27-JUN-14:00 | 228236.782 | 379607.201 | 91747.094 | 0 | 444204.723 | 0 | 53751.203 | 32306.8 | 0 | 0 | 0 | 0 | 7705.369 | 0 | 0
July | 2211290000000 | 1204710.572 | 13-JUL-14:00 | 228236.782 | 379607.201 | 92110.004 | 0 | 411347.599 | 0 | 53421.969 | 32306.8 | 0 | 0 | 0 | 0 | 7680.217 | 0 | 0
August | 2219670000000 | 1214327.978 | 21-AUG-14:30 | 228236.782 | 379607.201 | 88120.84 | 0 | 425350.734 | 0 | 52952.993 | 32306.8 | 0 | 0 | 0 | 0 | 7752.628 | 0 | 0
September | 2098010000000 | 1173176.223 | 07-SEP-13:00 | 228236.782 | 379607.201 | 90370.029 | 0 | 382020.087 | 0 | 52928.709 | 32306.8 | 0 | 0 | 0 | 0 | 7706.615 | 0 | 0
October | 2049690000000 | 1157967.656 | 06-OCT-14:00 | 228236.782 | 379607.201 | 91655.997 | 0 | 365783.418 | 0 | 52764.115 | 32306.8 | 0 | 0 | 0 | 0 | 7613.343 | 0 | 0
November | 1856820000000 | 1115461.456 | 03-NOV-14:00 | 228236.782 | 379607.201 | 87039.212 | 0 | 329085.073 | 0 | 51728.43 | 32306.8 | 0 | 0 | 0 | 0 | 7457.959 | 0 | 0
December | 1815160000000 | 1070231.202 | 15-DEC-15:00 | 228236.782 | 379607.201 | 88597.703 | 0 | 282893.15 | 0 | 51180.286 | 32306.8 | 0 | 0 | 0 | 0 | 7409.281 | 0 | 0
Annual Sum or Average | 23716900000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1672520000000 | 1070231.202 |  | 228236.782 | 379607.201 | 84902.165 | 0 | 282893.15 | 0 | 50721.697 | 32306.8 | 0 | 0 | 0 | 0 | 7341.594 | 0 | 0
Maximum of Months | 2219670000000 | 1237559.171 |  | 228236.782 | 379607.201 | 92110.004 | 0 | 444204.723 | 0 | 53751.203 | 32306.8 | 0 | 0 | 0 | 0 | 11387.707 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 495148.53 | 180064.23 | 0 | 675212.76
Cost per Total Building Area ($/m2) | 22.08 | 8.03 | 0 | 30.11
Cost per Net Conditioned Building Area ($/m2) | 22.08 | 8.03 | 0 | 30.11

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40525.77 | 1807.39 | 1807.39
Net Site Energy | 40525.77 | 1807.39 | 1807.39
Total Source Energy | 19654.68 | 876.57 | 876.57
Net Source Energy | 19654.68 | 876.57 | 876.57
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15413.53 | 0 | 0 | 0 | 0
Cooling | 6292.98 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2597.23 | 0 | 0 | 0 | 0 | 0
Pumps | 1436.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 964.42 | 0 | 0 | 0 | 0 | 25183.49
Humidification | 1.09 | 0 | 0 | 0 | 0 | 109.19
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 547.66 | 0 | 0 | 0 | 4037.86
Refrigeration | 204.04 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 22526.98 | 17998.79 | 0 | 0 | 0 | 29330.54
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 6.49 | 0.391 | 0.39 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 6.49 | 0.391 | 0.39 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 6.49 | 0.391 | 0.39 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 6.49 | 0.391 | 0.39 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 6.49 | 0.391 | 0.39 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.391 | 0.39 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.391 | 0.39 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.391 | 0.39 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.391 | 0.39 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 6.49 | 0.391 | 0.39 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 6.49 | 0.391 | 0.39 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 6.49 | 0.61 | 0.61 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 6.49 | 0.61 | 0.61 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 6.49 | 0.439 | 0.438
North Total or Average |  |  | 186.18 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 659.24 | 6.49 | 0.391 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2581190.8 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4337596.55 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2403469.46
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.15 | 39133.52 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.61 | 12407.6 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.78 | 24881.42 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 52.32 | 117635.22 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24101.78 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23653.04 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 33921.62 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 494063.5589 | 608.1017 | 2237.2091 | 0 | 0.0065 | 762966.7052 | 191570.5728
February | 438209.7871 | 539.0535 | 1980.0572 | 0 | 0.0058 | 675267.2348 | 169874.5781
March | 498562.5436 | 620.5128 | 2353.8493 | 0 | 0.0068 | 802782.4128 | 194201.0248
April | 494205.0916 | 619.05 | 2388.7464 | 0 | 0.0069 | 814704.7412 | 193014.2141
May | 536626.7099 | 676.5932 | 2655.4874 | 0 | 0.0076 | 905701.7452 | 210149.9956
June | 542267.3754 | 687.2336 | 2732.8187 | 0 | 0.0078 | 932094.4996 | 212813.773
July | 576125.7693 | 731.8683 | 2927.6086 | 0 | 0.0084 | 998540.7736 | 226323.8823
August | 576035.3515 | 731.4747 | 2923.245 | 0 | 0.0083 | 997051.1 | 226252.4314
September | 527617.7858 | 666.5528 | 2629.3703 | 0 | 0.0075 | 896800.5701 | 206791.9096
October | 518035.9616 | 649.9092 | 2518.0537 | 0 | 0.0072 | 858811.3515 | 202451.4335
November | 484321.486 | 603.3297 | 2294.1957 | 0 | 0.0066 | 782440.3495 | 188723.6051
December | 489188.4187 | 601.9083 | 2212.4297 | 0 | 0.0064 | 754514.9983 | 189655.3772
Annual Sum or Average | 6175260 | 7735.5878 | 29853.0711 | 0 | 0.0858 | 10181700 | 2411820
Minimum of Months | 438209.7871 | 539.0535 | 1980.0572 | 0 | 0.0058 | 675267.2348 | 169874.5781
Maximum of Months | 576125.7693 | 731.8683 | 2927.6086 | 0 | 0.0084 | 998540.7736 | 226323.8823
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1688070000000 | 1047278.836 | 03-JAN-11:50 | 228236.782 | 379607.201 | 84983.99 | 0 | 264762.326 | 0 | 49233.637 | 31545.537 | 0 | 0 | 0 | 0 | 8909.365 | 0 | 0
February | 1494030000000 | 1009834.853 | 15-FEB-14:00 | 228236.782 | 379607.201 | 87316.444 | 0 | 227054.701 | 0 | 48785.485 | 31545.537 | 0 | 0 | 0 | 0 | 7288.704 | 0 | 0
March | 1776160000000 | 1036909.403 | 24-MAR-12:09 | 228236.782 | 379607.201 | 87145.657 | 0 | 253770.869 | 0 | 49228.569 | 31545.537 | 0 | 0 | 0 | 0 | 7374.788 | 0 | 0
April | 1802540000000 | 1069967.114 | 10-APR-12:00 | 228236.782 | 379607.201 | 85972.64 | 0 | 287571.797 | 0 | 49613.244 | 31545.537 | 0 | 0 | 0 | 0 | 7419.913 | 0 | 0
May | 2003870000000 | 1169459.434 | 18-MAY-14:09 | 228236.782 | 379607.201 | 92649.407 | 0 | 377702.898 | 0 | 51994.441 | 31545.537 | 0 | 0 | 0 | 0 | 7723.169 | 0 | 0
June | 2062260000000 | 1161340.384 | 29-JUN-14:00 | 228236.782 | 379607.201 | 93505.15 | 0 | 368839.917 | 0 | 51904.795 | 31545.537 | 0 | 0 | 0 | 0 | 7701.003 | 0 | 0
July | 2209270000000 | 1249983.934 | 18-JUL-12:50 | 228236.782 | 379607.201 | 91540.926 | 0 | 457771.321 | 0 | 53506.818 | 31545.537 | 0 | 0 | 0 | 0 | 7775.35 | 0 | 0
August | 2205980000000 | 1211444.816 | 03-AUG-14:00 | 228236.782 | 379607.201 | 93909.028 | 0 | 417688.834 | 0 | 52726.077 | 31545.537 | 0 | 0 | 0 | 0 | 7731.358 | 0 | 0
September | 1984170000000 | 1230109.827 | 15-SEP-14:00 | 228236.782 | 379607.201 | 92350.498 | 0 | 437959.079 | 0 | 52682.916 | 31545.537 | 0 | 0 | 0 | 0 | 7727.815 | 0 | 0
October | 1900120000000 | 1131661.435 | 30-OCT-14:09 | 228236.782 | 379607.201 | 87740.716 | 0 | 346277.639 | 0 | 50739.393 | 31545.537 | 0 | 0 | 0 | 0 | 7514.168 | 0 | 0
November | 1731150000000 | 1080118.908 | 27-NOV-14:00 | 228236.782 | 379607.201 | 87318.97 | 0 | 295883.706 | 0 | 50125.244 | 31545.537 | 0 | 0 | 0 | 0 | 7401.468 | 0 | 0
December | 1669370000000 | 1044007.194 | 06-DEC-14:00 | 228236.782 | 379607.201 | 87378.537 | 0 | 260465.545 | 0 | 49485.999 | 31545.537 | 0 | 0 | 0 | 0 | 7287.594 | 0 | 0
Annual Sum or Average | 22527000000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1494030000000 | 1009834.853 |  | 228236.782 | 379607.201 | 84983.99 | 0 | 227054.701 | 0 | 48785.485 | 31545.537 | 0 | 0 | 0 | 0 | 7287.594 | 0 | 0
Maximum of Months | 2209270000000 | 1249983.934 |  | 228236.782 | 379607.201 | 93909.028 | 0 | 457771.321 | 0 | 53506.818 | 31545.537 | 0 | 0 | 0 | 0 | 8909.365 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 613416.62 | 147362.64 | 0 | 760779.26
Cost per Total Building Area ($/m2) | 27.36 | 6.57 | 0 | 33.93
Cost per Net Conditioned Building Area ($/m2) | 27.36 | 6.57 | 0 | 33.93

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 36842.39 | 1643.12 | 1643.12
Net Site Energy | 36842.39 | 1643.12 | 1643.12
Total Source Energy | 81559.6 | 3637.44 | 3637.44
Net Source Energy | 81559.6 | 3637.44 | 3637.44
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14354.06 | 0 | 0 | 0 | 0
Cooling | 4102.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2769.77 | 0 | 0 | 0 | 0 | 0
Pumps | 1107.43 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 730.23 | 0 | 0 | 0 | 0 | 27036.04
Humidification | 9.22 | 0 | 0 | 0 | 0 | 921.83
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 495.29 | 0 | 0 | 0 | 4037.86
Refrigeration | 205.79 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19955.44 | 16886.95 | 0 | 0 | 0 | 31995.73
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 6.49 | 0.391 | 0.39 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 6.49 | 0.391 | 0.39 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 6.49 | 0.391 | 0.39 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 6.49 | 0.391 | 0.39 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 6.49 | 0.391 | 0.39 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.391 | 0.39 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.391 | 0.39 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.391 | 0.39 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.391 | 0.39 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.391 | 0.39 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.391 | 0.39 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 6.49 | 0.391 | 0.39 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 6.49 | 0.391 | 0.39 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 6.49 | 0.61 | 0.61 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.391 | 0.39 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 6.49 | 0.61 | 0.61 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 6.49 | 0.439 | 0.438
North Total or Average |  |  | 186.18 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 659.24 | 6.49 | 0.391 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2083868.92 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4263269.29 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1940389.42
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.18 | 41481.9 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.91 | 12962.46 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.91 | 28459.37 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 56.85 | 127814.58 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23688.79 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19095.77 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 27385.89 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 378557.2635 | 564.202 | 1597.2134 | 0 | 0.0045 | 11794900 | 153324.877
February | 344856.3576 | 515.6815 | 1467.3731 | 0 | 0.0042 | 10836100 | 139847.8416
March | 403962.1202 | 619.2774 | 1828.9147 | 0 | 0.0051 | 13507000 | 165354.978
April | 392007.6262 | 606.5537 | 1815.3207 | 0 | 0.0051 | 13407000 | 161028.1547
May | 415295.1668 | 649.0775 | 1970.1177 | 0 | 0.0055 | 14550600 | 171250.5519
June | 413020.1121 | 653.8232 | 2019.3782 | 0 | 0.0056 | 14914900 | 171151.8735
July | 438805.7951 | 700.0554 | 2184.6077 | 0 | 0.006 | 16135600 | 182384.5745
August | 440491.8864 | 701.6618 | 2185.1643 | 0 | 0.006 | 16139600 | 182975.8187
September | 413108.2706 | 652.1965 | 2007.0319 | 0 | 0.0056 | 14823600 | 171009.796
October | 410681.621 | 636.9868 | 1912.9291 | 0 | 0.0053 | 14127900 | 168854.6376
November | 384907.2662 | 587.1277 | 1721.3881 | 0 | 0.0048 | 12712700 | 157258.0589
December | 379328.7833 | 563.2564 | 1585.3097 | 0 | 0.0045 | 11706800 | 153425.4605
Annual Sum or Average | 4815020 | 7449.8999 | 22294.7487 | 0 | 0.0623 | 164657000 | 1977870
Minimum of Months | 344856.3576 | 515.6815 | 1467.3731 | 0 | 0.0042 | 10836100 | 139847.8416
Maximum of Months | 440491.8864 | 701.6618 | 2185.1643 | 0 | 0.006 | 16139600 | 182975.8187
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1429470000000 | 936632.67 | 26-JAN-15:00 | 228236.782 | 379607.201 | 94260.639 | 0 | 163097.01 | 0 | 38069.619 | 25467.611 | 0 | 0 | 0 | 0 | 7280.623 | 0 | 0
February | 1313280000000 | 947875.699 | 28-FEB-15:00 | 228236.782 | 379607.201 | 95026.23 | 0 | 173032.266 | 0 | 38398.501 | 25467.611 | 0 | 0 | 0 | 0 | 7414.895 | 0 | 0
March | 1636970000000 | 972767.91 | 17-MAR-14:00 | 228236.782 | 379607.201 | 96988.28 | 0 | 195337.874 | 0 | 39178.405 | 25467.611 | 0 | 0 | 0 | 0 | 7651.803 | 0 | 0
April | 1624850000000 | 976185.224 | 26-APR-14:00 | 228236.782 | 379607.201 | 96697.754 | 0 | 198767.733 | 0 | 39241.241 | 25467.611 | 0 | 0 | 0 | 0 | 7690.065 | 0 | 0
May | 1763450000000 | 996846.483 | 19-MAY-14:00 | 228236.782 | 379607.201 | 98296.896 | 0 | 217120.96 | 0 | 39884.999 | 25467.611 | 0 | 0 | 0 | 0 | 7748.837 | 0 | 0
June | 1807600000000 | 1072502.045 | 30-JUN-12:00 | 228236.782 | 379607.201 | 99511.494 | 0 | 289415.955 | 0 | 42437.432 | 25467.611 | 0 | 0 | 0 | 0 | 7825.57 | 0 | 0
July | 1955540000000 | 1114275.564 | 18-JUL-14:00 | 228236.782 | 379607.201 | 101178.352 | 0 | 328197.526 | 0 | 43757.157 | 25467.611 | 0 | 0 | 0 | 0 | 7830.935 | 0 | 0
August | 1956030000000 | 1102425.407 | 11-AUG-14:00 | 228236.782 | 379607.201 | 101528.883 | 0 | 315940.189 | 0 | 43811.56 | 25467.611 | 0 | 0 | 0 | 0 | 7833.181 | 0 | 0
September | 1796530000000 | 1063655.331 | 12-SEP-14:00 | 228236.782 | 379607.201 | 100706.501 | 0 | 279437.498 | 0 | 42366.32 | 25467.611 | 0 | 0 | 0 | 0 | 7833.418 | 0 | 0
October | 1712220000000 | 1007099.543 | 03-OCT-08:39 | 228236.782 | 379607.201 | 90218.173 | 0 | 235903.648 | 0 | 40594.53 | 25467.611 | 0 | 0 | 0 | 0 | 7071.598 | 0 | 0
November | 1540710000000 | 957178.198 | 13-NOV-15:00 | 228236.782 | 379607.201 | 93947.511 | 0 | 183594.823 | 0 | 38572.408 | 25467.611 | 0 | 0 | 0 | 0 | 7569.514 | 0 | 0
December | 1418800000000 | 930672.605 | 08-DEC-14:00 | 228236.782 | 379607.201 | 93603.795 | 0 | 157801.855 | 0 | 37880.301 | 25467.611 | 0 | 0 | 0 | 0 | 7215.841 | 0 | 0
Annual Sum or Average | 19955400000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1313280000000 | 930672.605 |  | 228236.782 | 379607.201 | 90218.173 | 0 | 157801.855 | 0 | 37880.301 | 25467.611 | 0 | 0 | 0 | 0 | 7071.598 | 0 | 0
Maximum of Months | 1956030000000 | 1114275.564 |  | 228236.782 | 379607.201 | 101528.883 | 0 | 328197.526 | 0 | 43811.56 | 25467.611 | 0 | 0 | 0 | 0 | 7833.418 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 380991.75 | 144788.75 | 0 | 525780.5
Cost per Total Building Area ($/m2) | 16.99 | 6.46 | 0 | 23.45
Cost per Net Conditioned Building Area ($/m2) | 16.99 | 6.46 | 0 | 23.45

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 39392.49 | 1756.85 | 1756.85
Net Site Energy | 39392.49 | 1756.85 | 1756.85
Total Source Energy | 89754.89 | 4002.94 | 4002.94
Net Source Energy | 89754.89 | 4002.94 | 4002.94
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16148.01 | 0 | 0 | 0 | 0
Cooling | 4595.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2599.67 | 0 | 0 | 0 | 0 | 0
Pumps | 1295.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 849.78 | 0 | 0 | 0 | 0 | 19565.23
Humidification | 3.62 | 0 | 0 | 0 | 0 | 362.22
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 635.45 | 0 | 0 | 0 | 4037.86
Refrigeration | 197.65 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20571.43 | 18821.06 | 0 | 0 | 0 | 23965.31
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.402 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.402 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.402 | 0.495 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.402 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.424 | 0.523
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2420074.17 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4372251.69 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2253446.11
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.26 | 39383.38 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.59 | 12358.01 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.76 | 24850.58 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 53.17 | 119542.49 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24294.34 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22176.63 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 31804.25 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 409344.7744 | 675.4925 | 1491.653 | 0 | 0.0057 | 2652330 | 169743.7474
February | 368763.5319 | 613.9088 | 1370.1613 | 0 | 0.0052 | 2436370 | 153412.957
March | 408271.9825 | 698.7963 | 1610.6588 | 0 | 0.0061 | 2864240 | 171614.5542
April | 396412.0919 | 686.4472 | 1602.8434 | 0 | 0.006 | 2850440 | 167363.5518
May | 423256.737 | 743.1977 | 1761.706 | 0 | 0.0066 | 3133070 | 179645.2472
June | 425021.0041 | 754.1363 | 1807.485 | 0 | 0.0067 | 3214560 | 181118.1763
July | 451648.5398 | 805.8749 | 1942.7443 | 0 | 0.0072 | 3455170 | 192880.0733
August | 454342.7792 | 810.9293 | 1955.5446 | 0 | 0.0073 | 3477930 | 194053.4872
September | 426274.3847 | 754.7352 | 1804.8494 | 0 | 0.0067 | 3209860 | 181502.2183
October | 412075.3777 | 715.6167 | 1676.2067 | 0 | 0.0063 | 2980930 | 174165.5005
November | 392850.5367 | 667.5967 | 1526.2695 | 0 | 0.0058 | 2714120 | 164688.561
December | 407287.0671 | 677.7903 | 1512.0645 | 0 | 0.0057 | 2688690 | 169416.281
Annual Sum or Average | 4975550 | 8604.5219 | 20062.1865 | 0 | 0.0752 | 35677700 | 2099600
Minimum of Months | 368763.5319 | 613.9088 | 1370.1613 | 0 | 0.0052 | 2436370 | 153412.957
Maximum of Months | 454342.7792 | 810.9293 | 1955.5446 | 0 | 0.0073 | 3477930 | 194053.4872
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1529310000000 | 939893.7 | 24-JAN-15:00 | 228236.782 | 379607.201 | 87540.193 | 0 | 164140.735 | 0 | 43934.407 | 29576.48 | 0 | 0 | 0 | 0 | 6857.903 | 0 | 0
February | 1404790000000 | 930618.074 | 21-FEB-13:00 | 228236.782 | 379607.201 | 85125.273 | 0 | 157846.189 | 0 | 43344.643 | 29576.48 | 0 | 0 | 0 | 0 | 6881.506 | 0 | 0
March | 1651500000000 | 967227.615 | 29-MAR-14:00 | 228236.782 | 379607.201 | 89490.227 | 0 | 188011.705 | 0 | 45235.76 | 29576.48 | 0 | 0 | 0 | 0 | 7069.46 | 0 | 0
April | 1643530000000 | 995776.418 | 13-APR-14:00 | 228236.782 | 379607.201 | 90974.57 | 0 | 214038.884 | 0 | 45883.388 | 29576.48 | 0 | 0 | 0 | 0 | 7459.113 | 0 | 0
May | 1806500000000 | 1047557.378 | 31-MAY-14:00 | 228236.782 | 379607.201 | 91766.352 | 0 | 263500.33 | 0 | 47324.366 | 29576.48 | 0 | 0 | 0 | 0 | 7545.867 | 0 | 0
June | 1853490000000 | 1116360.375 | 08-JUN-14:00 | 228236.782 | 379607.201 | 92853.242 | 0 | 329788.232 | 0 | 48699.15 | 29576.48 | 0 | 0 | 0 | 0 | 7599.288 | 0 | 0
July | 1992220000000 | 1146466.576 | 03-JUL-12:09 | 228236.782 | 379607.201 | 89197.565 | 0 | 363568.66 | 0 | 48491.472 | 29576.48 | 0 | 0 | 0 | 0 | 7788.416 | 0 | 0
August | 2005340000000 | 1145383.98 | 17-AUG-14:00 | 228236.782 | 379607.201 | 94948.11 | 0 | 355974.543 | 0 | 49284.632 | 29576.48 | 0 | 0 | 0 | 0 | 7756.232 | 0 | 0
September | 1850770000000 | 1093851.143 | 01-SEP-14:20 | 228236.782 | 379607.201 | 91868.37 | 0 | 308810.603 | 0 | 48268.076 | 29576.48 | 0 | 0 | 0 | 0 | 7483.631 | 0 | 0
October | 1718770000000 | 1008739.834 | 20-OCT-14:00 | 228236.782 | 379607.201 | 90430.558 | 0 | 226965.126 | 0 | 46603.008 | 29576.48 | 0 | 0 | 0 | 0 | 7320.68 | 0 | 0
November | 1564940000000 | 951651.177 | 22-NOV-11:39 | 228236.782 | 379607.201 | 86930.17 | 0 | 172743.27 | 0 | 44105.858 | 29576.48 | 0 | 0 | 0 | 0 | 10451.417 | 0 | 0
December | 1550270000000 | 948862.73 | 26-DEC-14:30 | 228236.782 | 379607.201 | 85157.119 | 0 | 174942.919 | 0 | 44355.916 | 29576.48 | 0 | 0 | 0 | 0 | 6986.313 | 0 | 0
Annual Sum or Average | 20571400000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1404790000000 | 930618.074 |  | 228236.782 | 379607.201 | 85125.273 | 0 | 157846.189 | 0 | 43344.643 | 29576.48 | 0 | 0 | 0 | 0 | 6857.903 | 0 | 0
Maximum of Months | 2005340000000 | 1146466.576 |  | 228236.782 | 379607.201 | 94948.11 | 0 | 363568.66 | 0 | 49284.632 | 29576.48 | 0 | 0 | 0 | 0 | 10451.417 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 563344.71 | 202317.32 | 0 | 765662.03
Cost per Total Building Area ($/m2) | 25.12 | 9.02 | 0 | 34.15
Cost per Net Conditioned Building Area ($/m2) | 25.12 | 9.02 | 0 | 34.15

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 34481.24 | 1537.81 | 1537.81
Net Site Energy | 34481.24 | 1537.81 | 1537.81
Total Source Energy | 74637.37 | 3328.72 | 3328.72
Net Source Energy | 74637.37 | 3328.72 | 3328.72
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13360.98 | 0 | 0 | 0 | 0
Cooling | 3189.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2530.64 | 0 | 0 | 0 | 0 | 0
Pumps | 900.88 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 612.09 | 0 | 0 | 0 | 0 | 13517.54
Humidification | 2.79 | 0 | 0 | 0 | 0 | 278.72
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 618.43 | 0 | 0 | 0 | 4037.86
Refrigeration | 198.41 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18464.23 | 16017.01 | 0 | 0 | 0 | 17834.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.402 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.402 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.402 | 0.495 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.402 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.424 | 0.523
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1629000.04 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3906791.1 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1516839.38
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.46 | 37570.99 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.41 | 12030.41 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.11 | 23747.36 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 49.66 | 111653.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21708.02 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14927.53 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 21408.07 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 206459.8428 | 181.0603 | 1142.2947 | 0 | 0.0007 | 6889820 | 74941.1953
February | 184868.9399 | 162.072 | 1032.4229 | 0 | 0.0006 | 6227170 | 67133.3328
March | 208874.2455 | 182.8654 | 1211.5268 | 0 | 0.0007 | 7307710 | 75988.0482
April | 200007.73 | 174.9718 | 1183.5716 | 0 | 0.0007 | 7139210 | 72834.0421
May | 207608.4021 | 181.2796 | 1289.6355 | 0 | 0.0007 | 7779300 | 75788.2444
June | 200697.3337 | 175.001 | 1290.3646 | 0 | 0.0007 | 7783920 | 73398.5362
July | 203734.5264 | 177.3807 | 1357.9482 | 0 | 0.0007 | 8191840 | 74655.9087
August | 207324.0362 | 180.3552 | 1408.8422 | 0 | 0.0007 | 8498990 | 76053.5197
September | 198519.3718 | 172.8812 | 1315.8504 | 0 | 0.0007 | 7937850 | 72722.4962
October | 206610.8864 | 180.2269 | 1315.9511 | 0 | 0.0007 | 7938210 | 75523.2904
November | 202318.2815 | 176.9511 | 1204.7567 | 0 | 0.0007 | 7267040 | 73698.3628
December | 207757.4711 | 182.0514 | 1175.7654 | 0 | 0.0007 | 7091850 | 75492.4244
Annual Sum or Average | 2434780 | 2127.0965 | 14928.9302 | 0 | 0.0084 | 90052900 | 888229.4014
Minimum of Months | 184868.9399 | 162.072 | 1032.4229 | 0 | 0.0006 | 6227170 | 67133.3328
Maximum of Months | 208874.2455 | 182.8654 | 1408.8422 | 0 | 0.0007 | 8498990 | 76053.5197
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1412670000000 | 911852.571 | 26-JAN-13:00 | 228236.782 | 379607.201 | 87824.619 | 0 | 156920.286 | 0 | 31450.465 | 19908.517 | 0 | 0 | 0 | 0 | 7405.808 | 0 | 0
February | 1276800000000 | 896661.207 | 13-FEB-11:00 | 228236.782 | 379607.201 | 84510.044 | 0 | 146329.84 | 0 | 30754.84 | 19908.517 | 0 | 0 | 0 | 0 | 7280.278 | 0 | 0
March | 1498350000000 | 903588.203 | 31-MAR-14:00 | 228236.782 | 379607.201 | 90757.969 | 0 | 145816.992 | 0 | 31300.833 | 19908.517 | 0 | 0 | 0 | 0 | 7227.833 | 0 | 0
April | 1463810000000 | 933601.525 | 11-APR-13:00 | 228236.782 | 379607.201 | 88035.17 | 0 | 177018.006 | 0 | 33526.394 | 19908.517 | 0 | 0 | 0 | 0 | 7269.455 | 0 | 0
May | 1595050000000 | 953027.546 | 30-MAY-13:30 | 228236.782 | 379607.201 | 86387.819 | 0 | 197399.926 | 0 | 34201.86 | 19908.517 | 0 | 0 | 0 | 0 | 7285.441 | 0 | 0
June | 1596000000000 | 950023.088 | 28-JUN-13:00 | 228236.782 | 379607.201 | 89210.716 | 0 | 191467.46 | 0 | 34268.508 | 19908.517 | 0 | 0 | 0 | 0 | 7323.905 | 0 | 0
July | 1679640000000 | 975075.597 | 20-JUL-14:00 | 228236.782 | 379607.201 | 91069.526 | 0 | 213579.047 | 0 | 35401.43 | 19908.517 | 0 | 0 | 0 | 0 | 7273.095 | 0 | 0
August | 1742610000000 | 1009583.313 | 09-AUG-14:00 | 228236.782 | 379607.201 | 98542.175 | 0 | 239657.446 | 0 | 36323.288 | 19908.517 | 0 | 0 | 0 | 0 | 7307.904 | 0 | 0
September | 1627560000000 | 961071.482 | 08-SEP-14:00 | 228236.782 | 379607.201 | 92292.428 | 0 | 198775.447 | 0 | 34944.483 | 19908.517 | 0 | 0 | 0 | 0 | 7306.623 | 0 | 0
October | 1627630000000 | 946844.861 | 17-OCT-14:09 | 228236.782 | 379607.201 | 88410.586 | 0 | 190027.374 | 0 | 33506.904 | 19908.517 | 0 | 0 | 0 | 0 | 7147.497 | 0 | 0
November | 1490020000000 | 922162.772 | 07-NOV-13:09 | 228236.782 | 379607.201 | 85841.89 | 0 | 168966.58 | 0 | 32453.816 | 19908.517 | 0 | 0 | 0 | 0 | 7147.986 | 0 | 0
December | 1454100000000 | 908863.089 | 19-DEC-13:09 | 228236.782 | 379607.201 | 86817.683 | 0 | 155280.708 | 0 | 31263.778 | 19908.517 | 0 | 0 | 0 | 0 | 7410.004 | 0 | 0
Annual Sum or Average | 18464200000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1276800000000 | 896661.207 |  | 228236.782 | 379607.201 | 84510.044 | 0 | 145816.992 | 0 | 30754.84 | 19908.517 | 0 | 0 | 0 | 0 | 7147.497 | 0 | 0
Maximum of Months | 1742610000000 | 1009583.313 |  | 228236.782 | 379607.201 | 98542.175 | 0 | 239657.446 | 0 | 36323.288 | 19908.517 | 0 | 0 | 0 | 0 | 7410.004 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 228421.97 | 134744.77 | 0 | 363166.74
Cost per Total Building Area ($/m2) | 10.19 | 6.01 | 0 | 16.2
Cost per Net Conditioned Building Area ($/m2) | 10.19 | 6.01 | 0 | 16.2

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 35270.42 | 1573.01 | 1573.01
Net Site Energy | 35270.42 | 1573.01 | 1573.01
Total Source Energy | 84739.25 | 3779.25 | 3779.25
Net Source Energy | 84739.25 | 3779.25 | 3779.25
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14073.23 | 0 | 0 | 0 | 0
Cooling | 3071.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2737.53 | 0 | 0 | 0 | 0 | 0
Pumps | 961.46 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 575.95 | 0 | 0 | 0 | 0 | 22330.14
Humidification | 23.58 | 0 | 0 | 0 | 0 | 2357.8
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 558.4 | 0 | 0 | 0 | 4037.86
Refrigeration | 201.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18601.19 | 16669.22 | 0 | 0 | 0 | 28725.8
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.402 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.402 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.402 | 0.495 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.402 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.424 | 0.523
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1855594.22 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4219928.75 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1727832
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.23 | 41589.21 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.81 | 12784.2 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.25 | 27351.25 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 57.61 | 129518.09 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23447.96 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17003.95 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 24385.94 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 392723.5967 | 569.678 | 2005.3525 | 0 | 0.004 | 9998640 | 158081.3858
February | 360667.6088 | 533.1085 | 1935.0049 | 0 | 0.0038 | 9648360 | 146210.1688
March | 405590.8653 | 602.6796 | 2205.8099 | 0 | 0.0043 | 10998800 | 164750.9053
April | 412876.1821 | 626.7776 | 2370.1837 | 0 | 0.0046 | 11819000 | 169089.7161
May | 436040.0752 | 667.1648 | 2552.2496 | 0 | 0.0049 | 12727100 | 179119.1169
June | 437336.9928 | 678.1279 | 2644.2348 | 0 | 0.0051 | 13186200 | 180585.1038
July | 451789.5116 | 702.6826 | 2751.7781 | 0 | 0.0053 | 13722500 | 186775.7682
August | 460011.7642 | 715.6329 | 2803.3809 | 0 | 0.0054 | 13979900 | 190191.7907
September | 430164.2274 | 663.4293 | 2567.2484 | 0 | 0.0049 | 12802100 | 177251.5751
October | 427650.8339 | 648.6418 | 2449.6909 | 0 | 0.0047 | 12215400 | 175081.8331
November | 389683.8598 | 578.7428 | 2116.4789 | 0 | 0.0041 | 10553300 | 158258.2932
December | 391535.4327 | 570.762 | 2025.6749 | 0 | 0.004 | 10100100 | 157894.9349
Annual Sum or Average | 4996070 | 7557.4278 | 28427.0875 | 0 | 0.0551 | 141751000 | 2043290
Minimum of Months | 360667.6088 | 533.1085 | 1935.0049 | 0 | 0.0038 | 9648360 | 146210.1688
Maximum of Months | 460011.7642 | 715.6329 | 2803.3809 | 0 | 0.0054 | 13979900 | 190191.7907
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1312060000000 | 894648.858 | 18-JAN-14:00 | 228236.782 | 379607.201 | 92087.63 | 0 | 130863.289 | 0 | 33483.074 | 22677.795 | 0 | 0 | 0 | 0 | 7063.37 | 0 | 0
February | 1266100000000 | 909799.586 | 08-FEB-15:00 | 228236.782 | 379607.201 | 94026.297 | 0 | 142918.23 | 0 | 34066.606 | 22677.795 | 0 | 0 | 0 | 0 | 7171.664 | 0 | 0
March | 1443310000000 | 924570.232 | 31-MAR-14:00 | 228236.782 | 379607.201 | 95389.281 | 0 | 156308.901 | 0 | 34600.067 | 22677.795 | 0 | 0 | 0 | 0 | 7316.258 | 0 | 0
April | 1550940000000 | 960868.369 | 21-APR-14:00 | 228236.782 | 379607.201 | 98073.24 | 0 | 188684.299 | 0 | 35851.929 | 22677.795 | 0 | 0 | 0 | 0 | 7678.92 | 0 | 0
May | 1670100000000 | 976057.337 | 31-MAY-14:00 | 228236.782 | 379607.201 | 98876.632 | 0 | 202123.59 | 0 | 36347.461 | 22677.795 | 0 | 0 | 0 | 0 | 7752.418 | 0 | 0
June | 1730340000000 | 1020765.383 | 27-JUN-14:00 | 228236.782 | 379607.201 | 103538.172 | 0 | 240410.187 | 0 | 38100.272 | 22677.795 | 0 | 0 | 0 | 0 | 7757.822 | 0 | 0
July | 1800730000000 | 1027037.816 | 11-JUL-14:00 | 228236.782 | 379607.201 | 102352.958 | 0 | 248294.759 | 0 | 38043.989 | 22677.795 | 0 | 0 | 0 | 0 | 7824.332 | 0 | 0
August | 1834500000000 | 1065316.251 | 07-AUG-14:20 | 228236.782 | 379607.201 | 97157.263 | 0 | 289789.786 | 0 | 40017.527 | 22677.795 | 0 | 0 | 0 | 0 | 7829.898 | 0 | 0
September | 1679940000000 | 1003022.606 | 01-SEP-14:00 | 228236.782 | 379607.201 | 102490.711 | 0 | 224764.28 | 0 | 37464.653 | 22677.795 | 0 | 0 | 0 | 0 | 7781.184 | 0 | 0
October | 1602960000000 | 960058.085 | 03-OCT-14:00 | 228236.782 | 379607.201 | 97457.039 | 0 | 188352.321 | 0 | 35783.135 | 22677.795 | 0 | 0 | 0 | 0 | 7681.622 | 0 | 0
November | 1384850000000 | 911471.794 | 10-NOV-15:00 | 228236.782 | 379607.201 | 95023.669 | 0 | 143802.45 | 0 | 34162.953 | 22677.795 | 0 | 0 | 0 | 0 | 7176.125 | 0 | 0
December | 1325380000000 | 908711.549 | 05-DEC-14:00 | 228236.782 | 379607.201 | 92536.352 | 0 | 143388.848 | 0 | 33970.731 | 22677.795 | 0 | 0 | 0 | 0 | 7178.71 | 0 | 0
Annual Sum or Average | 18601200000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1266100000000 | 894648.858 |  | 228236.782 | 379607.201 | 92087.63 | 0 | 130863.289 | 0 | 33483.074 | 22677.795 | 0 | 0 | 0 | 0 | 7063.37 | 0 | 0
Maximum of Months | 1834500000000 | 1065316.251 |  | 228236.782 | 379607.201 | 103538.172 | 0 | 289789.786 | 0 | 40017.527 | 22677.795 | 0 | 0 | 0 | 0 | 7829.898 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 457050.01 | 135417.02 | 0 | 592467.03
Cost per Total Building Area ($/m2) | 20.38 | 6.04 | 0 | 26.42
Cost per Net Conditioned Building Area ($/m2) | 20.38 | 6.04 | 0 | 26.42

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 36723.01 | 1637.79 | 1637.79
Net Site Energy | 36723.01 | 1637.79 | 1637.79
Total Source Energy | 73764.6 | 3289.8 | 3289.8
Net Source Energy | 73764.6 | 3289.8 | 3289.8
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 17185.52 | 0 | 0 | 0 | 0
Cooling | 1703.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2648.93 | 0 | 0 | 0 | 0 | 0
Pumps | 726.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 502.94 | 0 | 0 | 0 | 0 | 7402.52
Humidification | 1.25 | 0 | 0 | 0 | 0 | 124.88
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 693.56 | 0 | 0 | 0 | 4037.86
Refrigeration | 192.39 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16806.33 | 19916.68 | 0 | 0 | 0 | 11565.26
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 6.49 | 0.61 | 0.61 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 6.49 | 0.61 | 0.61 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 6.49 | 0.61 | 0.61 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 6.49 | 0.82 | 0.82 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.82 | 0.82 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 6.49 | 0.61 | 0.61 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 6.49 | 0.61 | 0.61 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.61 | 0.61 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.61 | 0.61 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.82 | 0.82 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.82 | 0.82 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.61 | 0.61 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.82 | 0.82 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 6.49 | 0.61 | 0.61 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.61 | 0.61 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 6.49 | 0.82 | 0.82 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 6.49 | 0.82 | 0.82 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 6.49 | 0.61 | 0.61 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 6.49 | 0.61 | 0.61 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 6.49 | 0.82 | 0.82 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 6.49 | 0.61 | 0.61 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 6.49 | 0.61 | 0.61 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 6.49 | 0.61 | 0.61 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 6.49 | 0.61 | 0.61 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 6.49 | 0.82 | 0.82 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 6.49 | 0.61 | 0.61 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 6.49 | 0.82 | 0.82 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 6.49 | 0.656 | 0.656
North Total or Average |  |  | 186.18 | 6.49 | 0.82 | 0.82
Non-North Total or Average |  |  | 659.24 | 6.49 | 0.61 | 0.61
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1571446.78 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4190553.59 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1463248.8
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.04 | 38875.37 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.65 | 12467.93 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.24 | 27337.09 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 49.17 | 110554.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23284.74 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14400.13 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 20651.72 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 215499.4989 | 189.8909 | 1030.7382 | 0 | 0.0007 | 6216050 | 77729.481
February | 189945.6763 | 166.962 | 982.184 | 0 | 0.0006 | 5923720 | 68737.1229
March | 211252.6587 | 185.6815 | 1094.0134 | 0 | 0.0007 | 6598190 | 76452.6927
April | 201487.2276 | 176.9228 | 1074.8219 | 0 | 0.0007 | 6482630 | 73014.308
May | 210558.9856 | 184.5841 | 1177.6956 | 0 | 0.0007 | 7103410 | 76467.922
June | 204719.889 | 179.279 | 1178.3664 | 0 | 0.0007 | 7107640 | 74449.0476
July | 209345.1405 | 183.2211 | 1224.3856 | 0 | 0.0007 | 7385330 | 76190.2576
August | 213501.5137 | 186.7416 | 1269.6501 | 0 | 0.0007 | 7658470 | 77766.8856
September | 204798.6523 | 179.1211 | 1219.4227 | 0 | 0.0007 | 7355510 | 74601.5688
October | 212810.7993 | 186.4468 | 1210.2101 | 0 | 0.0007 | 7299640 | 77346.4792
November | 207498.7938 | 182.2422 | 1099.59 | 0 | 0.0007 | 6631970 | 75170.4877
December | 212844.6105 | 187.4913 | 1028.8132 | 0 | 0.0007 | 6204510 | 76804.7466
Annual Sum or Average | 2494260 | 2188.5843 | 13589.8914 | 0 | 0.0083 | 81967100 | 904730.9997
Minimum of Months | 189945.6763 | 166.962 | 982.184 | 0 | 0.0006 | 5923720 | 68737.1229
Maximum of Months | 215499.4989 | 189.8909 | 1269.6501 | 0 | 0.0007 | 7658470 | 77766.8856
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1274520000000 | 846383.004 | 06-JAN-15:00 | 228236.782 | 379607.201 | 90172.889 | 0 | 93510.576 | 0 | 28773.072 | 19205.141 | 0 | 0 | 0 | 0 | 6877.345 | 0 | 0
February | 1214580000000 | 902231.389 | 15-FEB-15:00 | 228236.782 | 379607.201 | 92816.45 | 0 | 144421.436 | 0 | 30728.055 | 19205.141 | 0 | 0 | 0 | 0 | 7216.325 | 0 | 0
March | 1352880000000 | 865879.885 | 01-MAR-13:09 | 228236.782 | 379607.201 | 89681.299 | 0 | 112766.855 | 0 | 29371.163 | 19205.141 | 0 | 0 | 0 | 0 | 7011.444 | 0 | 0
April | 1329180000000 | 899775.518 | 13-APR-14:00 | 228236.782 | 379607.201 | 94767.844 | 0 | 140124.018 | 0 | 30407.603 | 19205.141 | 0 | 0 | 0 | 0 | 7174.973 | 0 | 0
May | 1456470000000 | 923170.492 | 25-MAY-12:09 | 228236.782 | 379607.201 | 90232.789 | 0 | 167009.224 | 0 | 31756.423 | 19205.141 | 0 | 0 | 0 | 0 | 7122.934 | 0 | 0
June | 1457330000000 | 920243.05 | 15-JUN-12:00 | 228236.782 | 379607.201 | 92234.158 | 0 | 162212.161 | 0 | 31326.082 | 19205.141 | 0 | 0 | 0 | 0 | 7421.526 | 0 | 0
July | 1514270000000 | 941647.418 | 03-JUL-12:00 | 228236.782 | 379607.201 | 91600.729 | 0 | 183181.491 | 0 | 32227.775 | 19205.141 | 0 | 0 | 0 | 0 | 7588.301 | 0 | 0
August | 1570270000000 | 936729.449 | 15-AUG-12:09 | 228236.782 | 379607.201 | 90725.54 | 0 | 179300.428 | 0 | 32133.016 | 19205.141 | 0 | 0 | 0 | 0 | 7521.341 | 0 | 0
September | 1508150000000 | 959132.774 | 28-SEP-14:00 | 228236.782 | 379607.201 | 97724.89 | 0 | 193819.282 | 0 | 32783.185 | 19205.141 | 0 | 0 | 0 | 0 | 7756.293 | 0 | 0
October | 1496700000000 | 913934.221 | 17-OCT-12:00 | 228236.782 | 379607.201 | 91677.699 | 0 | 156428.253 | 0 | 31532.731 | 19205.141 | 0 | 0 | 0 | 0 | 7246.415 | 0 | 0
November | 1359800000000 | 896609.576 | 16-NOV-15:00 | 228236.782 | 379607.201 | 90358.116 | 0 | 141212.068 | 0 | 31067.602 | 19205.141 | 0 | 0 | 0 | 0 | 6922.667 | 0 | 0
December | 1272160000000 | 847338.806 | 14-DEC-14:00 | 228236.782 | 379607.201 | 89129.028 | 0 | 95280.686 | 0 | 29115.051 | 19205.141 | 0 | 0 | 0 | 0 | 6764.916 | 0 | 0
Annual Sum or Average | 16806300000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1214580000000 | 846383.004 |  | 228236.782 | 379607.201 | 89129.028 | 0 | 93510.576 | 0 | 28773.072 | 19205.141 | 0 | 0 | 0 | 0 | 6764.916 | 0 | 0
Maximum of Months | 1570270000000 | 959132.774 |  | 228236.782 | 379607.201 | 97724.89 | 0 | 193819.282 | 0 | 32783.185 | 19205.141 | 0 | 0 | 0 | 0 | 7756.293 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 617363.45 | 167566.2 | 0 | 784929.65
Cost per Total Building Area ($/m2) | 27.53 | 7.47 | 0 | 35.01
Cost per Net Conditioned Building Area ($/m2) | 27.53 | 7.47 | 0 | 35.01

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 41365.69 | 1844.85 | 1844.85
Net Site Energy | 41365.69 | 1844.85 | 1844.85
Total Source Energy | 94563.16 | 4217.38 | 4217.38
Net Source Energy | 94563.16 | 4217.38 | 4217.38
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 18739.64 | 0 | 0 | 0 | 0
Cooling | 4079.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2557.53 | 0 | 0 | 0 | 0 | 0
Pumps | 1257.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 761.07 | 0 | 0 | 0 | 0 | 16731.2
Humidification | 5.76 | 0 | 0 | 0 | 0 | 575.76
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 704.46 | 0 | 0 | 0 | 4037.86
Refrigeration | 192.9 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19883.99 | 21481.7 | 0 | 0 | 0 | 21344.82
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.402 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.402 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.402 | 0.495 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.402 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.424 | 0.523
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2408910.5 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4557915.14 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2243051.09
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.55 | 37774.81 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.52 | 12238.55 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.47 | 24359.3 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 51.24 | 115195.47 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25325.98 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22074.33 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 31657.54 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 383592.9071 | 615.5524 | 1477.887 | 0 | 0.0062 | 91873.1997 | 157209.2964
February | 340620.9331 | 553.9111 | 1352.722 | 0 | 0.0057 | 84095.6462 | 140266.8786
March | 370549.2364 | 626.3914 | 1603.0538 | 0 | 0.0067 | 99668.8 | 154768.527
April | 349852.64 | 603.9668 | 1582.8777 | 0 | 0.0066 | 98419.4991 | 147272.7224
May | 371560.265 | 655.6461 | 1759.5224 | 0 | 0.0073 | 109408.3883 | 157709.4944
June | 377696.3684 | 679.9147 | 1862.7954 | 0 | 0.0076 | 115835.0022 | 161542.9853
July | 397192.702 | 720.1377 | 1987.2569 | 0 | 0.0081 | 123576.2821 | 170350.4261
August | 404618.5547 | 735.3248 | 2033.9271 | 0 | 0.0083 | 126479.0431 | 173692.8673
September | 365430.853 | 649.6104 | 1756.8903 | 0 | 0.0072 | 109246.5068 | 155544.9329
October | 367316.7241 | 639.5776 | 1692.0498 | 0 | 0.007 | 105209.6916 | 155123.7475
November | 358137.2702 | 607.9471 | 1563.3684 | 0 | 0.0065 | 97202.4282 | 149816.3983
December | 375126.4995 | 611.1125 | 1495.7691 | 0 | 0.0063 | 92989.0404 | 154575.7739
Annual Sum or Average | 4461690 | 7699.0926 | 20168.12 | 0 | 0.0836 | 1254000 | 1877870
Minimum of Months | 340620.9331 | 553.9111 | 1352.722 | 0 | 0.0057 | 84095.6462 | 140266.8786
Maximum of Months | 404618.5547 | 735.3248 | 2033.9271 | 0 | 0.0083 | 126479.0431 | 173692.8673
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1456780000000 | 899925.745 | 09-JAN-13:09 | 228236.782 | 379607.201 | 83470.738 | 0 | 131388.137 | 0 | 41022.951 | 29440.046 | 0 | 0 | 0 | 0 | 6759.892 | 0 | 0
February | 1333450000000 | 898536.465 | 15-FEB-15:00 | 228236.782 | 379607.201 | 86486.502 | 0 | 128127.658 | 0 | 39741.97 | 29440.046 | 0 | 0 | 0 | 0 | 6812.61 | 0 | 0
March | 1580390000000 | 977462.349 | 09-MAR-15:00 | 228236.782 | 379607.201 | 87298.366 | 0 | 200410.195 | 0 | 45117.859 | 29440.046 | 0 | 0 | 0 | 0 | 7351.901 | 0 | 0
April | 1560580000000 | 965891.419 | 04-APR-14:00 | 228236.782 | 379607.201 | 87852.373 | 0 | 188948.044 | 0 | 44493.126 | 29440.046 | 0 | 0 | 0 | 0 | 7313.848 | 0 | 0
May | 1734820000000 | 1068725.669 | 31-MAY-14:00 | 228236.782 | 379607.201 | 88604.538 | 0 | 287799.152 | 0 | 47634.096 | 29440.046 | 0 | 0 | 0 | 0 | 7403.856 | 0 | 0
June | 1836730000000 | 1164007.367 | 30-JUN-14:00 | 228236.782 | 379607.201 | 93073.569 | 0 | 376561.938 | 0 | 49285.915 | 29440.046 | 0 | 0 | 0 | 0 | 7801.916 | 0 | 0
July | 1959480000000 | 1200833.978 | 25-JUL-10:39 | 228236.782 | 379607.201 | 88359.045 | 0 | 413803.078 | 0 | 49378.28 | 29440.046 | 0 | 0 | 0 | 0 | 12009.548 | 0 | 0
August | 2005500000000 | 1216810.107 | 09-AUG-14:00 | 228236.782 | 379607.201 | 96101.893 | 0 | 421785.452 | 0 | 53880.912 | 29440.046 | 0 | 0 | 0 | 0 | 7757.822 | 0 | 0
September | 1732260000000 | 1061316.853 | 27-SEP-14:00 | 228236.782 | 379607.201 | 88269.413 | 0 | 280945.169 | 0 | 47444.882 | 29440.046 | 0 | 0 | 0 | 0 | 7373.361 | 0 | 0
October | 1668250000000 | 1022144.546 | 03-OCT-10:39 | 228236.782 | 379607.201 | 85592.653 | 0 | 241783.555 | 0 | 46297.132 | 29440.046 | 0 | 0 | 0 | 0 | 11187.177 | 0 | 0
November | 1541280000000 | 984608.555 | 03-NOV-13:00 | 228236.782 | 379607.201 | 87479.449 | 0 | 207032.83 | 0 | 45497.858 | 29440.046 | 0 | 0 | 0 | 0 | 7314.389 | 0 | 0
December | 1474470000000 | 870534.706 | 08-DEC-11:09 | 228236.782 | 379607.201 | 84560.611 | 0 | 102269.361 | 0 | 37964.27 | 29440.046 | 0 | 0 | 0 | 0 | 8390.984 | 0 | 0
Annual Sum or Average | 19884000000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1333450000000 | 870534.706 |  | 228236.782 | 379607.201 | 83470.738 | 0 | 102269.361 | 0 | 37964.27 | 29440.046 | 0 | 0 | 0 | 0 | 6759.892 | 0 | 0
Maximum of Months | 2005500000000 | 1216810.107 |  | 228236.782 | 379607.201 | 96101.893 | 0 | 421785.452 | 0 | 53880.912 | 29440.046 | 0 | 0 | 0 | 0 | 12009.548 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 309970.93 | 216239.03 | 0 | 526209.97
Cost per Total Building Area ($/m2) | 13.82 | 9.64 | 0 | 23.47
Cost per Net Conditioned Building Area ($/m2) | 13.82 | 9.64 | 0 | 23.47

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 33399.2 | 1489.56 | 1489.56
Net Site Energy | 33399.2 | 1489.56 | 1489.56
Total Source Energy | 74325.66 | 3314.82 | 3314.82
Net Source Energy | 74325.66 | 3314.82 | 3314.82
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13664.96 | 0 | 0 | 0 | 0
Cooling | 1906.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2751.3 | 0 | 0 | 0 | 0 | 0
Pumps | 746.21 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 353.44 | 0 | 0 | 0 | 0 | 12406.64
Humidification | 23.44 | 0 | 0 | 0 | 0 | 2344.47
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 691.37 | 0 | 0 | 0 | 4037.86
Refrigeration | 193.75 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17005.27 | 16393.93 | 0 | 0 | 0 | 18788.97
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.402 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.402 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.402 | 0.495 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.402 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.424 | 0.523
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1468428.91 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4029205.91 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1367323.97
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.02 | 43164.25 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.8 | 12758.25 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.91 | 26785.29 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 61.57 | 138417.16 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22388.22 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13456.12 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 19297.87 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 435365.543 | 676.6045 | 1525.0452 | 0 | 0.0062 | 1585260 | 178284.9873
February | 390815.5312 | 613.6782 | 1403.1387 | 0 | 0.0056 | 1458590 | 160660.3276
March | 439057.2718 | 698.5848 | 1625.8921 | 0 | 0.0065 | 1690220 | 181390.0354
April | 427905.9855 | 692.9814 | 1650.3016 | 0 | 0.0066 | 1715690 | 177973.7872
May | 465756.6435 | 767.8581 | 1869.7747 | 0 | 0.0074 | 1943970 | 195048.4834
June | 465500.1241 | 774.867 | 1908.9694 | 0 | 0.0075 | 1984770 | 195670.036
July | 482308.7031 | 807.2423 | 2001.6928 | 0 | 0.0079 | 2081210 | 203166.6119
August | 489699.2465 | 819.6564 | 2032.6063 | 0 | 0.008 | 2113350 | 206284.1566
September | 457290.0432 | 756.9452 | 1852.2686 | 0 | 0.0073 | 1925790 | 191801.5758
October | 444667.5273 | 721.2968 | 1721.2816 | 0 | 0.0068 | 1789500 | 185060.0386
November | 417609.3334 | 660.775 | 1526.5279 | 0 | 0.0061 | 1586900 | 172167.7787
December | 434341.8379 | 673.6892 | 1514.2908 | 0 | 0.0061 | 1574070 | 177735.86
Annual Sum or Average | 5350320 | 8664.1789 | 20631.7897 | 0 | 0.0821 | 21449300 | 2225240
Minimum of Months | 390815.5312 | 613.6782 | 1403.1387 | 0 | 0.0056 | 1458590 | 160660.3276
Maximum of Months | 489699.2465 | 819.6564 | 2032.6063 | 0 | 0.008 | 2113350 | 206284.1566
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1256810000000 | 841623.403 | 26-JAN-15:00 | 228236.782 | 379607.201 | 95718.821 | 0 | 85411.795 | 0 | 26314.287 | 17946.127 | 0 | 0 | 0 | 0 | 6851.582 | 0 | 0
February | 1156390000000 | 883670.18 | 14-FEB-15:00 | 228236.782 | 379607.201 | 96651.512 | 0 | 124586.289 | 0 | 27797.931 | 17946.127 | 0 | 0 | 0 | 0 | 7151.501 | 0 | 0
March | 1340030000000 | 887677.823 | 02-MAR-14:00 | 228236.782 | 379607.201 | 96545.844 | 0 | 128144.91 | 0 | 27958.351 | 17946.127 | 0 | 0 | 0 | 0 | 7205.52 | 0 | 0
April | 1360220000000 | 913469.923 | 21-APR-14:00 | 228236.782 | 379607.201 | 100358.101 | 0 | 149578.926 | 0 | 29163.421 | 17946.127 | 0 | 0 | 0 | 0 | 7421.997 | 0 | 0
May | 1541200000000 | 924789.751 | 19-MAY-14:00 | 228236.782 | 379607.201 | 100657.275 | 0 | 160764.475 | 0 | 29665.967 | 17946.127 | 0 | 0 | 0 | 0 | 7582.022 | 0 | 0
June | 1573550000000 | 949058.756 | 29-JUN-14:00 | 228236.782 | 379607.201 | 104063.426 | 0 | 180540.827 | 0 | 30862.693 | 17946.127 | 0 | 0 | 0 | 0 | 7765.576 | 0 | 0
July | 1650000000000 | 951113.779 | 25-JUL-14:09 | 228236.782 | 379607.201 | 99025.278 | 0 | 187131.701 | 0 | 31537.629 | 17946.127 | 0 | 0 | 0 | 0 | 7629.061 | 0 | 0
August | 1675490000000 | 965113.721 | 01-AUG-14:00 | 228236.782 | 379607.201 | 103405.325 | 0 | 196449.583 | 0 | 31641.54 | 17946.127 | 0 | 0 | 0 | 0 | 7827.164 | 0 | 0
September | 1526790000000 | 932753.982 | 05-SEP-12:50 | 228236.782 | 379607.201 | 93160.106 | 0 | 175412.413 | 0 | 31098.713 | 17946.127 | 0 | 0 | 0 | 0 | 7292.641 | 0 | 0
October | 1418730000000 | 908779.438 | 13-OCT-14:00 | 228236.782 | 379607.201 | 99285.259 | 0 | 146578.638 | 0 | 28947.925 | 17946.127 | 0 | 0 | 0 | 0 | 7403.108 | 0 | 0
November | 1258110000000 | 873572.674 | 08-NOV-15:00 | 228236.782 | 379607.201 | 96888.997 | 0 | 114863.212 | 0 | 27375.812 | 17946.127 | 0 | 0 | 0 | 0 | 7072.165 | 0 | 0
December | 1247940000000 | 832614.526 | 05-DEC-14:00 | 228236.782 | 379607.201 | 94166.794 | 0 | 77791.065 | 0 | 25957.689 | 17946.127 | 0 | 0 | 0 | 0 | 6789.663 | 0 | 0
Annual Sum or Average | 17005300000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1156390000000 | 832614.526 |  | 228236.782 | 379607.201 | 93160.106 | 0 | 77791.065 | 0 | 25957.689 | 17946.127 | 0 | 0 | 0 | 0 | 6789.663 | 0 | 0
Maximum of Months | 1675490000000 | 965113.721 |  | 228236.782 | 379607.201 | 104063.426 | 0 | 196449.583 | 0 | 31641.54 | 17946.127 | 0 | 0 | 0 | 0 | 7827.164 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 174627.75 | 117263.48 | 0 | 291891.23
Cost per Total Building Area ($/m2) | 7.79 | 5.23 | 0 | 13.02
Cost per Net Conditioned Building Area ($/m2) | 7.79 | 5.23 | 0 | 13.02

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 36652.52 | 1634.65 | 1634.65
Net Site Energy | 36652.52 | 1634.65 | 1634.65
Total Source Energy | 50491.71 | 2251.86 | 2251.86
Net Source Energy | 50491.71 | 2251.86 | 2251.86
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 17771.22 | 0 | 0 | 0 | 0
Cooling | 1306 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2524.72 | 0 | 0 | 0 | 0 | 0
Pumps | 685.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 364.01 | 0 | 0 | 0 | 0 | 6242.73
Humidification | 3.45 | 0 | 0 | 0 | 0 | 345.11
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 740.37 | 0 | 0 | 0 | 4037.86
Refrigeration | 188.96 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16103.32 | 20549.19 | 0 | 0 | 0 | 10625.7
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.402 | 0.495 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.402 | 0.495 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.402 | 0.495 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.402 | 0.495 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.402 | 0.495 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.402 | 0.495 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.402 | 0.495 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.402 | 0.495 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.402 | 0.495 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.402 | 0.495 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.402 | 0.495 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.424 | 0.523
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1657963.86 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4240706.85 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1543808.97
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.3 | 37199.87 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.38 | 11969.66 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.27 | 24015.42 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 49.7 | 111736.56 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23563.42 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15192.94 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 21788.71 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 172415.9113 | 197.2226 | 260.6952 | 0 | 0.0013 | 3438220 | 64034.2432
February | 147971.2329 | 171.9607 | 240.9724 | 0 | 0.0011 | 3178880 | 55244.7892
March | 162611.1304 | 190.6548 | 275.5452 | 0 | 0.0013 | 3635410 | 60890.5833
April | 149761.8383 | 178.2663 | 270.8624 | 0 | 0.0012 | 3574310 | 56365.7776
May | 148516.0286 | 181.9786 | 301.7799 | 0 | 0.0013 | 3983550 | 56453.3078
June | 142976.5016 | 178.519 | 311.7728 | 0 | 0.0014 | 4116170 | 54704.0833
July | 145915.1167 | 184.7126 | 334.2997 | 0 | 0.0014 | 4414080 | 56098.8071
August | 147164.0994 | 187.9866 | 347.9699 | 0 | 0.0015 | 4594900 | 56760.3019
September | 144149.6273 | 179.2279 | 309.5053 | 0 | 0.0014 | 4086080 | 55071.985
October | 153846.4395 | 185.2331 | 291.689 | 0 | 0.0013 | 3849650 | 58128.527
November | 158320.3404 | 184.4344 | 260.6788 | 0 | 0.0012 | 3438960 | 59156.4622
December | 170890.4841 | 195.279 | 257.12 | 0 | 0.0012 | 3391010 | 63446.4274
Annual Sum or Average | 1844540 | 2215.4755 | 3462.8907 | 0 | 0.0157 | 45701200 | 696355.295
Minimum of Months | 142976.5016 | 171.9607 | 240.9724 | 0 | 0.0011 | 3178880 | 54704.0833
Maximum of Months | 172415.9113 | 197.2226 | 347.9699 | 0 | 0.0015 | 4594900 | 64034.2432
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1211490000000 | 776703.447 | 27-JAN-15:00 | 228236.782 | 379607.201 | 85681.606 | 0 | 31874.837 | 0 | 24474.529 | 20262.493 | 0 | 0 | 0 | 0 | 6565.999 | 0 | 0
February | 1120110000000 | 848029.964 | 21-FEB-13:00 | 228236.782 | 379607.201 | 83169.577 | 0 | 99873.277 | 0 | 29693.272 | 20262.493 | 0 | 0 | 0 | 0 | 6898.647 | 0 | 0
March | 1280980000000 | 877879.063 | 29-MAR-14:00 | 228236.782 | 379607.201 | 88876.055 | 0 | 123108.332 | 0 | 30683.129 | 20262.493 | 0 | 0 | 0 | 0 | 7057.44 | 0 | 0
April | 1259450000000 | 862082.043 | 14-APR-14:00 | 228236.782 | 379607.201 | 87856.096 | 0 | 108708.819 | 0 | 30228.5 | 20262.493 | 0 | 0 | 0 | 0 | 6970.321 | 0 | 0
May | 1403650000000 | 921452.325 | 05-MAY-14:00 | 228236.782 | 379607.201 | 89312.376 | 0 | 163733.76 | 0 | 32983.911 | 20262.493 | 0 | 0 | 0 | 0 | 7315.803 | 0 | 0
June | 1450380000000 | 924144.835 | 28-JUN-12:00 | 228236.782 | 379607.201 | 89582.304 | 0 | 166281.173 | 0 | 32744.598 | 20262.493 | 0 | 0 | 0 | 0 | 7430.285 | 0 | 0
July | 1555350000000 | 948313.423 | 24-JUL-14:00 | 228236.782 | 379607.201 | 90386.325 | 0 | 188495.057 | 0 | 33703.28 | 20262.493 | 0 | 0 | 0 | 0 | 7622.286 | 0 | 0
August | 1619060000000 | 944344.311 | 18-AUG-14:00 | 228236.782 | 379607.201 | 91281.102 | 0 | 183509.032 | 0 | 34008.606 | 20262.493 | 0 | 0 | 0 | 0 | 7439.096 | 0 | 0
September | 1439780000000 | 949930.45 | 01-SEP-14:00 | 228236.782 | 379607.201 | 90357.191 | 0 | 189903.124 | 0 | 33999.904 | 20262.493 | 0 | 0 | 0 | 0 | 7563.755 | 0 | 0
October | 1356460000000 | 885622.852 | 17-OCT-14:00 | 228236.782 | 379607.201 | 87865.274 | 0 | 131568.715 | 0 | 30919.882 | 20262.493 | 0 | 0 | 0 | 0 | 7162.505 | 0 | 0
November | 1211760000000 | 868266.181 | 03-NOV-13:00 | 228236.782 | 379607.201 | 85204.313 | 0 | 116971.745 | 0 | 31116.546 | 20262.493 | 0 | 0 | 0 | 0 | 6867.101 | 0 | 0
December | 1194860000000 | 742508.922 | 06-DEC-11:20 | 228236.782 | 379607.201 | 83612.745 | 0 | 0 | 0 | 22394.475 | 20262.493 | 0 | 0 | 0 | 0 | 8395.226 | 0 | 0
Annual Sum or Average | 16103300000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1120110000000 | 742508.922 |  | 228236.782 | 379607.201 | 83169.577 | 0 | 0 | 0 | 22394.475 | 20262.493 | 0 | 0 | 0 | 0 | 6565.999 | 0 | 0
Maximum of Months | 1619060000000 | 949930.45 |  | 228236.782 | 379607.201 | 91281.102 | 0 | 189903.124 | 0 | 34008.606 | 20262.493 | 0 | 0 | 0 | 0 | 8395.226 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 297893.17 | 170489.97 | 0 | 468383.15
Cost per Total Building Area ($/m2) | 13.29 | 7.6 | 0 | 20.89
Cost per Net Conditioned Building Area ($/m2) | 13.29 | 7.6 | 0 | 20.89

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 41355.4 | 1844.39 | 1844.39
Net Site Energy | 41355.4 | 1844.39 | 1844.39
Total Source Energy | 88873.92 | 3963.65 | 3963.65
Net Source Energy | 88873.92 | 3963.65 | 3963.65
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 20739.49 | 0 | 0 | 0 | 0
Cooling | 2348.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2626.76 | 0 | 0 | 0 | 0 | 0
Pumps | 1128.09 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 480.02 | 0 | 0 | 0 | 0 | 11291.71
Humidification | 9.98 | 0 | 0 | 0 | 0 | 997.94
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 765.02 | 0 | 0 | 0 | 4037.86
Refrigeration | 189.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17813.29 | 23542.11 | 0 | 0 | 0 | 16327.51
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.501 | 0.622 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.501 | 0.622 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.501 | 0.622 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.501 | 0.622 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.501 | 0.622 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2419906.61 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4906694.26 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2253290.09
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.02 | 38837.97 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.7 | 12560.25 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.46 | 26024.27 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 51.87 | 116610.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27263.97 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22175.09 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 31802.05 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 588113.7874 | 927.6858 | 2363.4822 | 0 | 0.0075 | 543914.6245 | 241203.5991
February | 519909.8832 | 828.2927 | 2138.4919 | 0 | 0.0067 | 492151.4788 | 214014.2425
March | 570454.2368 | 925.6629 | 2447.3755 | 0 | 0.0076 | 563266.9013 | 236430.7946
April | 541821.5726 | 899.2904 | 2444.9636 | 0 | 0.0076 | 562745.0789 | 226484.4138
May | 619587.2428 | 1053.2459 | 2945.0511 | 0 | 0.009 | 677886.8977 | 261370.0354
June | 671599.7911 | 1158.3275 | 3292.1794 | 0 | 0.0101 | 757813.2219 | 284904.6041
July | 715546.0649 | 1238.9582 | 3536.5902 | 0 | 0.0108 | 814080.1322 | 304009.7024
August | 726990.8579 | 1259.3448 | 3596.5742 | 0 | 0.011 | 827888.5422 | 308926.697
September | 646738.3529 | 1109.5591 | 3135.0051 | 0 | 0.0096 | 721625.3815 | 273794.8772
October | 594694.5933 | 998.3445 | 2751.2804 | 0 | 0.0085 | 633266.2779 | 249665.8287
November | 542340.0249 | 885.1397 | 2357.315 | 0 | 0.0073 | 542547.7902 | 225265.8984
December | 575550.0451 | 913.1218 | 2344.4876 | 0 | 0.0074 | 539552.6392 | 236553.1535
Annual Sum or Average | 7313350 | 12196.9734 | 33352.7964 | 0 | 0.1031 | 7676740 | 3062620
Minimum of Months | 519909.8832 | 828.2927 | 2138.4919 | 0 | 0.0067 | 492151.4788 | 214014.2425
Maximum of Months | 726990.8579 | 1259.3448 | 3596.5742 | 0 | 0.011 | 827888.5422 | 308926.697
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1262110000000 | 784135.6 | 17-JAN-14:09 | 228236.782 | 379607.201 | 86076.638 | 0 | 20232.689 | 0 | 33741.609 | 29574.432 | 0 | 0 | 0 | 0 | 6548.385 | 0 | 0
February | 1142000000000 | 790369.808 | 28-FEB-11:50 | 228236.782 | 379607.201 | 86780.92 | 0 | 24148.761 | 0 | 33958.912 | 29574.432 | 0 | 0 | 0 | 0 | 7802.998 | 0 | 0
March | 1307020000000 | 932583.234 | 31-MAR-14:00 | 228236.782 | 379607.201 | 90109.474 | 0 | 156272.968 | 0 | 41571.206 | 29574.432 | 0 | 0 | 0 | 0 | 7189.357 | 0 | 0
April | 1305810000000 | 956131.356 | 03-APR-13:50 | 228236.782 | 379607.201 | 86931.96 | 0 | 180656.66 | 0 | 44036.58 | 29574.432 | 0 | 0 | 0 | 0 | 7087.741 | 0 | 0
May | 1572990000000 | 1023863.994 | 30-MAY-09:00 | 228236.782 | 379607.201 | 85542.173 | 0 | 247167.209 | 0 | 46555.333 | 29574.432 | 0 | 0 | 0 | 0 | 7180.864 | 0 | 0
June | 1758450000000 | 1172859.24 | 08-JUN-12:00 | 228236.782 | 379607.201 | 92984.258 | 0 | 385267.982 | 0 | 49438.325 | 29574.432 | 0 | 0 | 0 | 0 | 7750.26 | 0 | 0
July | 1889010000000 | 1156721.659 | 13-JUL-12:00 | 228236.782 | 379607.201 | 93954.527 | 0 | 368268.471 | 0 | 49300.218 | 29574.432 | 0 | 0 | 0 | 0 | 7780.027 | 0 | 0
August | 1921050000000 | 1201110.392 | 04-AUG-14:00 | 228236.782 | 379607.201 | 95309.467 | 0 | 410359.334 | 0 | 50367.984 | 29574.432 | 0 | 0 | 0 | 0 | 7655.192 | 0 | 0
September | 1674480000000 | 1046209.769 | 07-SEP-13:09 | 228236.782 | 379607.201 | 90975.846 | 0 | 262625.2 | 0 | 47895.955 | 29574.432 | 0 | 0 | 0 | 0 | 7294.353 | 0 | 0
October | 1469450000000 | 1004754.704 | 30-OCT-10:50 | 228236.782 | 379607.201 | 85626.349 | 0 | 229488.969 | 0 | 45178.166 | 29574.432 | 0 | 0 | 0 | 0 | 7042.805 | 0 | 0
November | 1258940000000 | 1011768.012 | 02-NOV-09:20 | 228236.782 | 379607.201 | 85790.249 | 0 | 236133.417 | 0 | 45429.667 | 29574.432 | 0 | 0 | 0 | 0 | 6996.264 | 0 | 0
December | 1251990000000 | 795413.199 | 12-DEC-13:09 | 228236.782 | 379607.201 | 86860.688 | 0 | 30258.051 | 0 | 34323.739 | 29574.432 | 0 | 0 | 0 | 0 | 6552.306 | 0 | 0
Annual Sum or Average | 17813300000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1142000000000 | 784135.6 |  | 228236.782 | 379607.201 | 85542.173 | 0 | 20232.689 | 0 | 33741.609 | 29574.432 | 0 | 0 | 0 | 0 | 6548.385 | 0 | 0
Maximum of Months | 1921050000000 | 1201110.392 |  | 228236.782 | 379607.201 | 95309.467 | 0 | 410359.334 | 0 | 50367.984 | 29574.432 | 0 | 0 | 0 | 0 | 7802.998 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 477301.69 | 208523.37 | 0 | 685825.05
Cost per Total Building Area ($/m2) | 21.29 | 9.3 | 0 | 30.59
Cost per Net Conditioned Building Area ($/m2) | 21.29 | 9.3 | 0 | 30.59

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 35546.68 | 1585.33 | 1585.33
Net Site Energy | 35546.68 | 1585.33 | 1585.33
Total Source Energy | 75693.28 | 3375.81 | 3375.81
Net Source Energy | 75693.28 | 3375.81 | 3375.81
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16181.05 | 0 | 0 | 0 | 0
Cooling | 1486.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2806.97 | 0 | 0 | 0 | 0 | 0
Pumps | 728.47 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 302.64 | 0 | 0 | 0 | 0 | 9649.06
Humidification | 21.6 | 0 | 0 | 0 | 0 | 2160.5
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 761.85 | 0 | 0 | 0 | 4037.86
Refrigeration | 189.85 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16566.17 | 18980.5 | 0 | 0 | 0 | 15847.42
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.501 | 0.622 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.501 | 0.622 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.501 | 0.622 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.501 | 0.622 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.501 | 0.622 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.501 | 0.622 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 186.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1495669.88 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4351623.21 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1392689.33
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.34 | 43906.56 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.94 | 13014.11 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.95 | 28537.37 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 60.75 | 136592.06 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24179.72 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13705.74 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 19655.87 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 453908.6984 | 696.0092 | 1539.05 | 0 | 0.0062 | 1599740 | 184955.1716
February | 402286.7388 | 621.7278 | 1390.3988 | 0 | 0.0056 | 1445270 | 164398.7591
March | 447064.574 | 701.7875 | 1603.9211 | 0 | 0.0064 | 1667310 | 183762.5805
April | 426383.1397 | 681.4023 | 1595.1052 | 0 | 0.0064 | 1658240 | 176446.5367
May | 450290.3412 | 729.8051 | 1739.7323 | 0 | 0.0069 | 1808670 | 187340.045
June | 455280.1864 | 748.6079 | 1817.0087 | 0 | 0.0072 | 1889090 | 190467.1121
July | 485598.3232 | 808.4118 | 1991.8749 | 0 | 0.0079 | 2070970 | 204126.9734
August | 487341.412 | 807.9296 | 1980.7088 | 0 | 0.0078 | 2059330 | 204527.7633
September | 443526.3397 | 725.171 | 1747.8527 | 0 | 0.0069 | 1817160 | 185146.7003
October | 442362.6169 | 709.8462 | 1670.6196 | 0 | 0.0067 | 1736770 | 183344.3486
November | 425723.7856 | 665.0503 | 1509.8365 | 0 | 0.0061 | 1569480 | 174673.0826
December | 449214.518 | 687.0771 | 1513.7477 | 0 | 0.0061 | 1573430 | 182872.3246
Annual Sum or Average | 5368980 | 8582.826 | 20099.8562 | 0 | 0.0803 | 20895500 | 2222060
Minimum of Months | 402286.7388 | 621.7278 | 1390.3988 | 0 | 0.0056 | 1445270 | 164398.7591
Maximum of Months | 487341.412 | 808.4118 | 1991.8749 | 0 | 0.0079 | 2070970 | 204527.7633
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1268290000000 | 863100.582 | 24-JAN-13:00 | 228236.782 | 379607.201 | 95129.795 | 0 | 105191.553 | 0 | 27302.359 | 18279.047 | 0 | 0 | 0 | 0 | 6971.947 | 0 | 0
February | 1145830000000 | 842218.634 | 07-FEB-14:00 | 228236.782 | 379607.201 | 96540.645 | 0 | 83470.08 | 0 | 26680.541 | 18279.047 | 0 | 0 | 0 | 0 | 6829.317 | 0 | 0
March | 1321860000000 | 900512.23 | 30-MAR-14:00 | 228236.782 | 379607.201 | 100215.689 | 0 | 135826.971 | 0 | 28867.295 | 18279.047 | 0 | 0 | 0 | 0 | 7219.308 | 0 | 0
April | 1314670000000 | 908250.213 | 25-APR-14:00 | 228236.782 | 379607.201 | 101662.95 | 0 | 143698.206 | 0 | 29288.739 | 18279.047 | 0 | 0 | 0 | 0 | 7346.845 | 0 | 0
May | 1433940000000 | 921104.83 | 23-MAY-14:00 | 228236.782 | 379607.201 | 102634.296 | 0 | 154739.824 | 0 | 29814.952 | 18279.047 | 0 | 0 | 0 | 0 | 7480.886 | 0 | 0
June | 1497690000000 | 945310.917 | 30-JUN-10:09 | 228236.782 | 379607.201 | 95124.718 | 0 | 183572.517 | 0 | 31909.718 | 18279.047 | 0 | 0 | 0 | 0 | 8580.935 | 0 | 0
July | 1641890000000 | 970767.948 | 25-JUL-13:20 | 228236.782 | 379607.201 | 96754.237 | 0 | 207645.637 | 0 | 33023.075 | 18279.047 | 0 | 0 | 0 | 0 | 7221.969 | 0 | 0
August | 1632660000000 | 953162.39 | 30-AUG-13:00 | 228236.782 | 379607.201 | 103738.242 | 0 | 184332.982 | 0 | 31158.605 | 18279.047 | 0 | 0 | 0 | 0 | 7809.531 | 0 | 0
September | 1440670000000 | 934284.138 | 06-SEP-14:00 | 228236.782 | 379607.201 | 102261.139 | 0 | 167058.373 | 0 | 30295.504 | 18279.047 | 0 | 0 | 0 | 0 | 7637.278 | 0 | 0
October | 1376930000000 | 923601.685 | 05-OCT-14:00 | 228236.782 | 379607.201 | 102071.163 | 0 | 157188.812 | 0 | 29861.809 | 18279.047 | 0 | 0 | 0 | 0 | 7509.79 | 0 | 0
November | 1244300000000 | 887063.014 | 10-NOV-13:00 | 228236.782 | 379607.201 | 96765.372 | 0 | 127111.978 | 0 | 28239.19 | 18279.047 | 0 | 0 | 0 | 0 | 7152.583 | 0 | 0
December | 1247430000000 | 832656.651 | 29-DEC-14:00 | 228236.782 | 379607.201 | 95754.962 | 0 | 75253.672 | 0 | 26210.344 | 18279.047 | 0 | 0 | 0 | 0 | 6740.08 | 0 | 0
Annual Sum or Average | 16566200000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1145830000000 | 832656.651 |  | 228236.782 | 379607.201 | 95124.718 | 0 | 75253.672 | 0 | 26210.344 | 18279.047 | 0 | 0 | 0 | 0 | 6740.08 | 0 | 0
Maximum of Months | 1641890000000 | 970767.948 |  | 228236.782 | 379607.201 | 103738.242 | 0 | 207645.637 | 0 | 33023.075 | 18279.047 | 0 | 0 | 0 | 0 | 8580.935 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 170123.6 | 135818.97 | 0 | 305942.57
Cost per Total Building Area ($/m2) | 7.59 | 6.06 | 0 | 13.64
Cost per Net Conditioned Building Area ($/m2) | 7.59 | 6.06 | 0 | 13.64

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 43166.63 | 1925.17 | 1925.17
Net Site Energy | 43166.63 | 1925.17 | 1925.17
Total Source Energy | 88229.5 | 3934.91 | 3934.91
Net Source Energy | 88229.5 | 3934.91 | 3934.91
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 22788.63 | 0 | 0 | 0 | 0
Cooling | 2137.53 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2643.43 | 0 | 0 | 0 | 0 | 0
Pumps | 1079.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 432.38 | 0 | 0 | 0 | 0 | 10164.86
Humidification | 10.99 | 0 | 0 | 0 | 0 | 1099.42
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 817.35 | 0 | 0 | 0 | 4037.86
Refrigeration | 188.48 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17523.04 | 25643.59 | 0 | 0 | 0 | 15302.14
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.501 | 0.622 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.501 | 0.622 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.501 | 0.622 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.651 | 0.813 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.813 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.501 | 0.622 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.651 | 0.813 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.651 | 0.813 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.813 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.651 | 0.813 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.651 | 0.813 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.813 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.501 | 0.622 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.651 | 0.813 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.651 | 0.813 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.534 | 0.664
North Total or Average |  |  | 186.18 | 3.18 | 0.651 | 0.813
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2292045.41 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5074717.96 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2134232.45
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.2 | 39252.96 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.7 | 12571.81 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.75 | 26512.11 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 51.96 | 116810.08 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28197.59 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21003.42 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 30121.71 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 468291.2303 | 678.427 | 827.1288 | 0 | 0.0064 | 543059.7819 | 186293.9054
February | 403795.1595 | 595.8224 | 748.4845 | 0 | 0.0058 | 491492.6957 | 161671.7798
March | 417104.9266 | 641.6908 | 858.562 | 0 | 0.0065 | 563931.2103 | 169507.9059
April | 387515.8192 | 618.9002 | 871.6703 | 0 | 0.0066 | 572662.987 | 159655.8732
May | 428408.1452 | 708.1482 | 1041.6018 | 0 | 0.0078 | 684420.6353 | 178791.6904
June | 450456.4621 | 758.5538 | 1140.6654 | 0 | 0.0085 | 749577.114 | 189327.7398
July | 474380.5758 | 802.9952 | 1214.7731 | 0 | 0.009 | 798294.3676 | 199780.1573
August | 482891.1952 | 817.7163 | 1237.5923 | 0 | 0.0092 | 813291.4853 | 203394.4178
September | 420681.774 | 697.5065 | 1029.7515 | 0 | 0.0077 | 676643.5979 | 175770.7506
October | 398393.1787 | 636.1847 | 895.8518 | 0 | 0.0067 | 588549.1343 | 164128.9374
November | 396880.0487 | 607.866 | 808.1069 | 0 | 0.0062 | 530776.1607 | 161029.6375
December | 448283.7738 | 658.3483 | 820.7919 | 0 | 0.0063 | 538954.8305 | 179185.9739
Annual Sum or Average | 5177080 | 8222.1594 | 11494.9802 | 0 | 0.0866 | 7551650 | 2128540
Minimum of Months | 387515.8192 | 595.8224 | 748.4845 | 0 | 0.0058 | 491492.6957 | 159655.8732
Maximum of Months | 482891.1952 | 817.7163 | 1237.5923 | 0 | 0.0092 | 813291.4853 | 203394.4178
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1260130000000 | 738696.523 | 04-JAN-11:39 | 228236.782 | 379607.201 | 86382.883 | 0 | 742.906 | 0 | 34188.269 | 0 | 0 | 0 | 0 | 0 | 8772.768 | 0 | 0
February | 1140470000000 | 739016.796 | 03-FEB-11:39 | 228236.782 | 379607.201 | 87072.206 | 0 | 1572.056 | 0 | 32837.844 | 0 | 0 | 0 | 0 | 0 | 8786.43 | 0 | 0
March | 1308560000000 | 884470.39 | 23-MAR-14:00 | 228236.782 | 379607.201 | 90698.698 | 0 | 113571.337 | 0 | 37400.1 | 28011.801 | 0 | 0 | 0 | 0 | 6898.204 | 0 | 0
April | 1328820000000 | 925086.978 | 14-APR-14:00 | 228236.782 | 379607.201 | 92111.913 | 0 | 149914.684 | 0 | 39999.545 | 28011.801 | 0 | 0 | 0 | 0 | 7139.806 | 0 | 0
May | 1588150000000 | 1005719.476 | 31-MAY-12:20 | 228236.782 | 379607.201 | 91217.284 | 0 | 226724.428 | 0 | 44384.915 | 28011.801 | 0 | 0 | 0 | 0 | 7537.065 | 0 | 0
June | 1739340000000 | 1121461.169 | 29-JUN-14:00 | 228236.782 | 379607.201 | 97379.671 | 0 | 333376.047 | 0 | 47114.824 | 28011.801 | 0 | 0 | 0 | 0 | 7734.844 | 0 | 0
July | 1852380000000 | 1152389.517 | 13-JUL-14:00 | 228236.782 | 379607.201 | 94240.621 | 0 | 367188.9 | 0 | 47404.468 | 28011.801 | 0 | 0 | 0 | 0 | 7699.745 | 0 | 0
August | 1887180000000 | 1130365.642 | 25-AUG-14:00 | 228236.782 | 379607.201 | 96078.186 | 0 | 343483.606 | 0 | 47289.389 | 28011.801 | 0 | 0 | 0 | 0 | 7658.677 | 0 | 0
September | 1570100000000 | 1028732.245 | 22-SEP-12:30 | 228236.782 | 379607.201 | 89537.238 | 0 | 251874.167 | 0 | 44326.321 | 28011.801 | 0 | 0 | 0 | 0 | 7138.736 | 0 | 0
October | 1365680000000 | 934472.446 | 06-OCT-14:00 | 228236.782 | 379607.201 | 91922.478 | 0 | 158988.029 | 0 | 40453.564 | 28011.801 | 0 | 0 | 0 | 0 | 7252.591 | 0 | 0
November | 1231630000000 | 905127.998 | 02-NOV-14:00 | 228236.782 | 379607.201 | 90575.992 | 0 | 132756.561 | 0 | 38880.826 | 28011.801 | 0 | 0 | 0 | 0 | 7058.835 | 0 | 0
December | 1250600000000 | 738603.743 | 29-DEC-11:39 | 228236.782 | 379607.201 | 87074.462 | 0 | 2045.243 | 0 | 31806.693 | 0 | 0 | 0 | 0 | 0 | 8811.744 | 0 | 0
Annual Sum or Average | 17523000000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1140470000000 | 738603.743 |  | 228236.782 | 379607.201 | 86382.883 | 0 | 742.906 | 0 | 31806.693 | 0 | 0 | 0 | 0 | 0 | 6898.204 | 0 | 0
Maximum of Months | 1887180000000 | 1152389.517 |  | 228236.782 | 379607.201 | 97379.671 | 0 | 367188.9 | 0 | 47404.468 | 28011.801 | 0 | 0 | 0 | 0 | 8811.744 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 259800.03 | 204049.29 | 0 | 463849.32
Cost per Total Building Area ($/m2) | 11.59 | 9.1 | 0 | 20.69
Cost per Net Conditioned Building Area ($/m2) | 11.59 | 9.1 | 0 | 20.69

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 38447.8 | 1714.72 | 1714.72
Net Site Energy | 38447.8 | 1714.72 | 1714.72
Total Source Energy | 80212.38 | 3577.36 | 3577.36
Net Source Energy | 80212.38 | 3577.36 | 3577.36
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 19548.36 | 0 | 0 | 0 | 0
Cooling | 1093.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2763.55 | 0 | 0 | 0 | 0 | 0
Pumps | 694.52 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 248.09 | 0 | 0 | 0 | 0 | 6960.81
Humidification | 18.79 | 0 | 0 | 0 | 0 | 1878.99
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 826.87 | 0 | 0 | 0 | 4037.86
Refrigeration | 186.32 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16034.97 | 22412.83 | 0 | 0 | 0 | 12877.66
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.501 | 0.622 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.501 | 0.622 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.501 | 0.622 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.651 | 0.813 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.813 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.501 | 0.622 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.501 | 0.622 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.651 | 0.813 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.651 | 0.813 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.813 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.622 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.651 | 0.813 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.651 | 0.813 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.622 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.813 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.622 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.622 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.501 | 0.622 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.651 | 0.813 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.622 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.651 | 0.813 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.534 | 0.664
North Total or Average |  |  | 186.18 | 3.18 | 0.651 | 0.813
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1475048.83 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4781158.39 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1373488.09
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.69 | 42647.53 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.84 | 12825.75 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.88 | 28421.14 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 57.64 | 129586.08 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26566.43 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13516.78 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 19384.87 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 446877.5152 | 659.8303 | 921.3374 | 0 | 0.0067 | 21838400 | 179236.6343
February | 393420.1171 | 588.2599 | 837.7453 | 0 | 0.0061 | 19858600 | 158507.1555
March | 418723.7383 | 647.9362 | 970.6152 | 0 | 0.007 | 23012800 | 170813.1149
April | 385296.4822 | 603.8014 | 920.5818 | 0 | 0.0066 | 21828000 | 157910.6394
May | 402889.7852 | 645.7085 | 1014.4651 | 0 | 0.0072 | 24056700 | 166506.9308
June | 408680.6196 | 668.4346 | 1077.6704 | 0 | 0.0076 | 25557900 | 170199.8281
July | 428561.8549 | 709.1904 | 1159.89 | 0 | 0.0082 | 27509200 | 179275.9437
August | 432265.105 | 713.4969 | 1163.3244 | 0 | 0.0082 | 27590400 | 180648.9916
September | 399593.5036 | 648.1561 | 1034.1224 | 0 | 0.0073 | 24524200 | 165891.8936
October | 402817.387 | 636.0554 | 979.792 | 0 | 0.007 | 23232800 | 165555.1215
November | 398128.7467 | 610.8269 | 903.9233 | 0 | 0.0065 | 21430600 | 161905.0864
December | 436310.5958 | 648.6871 | 915.6781 | 0 | 0.0066 | 21705200 | 175429.4259
Annual Sum or Average | 4953570 | 7780.3837 | 11899.1454 | 0 | 0.0849 | 282145000 | 2031880
Minimum of Months | 385296.4822 | 588.2599 | 837.7453 | 0 | 0.0061 | 19858600 | 157910.6394
Maximum of Months | 446877.5152 | 713.4969 | 1163.3244 | 0 | 0.0082 | 27590400 | 180648.9916
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1241130000000 | 734038.538 | 25-JAN-11:39 | 228236.782 | 379607.201 | 91774.998 | 0 | 3845.259 | 0 | 20271.447 | 0 | 0 | 0 | 0 | 0 | 9046.632 | 0 | 0
February | 1128610000000 | 852792.828 | 02-FEB-14:00 | 228236.782 | 379607.201 | 93717.835 | 0 | 99290.658 | 0 | 26940.948 | 18027.031 | 0 | 0 | 0 | 0 | 6960.421 | 0 | 0
March | 1307870000000 | 883095.535 | 30-MAR-14:00 | 228236.782 | 379607.201 | 96701.348 | 0 | 124473.745 | 0 | 27979.031 | 18027.031 | 0 | 0 | 0 | 0 | 7126.409 | 0 | 0
April | 1240540000000 | 877559.594 | 06-APR-14:00 | 228236.782 | 379607.201 | 95974.621 | 0 | 118861.458 | 0 | 27662.576 | 18027.031 | 0 | 0 | 0 | 0 | 7067.594 | 0 | 0
May | 1367200000000 | 902927.517 | 16-MAY-14:00 | 228236.782 | 379607.201 | 98348.155 | 0 | 142183.876 | 0 | 28880.976 | 18027.031 | 0 | 0 | 0 | 0 | 7317.979 | 0 | 0
June | 1452520000000 | 957914.421 | 30-JUN-12:00 | 228236.782 | 379607.201 | 99897.13 | 0 | 193004.127 | 0 | 31320.882 | 18027.031 | 0 | 0 | 0 | 0 | 7821.268 | 0 | 0
July | 1563410000000 | 948965.872 | 21-JUL-14:00 | 228236.782 | 379607.201 | 103342.66 | 0 | 180960.377 | 0 | 31036.977 | 18027.031 | 0 | 0 | 0 | 0 | 7754.845 | 0 | 0
August | 1568030000000 | 937140.212 | 09-AUG-14:00 | 228236.782 | 379607.201 | 101077.19 | 0 | 172089.147 | 0 | 30411.821 | 18027.031 | 0 | 0 | 0 | 0 | 7678.808 | 0 | 0
September | 1393770000000 | 921151.095 | 12-SEP-14:30 | 228236.782 | 379607.201 | 98418.443 | 0 | 159301.574 | 0 | 30135.485 | 18027.031 | 0 | 0 | 0 | 0 | 7424.58 | 0 | 0
October | 1320380000000 | 895308.015 | 06-OCT-14:00 | 228236.782 | 379607.201 | 98426.299 | 0 | 135147.275 | 0 | 28594.27 | 18027.031 | 0 | 0 | 0 | 0 | 7221.133 | 0 | 0
November | 1217950000000 | 827521.771 | 21-NOV-11:39 | 228236.782 | 379607.201 | 91756.648 | 0 | 72758.928 | 0 | 25748.686 | 18027.031 | 0 | 0 | 0 | 0 | 9809.855 | 0 | 0
December | 1233560000000 | 736687.518 | 01-DEC-14:00 | 228236.782 | 379607.201 | 93390.257 | 0 | 5482.437 | 0 | 20336.696 | 1486.46 | 0 | 0 | 0 | 0 | 6417.441 | 0 | 0
Annual Sum or Average | 16035000000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1128610000000 | 734038.538 |  | 228236.782 | 379607.201 | 91756.648 | 0 | 3845.259 | 0 | 20271.447 | 0 | 0 | 0 | 0 | 0 | 6417.441 | 0 | 0
Maximum of Months | 1568030000000 | 957914.421 |  | 228236.782 | 379607.201 | 103342.66 | 0 | 193004.127 | 0 | 31320.882 | 18027.031 | 0 | 0 | 0 | 0 | 9809.855 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 313674.09 | 193795.88 | 0 | 507469.98
Cost per Total Building Area ($/m2) | 13.99 | 8.64 | 0 | 22.63
Cost per Net Conditioned Building Area ($/m2) | 13.99 | 8.64 | 0 | 22.63

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 43557.82 | 1942.62 | 1942.62
Net Site Energy | 43557.82 | 1942.62 | 1942.62
Total Source Energy | 85395.94 | 3808.54 | 3808.54
Net Source Energy | 85395.94 | 3808.54 | 3808.54
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 24483.99 | 0 | 0 | 0 | 0
Cooling | 1136.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2614.46 | 0 | 0 | 0 | 0 | 0
Pumps | 877.48 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 276.64 | 0 | 0 | 0 | 0 | 5497.96
Humidification | 13.52 | 0 | 0 | 0 | 0 | 1351.66
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 903.69 | 0 | 0 | 0 | 4037.86
Refrigeration | 183.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16132.54 | 27425.28 | 0 | 0 | 0 | 10887.48
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.357 | 0.38 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 3.18 | 0.501 | 0.49 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 3.18 | 0.501 | 0.49 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 3.18 | 0.501 | 0.49 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 3.18 | 0.651 | 0.64 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.64 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 3.18 | 0.501 | 0.49 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 3.18 | 0.501 | 0.49 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.49 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.49 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.49 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.49 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.651 | 0.64 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.651 | 0.64 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.49 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.49 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.64 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 3.18 | 0.501 | 0.49 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 3.18 | 0.501 | 0.49 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.49 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 3.18 | 0.651 | 0.64 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 3.18 | 0.651 | 0.64 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 3.18 | 0.501 | 0.49 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 3.18 | 0.501 | 0.49 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 3.18 | 0.651 | 0.64 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 3.18 | 0.501 | 0.49 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 3.18 | 0.501 | 0.49 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 3.18 | 0.501 | 0.49 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.49 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 3.18 | 0.501 | 0.49 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 3.18 | 0.651 | 0.64 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 3.18 | 0.501 | 0.49 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 3.18 | 0.651 | 0.64 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 3.18 | 0.534 | 0.523
North Total or Average |  |  | 186.18 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 659.24 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1969943.19 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5031723 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1834307.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.11 | 39043.99 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.64 | 12459.31 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.33 | 25804.07 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 51.79 | 116431.42 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27958.69 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18051.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 25888.7 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 466688.7443 | 674.2311 | 818.1951 | 0 | 0.0064 | 537182.5656 | 185477.2447
February | 411571.7597 | 600.4598 | 740.6356 | 0 | 0.0057 | 486298.0338 | 164131.8128
March | 428009.5817 | 644.3307 | 834.9779 | 0 | 0.0064 | 548364.7142 | 172588.226
April | 376527.365 | 585.7684 | 796.2149 | 0 | 0.006 | 523014.4742 | 153639.1958
May | 387675.7472 | 623.574 | 886.4168 | 0 | 0.0067 | 582372.6702 | 160144.0949
June | 402444.1892 | 666.9305 | 984.0107 | 0 | 0.0073 | 646586.074 | 168118.4098
July | 437874.1849 | 736.7918 | 1106.9356 | 0 | 0.0082 | 727409.4327 | 183984.5367
August | 429910.0006 | 718.1983 | 1069.8946 | 0 | 0.0079 | 703045.7105 | 180141.8339
September | 383288.2365 | 623.4314 | 898.9002 | 0 | 0.0067 | 590607.6232 | 158992.624
October | 385073.7742 | 606.8561 | 839.6592 | 0 | 0.0063 | 551592.635 | 157871.3008
November | 402175.4801 | 608.7794 | 795.4542 | 0 | 0.0061 | 522426.7315 | 162490.2521
December | 453870.3776 | 660.8796 | 812.5477 | 0 | 0.0063 | 533507.3203 | 180876.7389
Annual Sum or Average | 4965110 | 7750.2311 | 10583.8425 | 0 | 0.0801 | 6952410 | 2028460
Minimum of Months | 376527.365 | 585.7684 | 740.6356 | 0 | 0.0057 | 486298.0338 | 153639.1958
Maximum of Months | 466688.7443 | 736.7918 | 1106.9356 | 0 | 0.0082 | 727409.4327 | 185477.2447
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1246490000000 | 733687.704 | 26-JAN-11:39 | 228236.782 | 379607.201 | 86193.423 | 0 | 759.121 | 0 | 29298.458 | 0 | 0 | 0 | 0 | 0 | 8774.317 | 0 | 0
February | 1128420000000 | 737692.871 | 28-FEB-15:00 | 228236.782 | 379607.201 | 88240.403 | 0 | 3660.622 | 0 | 26701.506 | 3631.239 | 0 | 0 | 0 | 0 | 6444.497 | 0 | 0
March | 1272440000000 | 736163.733 | 21-MAR-14:00 | 228236.782 | 379607.201 | 88545.679 | 0 | 5019.79 | 0 | 26799.239 | 0 | 0 | 0 | 0 | 0 | 6308.073 | 0 | 0
April | 1213620000000 | 872773.393 | 04-APR-14:00 | 228236.782 | 379607.201 | 89874.416 | 0 | 110029.717 | 0 | 33835.702 | 24075.289 | 0 | 0 | 0 | 0 | 6934.893 | 0 | 0
May | 1351350000000 | 917573.005 | 31-MAY-14:00 | 228236.782 | 379607.201 | 93216.831 | 0 | 148914.993 | 0 | 36125.615 | 24075.289 | 0 | 0 | 0 | 0 | 7198.279 | 0 | 0
June | 1500350000000 | 1033809.89 | 14-JUN-14:00 | 228236.782 | 379607.201 | 94423.064 | 0 | 259062.286 | 0 | 40908.527 | 24075.289 | 0 | 0 | 0 | 0 | 7496.74 | 0 | 0
July | 1687900000000 | 1050002.446 | 31-JUL-14:00 | 228236.782 | 379607.201 | 89941.026 | 0 | 280902.337 | 0 | 40105.06 | 24075.289 | 0 | 0 | 0 | 0 | 7134.751 | 0 | 0
August | 1631360000000 | 1038133.55 | 11-AUG-14:00 | 228236.782 | 379607.201 | 95311.173 | 0 | 262379.049 | 0 | 40948.6 | 24075.289 | 0 | 0 | 0 | 0 | 7575.454 | 0 | 0
September | 1370460000000 | 1007009.899 | 08-SEP-13:20 | 228236.782 | 379607.201 | 91549.152 | 0 | 236716.361 | 0 | 39636.856 | 24075.289 | 0 | 0 | 0 | 0 | 7188.258 | 0 | 0
October | 1279930000000 | 884521.694 | 27-OCT-14:00 | 228236.782 | 379607.201 | 90717.637 | 0 | 120143.308 | 0 | 34722.65 | 24075.289 | 0 | 0 | 0 | 0 | 7010.705 | 0 | 0
November | 1212250000000 | 839741.767 | 09-NOV-11:39 | 228236.782 | 379607.201 | 87242.18 | 0 | 78936.256 | 0 | 32038.939 | 24075.289 | 0 | 0 | 0 | 0 | 9605.12 | 0 | 0
December | 1237960000000 | 733734.068 | 29-DEC-11:39 | 228236.782 | 379607.201 | 86525.455 | 0 | 1910.22 | 0 | 27690.573 | 0 | 0 | 0 | 0 | 0 | 8806.619 | 0 | 0
Annual Sum or Average | 16132500000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1128420000000 | 733687.704 |  | 228236.782 | 379607.201 | 86193.423 | 0 | 759.121 | 0 | 26701.506 | 0 | 0 | 0 | 0 | 0 | 6308.073 | 0 | 0
Maximum of Months | 1687900000000 | 1050002.446 |  | 228236.782 | 379607.201 | 95311.173 | 0 | 280902.337 | 0 | 40948.6 | 24075.289 | 0 | 0 | 0 | 0 | 9605.12 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 240962.23 | 218043.66 | 0 | 459005.89
Cost per Total Building Area ($/m2) | 10.75 | 9.72 | 0 | 20.47
Cost per Net Conditioned Building Area ($/m2) | 10.75 | 9.72 | 0 | 20.47

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 50695.45 | 2260.94 | 2260.94
Net Site Energy | 50695.45 | 2260.94 | 2260.94
Total Source Energy | 93216.09 | 4157.3 | 4157.3
Net Source Energy | 93216.09 | 4157.3 | 4157.3
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 32384.9 | 0 | 0 | 0 | 0
Cooling | 654.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4029.97 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 7000.33 | 2037.6 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2616.49 | 0 | 0 | 0 | 0 | 0
Pumps | 615.51 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 150.03 | 0 | 0 | 0 | 0 | 3341.37
Humidification | 16.44 | 0 | 0 | 0 | 0 | 1643.96
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1008.17 | 0 | 0 | 0 | 4037.86
Refrigeration | 181.38 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15264.78 | 35430.67 | 0 | 0 | 0 | 9023.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 10.76 | 37.17 | 8.07
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM4_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 13.93 | 32.28
ER_EXAM5_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 13.93 | 32.28
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
LOBBY_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 13.99 | 18.59 | 1.08
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
ER_NURSESTAT_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 10.76 | 46.51 | 8.07
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 53.8
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 53.8
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 53.8
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 53.8
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 13.93 | 10.76
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 10.45 | 10.76
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 46.51 | 10.76
ICU_NURSESAT_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 18.59 | 10.76
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
OR_NURSESAT_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 10.76 | 18.59 | 8.07
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 4.64 | 16.15
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 23.2 | 10.76
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 13.93 | 10.76
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.8
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 13.48 | 10.76
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 10.76
NURSESAT_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 3.72 | 32.28
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 1.39 | 2.69
NURSESAT_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 10.76 | 18.59 | 8.07
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 538.2517
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 18.59 | 8.07
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 18.59 | 8.07
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.95 | 8.07
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 328.4454
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 11.31 | 14.17 | 39.1797
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 0 | 90 | N
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 90 | 90 | E
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.9 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.9 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.9 | 3739.35 | 0 | 180
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 104.08 | 180 | 90 | S
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 78.06 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 0 | 90 | N
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 90 | 90 | E
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 104.08 | 0 | 90 | N
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 52.04 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 123.59 | 0 | 90 | N
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 32.5 | 180 | 90 | S
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 180 | 90 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 110.58 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 39.03 | 0 | 90 | N
OR1_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 90 | 90 | E
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 39.03 | 0 | 90 | N
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 117.09 | 270 | 90 | W
ICU_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 91.09 | 270 | 90 | W
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 180 | 90 | S
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 130.1 | 180 | 90 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 32.52 | 0 | 90 | N
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 0 | 90 | N
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 195.15 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 188.66 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 90 | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 195.15 | 0 | 90 | N
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 188.66 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 19.51 | 270 | 90 | W
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 180 | 90 | S
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 45.53 | 0 | 90 | N
DINING_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 696.77 | 90 | 0
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 1040.51 | 90 | 0
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 929.03 | 180 | 0
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 69.7 | 180 | 0
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS | 0.08 | 0.404 | 0.43 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 83.61 | 180 | 0
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS | 0.08 | 0.404 | 0.43 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOFS | 0.3 | 0.273 | 0.29 | 501.68 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 2.96 | 11.86 | 2.58 | 0.504 | 0.49 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
LOBBY_FLR_1_WALL_2_WEST | WINDOW_WEST | 62.63 | 62.63 | 2.58 | 0.504 | 0.49 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW_EAST | 30.42 | 30.42 | 2.58 | 0.504 | 0.49 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 24.53 | 2.58 | 0.654 | 0.64 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 2.58 | 0.654 | 0.64 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 29.43 | 2.58 | 0.504 | 0.49 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW_WEST | 25.03 | 25.03 | 2.58 | 0.504 | 0.49 | No | ICU_FLR_2_WALL_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 2.58 | 0.504 | 0.49 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 2.58 | 0.504 | 0.49 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 2.58 | 0.504 | 0.49 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 2.58 | 0.504 | 0.49 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 2.58 | 0.654 | 0.64 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 2.58 | 0.654 | 0.64 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 2.58 | 0.504 | 0.49 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 2.58 | 0.504 | 0.49 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 2.58 | 0.654 | 0.64 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 4.91 | 49.05 | 2.58 | 0.504 | 0.49 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 8.17 | 8.17 | 2.58 | 0.504 | 0.49 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 2.58 | 0.504 | 0.49 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 8.17 | 8.17 | 2.58 | 0.654 | 0.64 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW_EAST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 4.91 | 49.05 | 2.58 | 0.654 | 0.64 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 6.54 | 6.54 | 2.58 | 0.504 | 0.49 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW_EAST | 4.74 | 47.41 | 2.58 | 0.504 | 0.49 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW_NORTH | 6.54 | 6.54 | 2.58 | 0.654 | 0.64 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW_WEST | 4.91 | 4.91 | 2.58 | 0.504 | 0.49 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 35.76 | 35.76 | 2.58 | 0.504 | 0.49 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 9.81 | 9.81 | 2.58 | 0.504 | 0.49 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 2.58 | 0.504 | 0.49 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 40.87 | 2.58 | 0.504 | 0.49 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 9.81 | 9.81 | 2.58 | 0.654 | 0.64 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW_WEST | 8.17 | 8.17 | 2.58 | 0.504 | 0.49 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW_NORTH | 2.96 | 17.77 | 2.58 | 0.654 | 0.64 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
Total or Average |  |  | 845.42 | 2.58 | 0.537 | 0.523
North Total or Average |  |  | 186.18 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 659.24 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1298866.76 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 5632467.72 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1209436.59
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ER_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_OR_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_ICU_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
CAV_PATRMS_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | - | - | - | - | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_EXAM5_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ER_NURSESTAT_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
ICU_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OR_NURSESAT_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
NURSESAT_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_1_HEATC | Coil:Heating:Water | -99999 | -
CAV_ER_HEATC | Coil:Heating:Water | -99999 | -
CAV_OR_HEATC | Coil:Heating:Water | -99999 | -
CAV_ICU_HEATC | Coil:Heating:Water | -99999 | -
CAV_PATRMS_HEATC | Coil:Heating:Water | -99999 | -
VAV_2_HEATC | Coil:Heating:Water | -99999 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 3.78 | 471.95 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.93 | 38632.66 | 1 | Fan Energy
CAV_ER_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.55 | 10414.5 | 1 | Fan Energy
CAV_OR_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 10.9 | 18475.34 | 1 | Fan Energy
CAV_ICU_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.56 | 12301.39 | 1 | Fan Energy
CAV_PATRMS_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.89 | 26744.65 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 48.63 | 109341.71 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31296.71 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11902.32 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 17069.51 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 503793.1637 | 540.1876 | 1735.0501 | 0 | 0.0064 | 347964.797 | 187114.7767
February | 444013.3582 | 478.0249 | 1569.6655 | 0 | 0.0058 | 314809.0193 | 165209.7123
March | 438762.3974 | 482.758 | 1768.3956 | 0 | 0.0064 | 354729.4415 | 164854.2337
April | 367569.0433 | 414.0034 | 1681.8267 | 0 | 0.006 | 337415.5985 | 139578.9068
May | 352348.5899 | 409.0955 | 1868.1621 | 0 | 0.0065 | 374856.8353 | 135682.0205
June | 351399.1962 | 414.6921 | 2003.2766 | 0 | 0.0069 | 401995.6163 | 136347.2983
July | 363541.9241 | 430.4664 | 2102.7203 | 0 | 0.0073 | 421956.3528 | 141281.1118
August | 361214.1742 | 424.0575 | 2012.8388 | 0 | 0.007 | 403906.0327 | 139814.3963
September | 339908.5591 | 390.6998 | 1719.5197 | 0 | 0.006 | 345014.8294 | 130283.4323
October | 390282.0605 | 437.0294 | 1732.2697 | 0 | 0.0062 | 347523.6194 | 147810.454
November | 441250.7074 | 480.7402 | 1678.931 | 0 | 0.0061 | 336757.8706 | 165057.3241
December | 480698.658 | 518.5663 | 1721.2378 | 0 | 0.0063 | 345214.4554 | 179020.6435
Annual Sum or Average | 4834780 | 5420.3212 | 21593.8939 | 0 | 0.0769 | 4332140 | 1832050
Minimum of Months | 339908.5591 | 390.6998 | 1569.6655 | 0 | 0.0058 | 314809.0193 | 130283.4323
Maximum of Months | 503793.1637 | 540.1876 | 2102.7203 | 0 | 0.0073 | 421956.3528 | 187114.7767
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1226090000000 | 729159.21 | 10-JAN-11:39 | 228236.782 | 379607.201 | 85709.835 | 0 | 781.897 | 0 | 25512.107 | 0 | 0 | 0 | 0 | 0 | 8751.675 | 0 | 0
February | 1109260000000 | 727448.948 | 02-FEB-11:39 | 228236.782 | 379607.201 | 84600.485 | 0 | 194.923 | 0 | 25513.16 | 0 | 0 | 0 | 0 | 0 | 8749.751 | 0 | 0
March | 1249930000000 | 730755.099 | 31-MAR-14:00 | 228236.782 | 379607.201 | 89108.759 | 0 | 2554.059 | 0 | 17794.768 | 6144.845 | 0 | 0 | 0 | 0 | 6469.073 | 0 | 0
April | 1188920000000 | 771478.399 | 25-APR-14:00 | 228236.782 | 379607.201 | 91002.215 | 0 | 28801.807 | 0 | 19578.774 | 15873.855 | 0 | 0 | 0 | 0 | 6595.935 | 0 | 0
May | 1320850000000 | 873859.978 | 24-MAY-14:00 | 228236.782 | 379607.201 | 94280.786 | 0 | 120538.483 | 0 | 26106.743 | 15873.855 | 0 | 0 | 0 | 0 | 7067.843 | 0 | 0
June | 1416480000000 | 910552.775 | 21-JUN-14:00 | 228236.782 | 379607.201 | 95563.763 | 0 | 156066.643 | 0 | 27851.665 | 15873.855 | 0 | 0 | 0 | 0 | 7352.866 | 0 | 0
July | 1486810000000 | 908183.992 | 19-JUL-12:00 | 228236.782 | 379607.201 | 91435.865 | 0 | 157743.171 | 0 | 28080.222 | 15873.855 | 0 | 0 | 0 | 0 | 7206.896 | 0 | 0
August | 1423210000000 | 903133.623 | 15-AUG-14:00 | 228236.782 | 379607.201 | 95567.273 | 0 | 149339.407 | 0 | 27088.435 | 15873.855 | 0 | 0 | 0 | 0 | 7420.67 | 0 | 0
September | 1215700000000 | 824099.21 | 07-SEP-14:00 | 228236.782 | 379607.201 | 90209.576 | 0 | 78799.422 | 0 | 24273.754 | 15873.855 | 0 | 0 | 0 | 0 | 6829.079 | 0 | 0
October | 1224540000000 | 792483.815 | 03-OCT-14:00 | 228236.782 | 379607.201 | 89065.145 | 0 | 51426.98 | 0 | 21174.278 | 15873.855 | 0 | 0 | 0 | 0 | 6648.984 | 0 | 0
November | 1186600000000 | 724425.275 | 15-NOV-11:39 | 228236.782 | 379607.201 | 86740.288 | 0 | 1780.019 | 0 | 18325.261 | 0 | 0 | 0 | 0 | 0 | 8898.318 | 0 | 0
December | 1216400000000 | 727703.157 | 28-DEC-11:39 | 228236.782 | 379607.201 | 84854.139 | 0 | 191.596 | 0 | 25526.735 | 0 | 0 | 0 | 0 | 0 | 8749.675 | 0 | 0
Annual Sum or Average | 15264800000000 | [7 empty] | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1109260000000 | 724425.275 |  | 228236.782 | 379607.201 | 84600.485 | 0 | 191.596 | 0 | 17794.768 | 0 | 0 | 0 | 0 | 0 | 6469.073 | 0 | 0
Maximum of Months | 1486810000000 | 910552.775 |  | 228236.782 | 379607.201 | 95567.273 | 0 | 157743.171 | 0 | 28080.222 | 15873.855 | 0 | 0 | 0 | 0 | 8898.318 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 377812.62 | 148017.49 | 0 | 525830.11
Cost per Total Building Area ($/m2) | 16.85 | 6.6 | 0 | 23.45
Cost per Net Conditioned Building Area ($/m2) | 16.85 | 6.6 | 0 | 23.45

## Picture
DOE Commercial Building Benchmark - Hospital
Second Floor
Third Floor
Forth Floor
Fifth Floor

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 60.1 | 3133.79
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
BLDG_LIGHT_EXTD_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.2 | 104.6 | 5454.14
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 13.6
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 | 8.5 | 46.7 | 2435.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 3.8
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4
BLDG_OCC_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 13.5 | 90.4 | 4713.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.7
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 96.7 | 5042.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8
BLDG_EQUIP_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 99.9 | 5209.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
INFIL_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 77 | 4015
|  |  | Sat, WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ER_Exam1_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam1_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam1_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam1_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam2_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam2_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam2_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam2_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam3_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam3_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam3_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam3_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam5_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam5_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam5_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam5_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR1_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR1_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR1_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR1_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR2_Mult5_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR2_Mult5_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR2_Mult5_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR2_Mult5_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR3_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR3_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR3_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR3_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR4_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR4_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR4_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR4_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PhysTherapy_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PhysTherapy_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PhysTherapy_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PhysTherapy_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Radiology_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Radiology_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Radiology_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Radiology_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_5 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_5 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen_Flr_5 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720