## BuildingSummary
Building Summary Hospital new construction
|  | Value | Data Source
Program
| Building Name | Hospital
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, inpatient
Form
| Total Floor Area (m2) | 22422.1768 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3142
| Number of Floors | 5 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.1334
| East | 0.121
| North | 0.117
| West | 0.2315
| Total | 0.1461
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures and zone summary
| Floor to Ceiling Height (m) | 4.27
| Floor to Floor Height (m) | 4.27
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 5184.32
| Net Dimensions - Total Area (m2) | 4338.78
| Wall to Skin Ratio | 0.41902
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3739.134
| Net Dimensions - Total Area (m2) | 3739.134
| Roof to Skin Ratio | 0.58098
Window Dimensions (m2)
| South | 220.72
| East | 144.86
| North | 186.18
| West | 293.66
| Total Area (m2) | 845.42
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab
| Dimensions - Total Area (m2) | 3739.134
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15534.17
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 44872.35
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.11 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Boiler | 2003 CBECS
| Cooling Type | Chiller, water cooled | 2003 CBECS
| Fan Control | CAV, VAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 4037.86

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 11.836 | 8.07 |  |  | 10 | 0 | 1006.2497 |  | 0
ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 29.052 | 16.14 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
ER_Exam2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 29.052 | 43.04 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 4.6452 | 5.9998 | 29.052 | 16.14 |  | 3.7854 |  |  | 66.0874 |  | 0.1785
ER_Exam4_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 29.052 | 43.04 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
ER_Exam5_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 29.052 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1.0503 | 11.836 | 11.836 |  |  | 10 | 0 | 10.5034 |  | 0.23798
Lobby_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.78 | 62.63 | 13.0064 | 113.3908 | 15.8172 | 1.076 |  |  | 10 | 0 | 1133.9077 |  | 0.070849
Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.07 | 0 | 92.9031 | 6.125 | 10.76 | 0 |  |  | 0 | 0.25 | 142.2575 |  | 0.040809
ER_NurseStat_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.58 | 30.42 | 14.8645 | 83.1249 | 12.0512 | 14.6336 |  |  |  |  | 2929.97 |  | 0.02282
OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.05 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.29758
OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.11903
OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 23.672 | 53.8 |  | 7.5708 |  |  | 198.2622 |  | 0.17855
OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 23.672 | 53.8 |  | 22.7124 |  |  | 793.0845 |  | 0
IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 8.608 | 32.28 |  |  |  |  | 49.5596 |  | 0.23803
IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 8.608 | 32.28 |  |  |  |  | 66.0874 |  | 0.41656
IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 8.608 | 32.28 |  |  |  |  | 49.5596 |  | 0.23803
ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.68 | 25.03 | 4.6452 | 133.0332 | 8.608 | 32.28 |  |  |  |  | 1465.3525 |  | 0.088583
ICU_NurseSat_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 10.76 | 21.52 |  |  | 10 | 0 | 359.9287 |  | 0
Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.07 | 0 | 92.9031 | 6.125 | 10.76 | 0 |  |  | 0 | 0.25 | 142.2575 |  | 0.040809
OR_NurseSat_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.14 | 35.76 | 13.0064 | 77.8568 | 12.6968 | 11.1904 |  |  | 10 | 0 | 778.5683 |  | 0.045864
PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.532 | 21.52 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.532 | 21.52 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.532 | 21.52 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.532 | 21.52 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.532 | 21.52 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 9.684 | 16.14 |  | 3.7854 | 8 | 0 | 209.9994 |  | 0
PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.532 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.532 | 21.52 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.532 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
NurseSat_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 12.6968 | 11.1904 |  |  | 10 | 0 | 696.4243 |  | 0
Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 15.064 | 43.04 |  | 7.5708 | 10 | 0 | 142.4979 |  | 0
Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.532 | 21.52 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.532 | 21.52 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.532 | 21.52 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.532 | 21.52 |  | 3.7854 |  |  | 82.6152 |  | 0.38087
PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.532 | 21.52 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 4.304 | 107.6 |  | 3.7854 | 8 | 0 | 209.9994 |  | 0
PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.532 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.532 | 21.52 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.532 | 21.52 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
NurseSat_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 12.6968 | 11.1904 |  |  | 10 | 0 | 696.4243 |  | 0
Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 15.064 | 43.04 |  | 7.5708 | 10 | 0 | 142.4979 |  | 0
Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.76 | 0 |  |  | 0 | 0.25 | 141.6775 |  | 0.020486
Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.67 | 35.76 | 9.2903 | 74.9999 | 9.684 | 10.76 |  |  | 10 | 0 | 749.9993 |  | 0.33831
NurseSat_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.08 | 0 | 13.0064 | 79.9999 | 12.6968 | 11.1904 |  |  | 10 | 0 | 799.9992 |  | 0.28049
Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2 | 0 | 18.5806 | 49.9999 | 12.912 | 80.7001 | 304.8308 | 567.81 | 8 | 0 | 399.9994 | 2501.3191 | 0.32641
Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.56 | 17.98 | 13.2719 | 5.2517 | 11.836 | 10.76 |  |  | 10 | 0 | 52.5171 |  | 0.51678
Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 13.2719 | 5.2502 | 11.836 | 10.76 |  |  | 10 | 0 | 52.502 |  | 0.37399
Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.55 | 17.98 | 13.2719 | 5.2502 | 11.836 | 10.76 |  |  | 10 | 0 | 52.502 |  | 0.51682
Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.94 | 1 | 11.836 | 10.76 |  |  | 10 | 0 | 10 |  | 0.49297
Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.06 | 0 | 92.9031 | 5.4 | 10.76 | 0 |  |  | 0 | 0.25 | 125.42 |  | 0.29466
Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.32 | 845.54 |  | 1291.1824 |  |  |  | 1052.3412
Data Source | [7 empty] | 1 |  | 2 | 5, 6 | 5, 6 | 5, 6 | 3, 4 | 3, 4 | 3, 4 | 5 | 5
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] DOE Benchmark Report
[6] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 2.212 | 26.2479 | 5.2507 | 25.6471 |  | 14.9424 | 2.1414 | 33.7424 | 1.2208 | 5.8045 | 44.5219 | 11.9724 | 12.1239 | 1.2983 | 1.8482 | 0.07226
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
| R-value (m2·K / W) | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 2893.6051 | 2863.8521 | 2607.7141 | 2619.9475 | 2226.4236 | 2228.8293 | 1985.3378 | 2670.4663 | 1872.287 | 1993.2511 | 2623.3182 | 1848.4143 | 2526.3937 | 1777.6523 | 2238.5396 | 1839.0298
Heating (kW)
| HEATSYS1 BOILER | 2867.4093 | 2986.1426 | 2943.1429 | 3121.5755 | 2851.9459 | 2882.3605 | 3022.2503 | 3295.7007 | 2772.5611 | 3071.4234 | 3439.422 | 2950.1731 | 3541.0801 | 3226.9444 | 3555.1331 | 4123.1946
HVAC Efficiency
| Air Conditioning (COP) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
| Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
HVAC Control - Economizer
| CAV_1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| CAV_2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CAV_1_FAN | 15.94 | 16.05 | 16.68 | 15.85 | 15.49 | 16.15 | 17.4 | 15.76 | 16.15 | 15.58 | 15.76 | 16.04 | 15.71 | 15.87 | 16.13 | 18.03
| CAV_2_FAN | 12.17 | 12.19 | 12.42 | 12.09 | 12 | 12.16 | 12.34 | 12.1 | 12.14 | 12.06 | 12.1 | 12.11 | 12.09 | 12.09 | 12.13 | 12.47
| VAV_1_FAN | 26.1 | 26.08 | 25.44 | 24.67 | 23.58 | 23.43 | 22.38 | 24.41 | 26.07 | 22.7 | 24.29 | 25.82 | 24.16 | 24.69 | 23.32 | 22.93
| VAV_2_FAN | 42.65 | 43.14 | 44.93 | 42.27 | 40.54 | 43.15 | 40.41 | 41.92 | 44.49 | 41.1 | 41.85 | 43.85 | 41.56 | 42.9 | 41.82 | 40.82
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.0752 | 0.097495 | 0.068123 | 0.098033 | 0.044267 | 0.08719 | 0.13041 | 0.05548 | 0.036961 | 0.065763 | 0.098149 | 0.036962 | 0.051655 | 0.069144 | 0.051708 | 0.087327
| Total Cost ($/m2) | 23.12 | 28.51 | 19.04 | 26.62 | 11.37 | 23.72 | 31.48 | 14.89 | 9.46 | 15.68 | 25.38 | 9.28 | 13.28 | 17.02 | 12.91 | 22.06
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01145 | 0.0081761 | 0.0085584 | 0.010794 | 0.0083997 | 0.0081496 | 0.0084041 | 0.010092 | 0.0071899 | 0.0082864 | 0.0089079 | 0.0071821 | 0.0079766 | 0.0086955 | 0.0079705 | 0.004178
| Total Cost ($/m2) | 6.21 | 5.04 | 4.83 | 6.85 | 5.31 | 4.54 | 6.21 | 7.23 | 3.78 | 5.94 | 6.69 | 4.12 | 6.46 | 5.84 | 6.91 | 4.99
Total Utility Costs
| Cost Intensity ($/m2) | 29.33 | 33.55 | 23.87 | 33.47 | 16.68 | 28.26 | 37.7 | 22.12 | 13.24 | 21.62 | 32.07 | 13.41 | 19.74 | 22.86 | 19.81 | 27.05
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1789088.8889 | 1432561.1111 | 980655.5556 | 960780.5556 | 813430.5556 | 700752.7778 | 519663.8889 | 810738.8889 | 477516.6667 | 422488.8889 | 594027.7778 | 379963.8889 | 533958.3333 | 305827.7778 | 331063.8889 | 226819.4444
| Interior Lighting | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222 | 1153597.2222
| Exterior Lighting | 14163.8889 | 14136.1111 | 14133.3333 | 14155.5556 | 14155.5556 | 14141.6667 | 14125 | 14138.8889 | 14136.1111 | 14116.6667 | 14119.4444 | 14122.2222 | 14130.5556 | 14113.8889 | 14111.1111 | 14027.7778
| Interior Equipment | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444
| Exterior Equipment | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667
| Fans | 616908.3333 | 609950 | 637241.6667 | 596058.3333 | 583180.5556 | 609969.4444 | 620172.2222 | 590602.7778 | 615197.2222 | 580347.2222 | 589427.7778 | 608313.8889 | 588383.3333 | 594947.2222 | 593519.4444 | 644313.8889
| Pumps | 435830.5556 | 415619.4444 | 364533.3333 | 366536.1111 | 321161.1111 | 308275 | 276066.6667 | 363483.3333 | 256805.5556 | 268680.5556 | 341763.8889 | 244522.2222 | 313538.8889 | 224733.3333 | 263091.6667 | 180327.7778
| Heat Rejection | 309680.5556 | 292238.8889 | 270777.7778 | 247597.2222 | 237766.6667 | 214900 | 210647.2222 | 218852.7778 | 148741.6667 | 191994.4444 | 180491.6667 | 130383.3333 | 161175 | 114525 | 124411.1111 | 84677.7778
| Humidification | 5800 | 72113.8889 | 277697.2222 | 186058.3333 | 71933.3333 | 533691.6667 | 55633.3333 | 302950 | 511394.4444 | 153847.2222 | 362063.8889 | 539080.5556 | 438675 | 550630.5556 | 555911.1111 | 801180.5556
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 57377.7778 | 54983.3333 | 55283.3333 | 53011.1111 | 53480.5556 | 53605.5556 | 51847.2222 | 51605.5556 | 51269.4444 | 50644.4444 | 50636.1111 | 50102.7778 | 50191.6667 | 49394.4444 | 48813.8889 | 47819.4444
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas (MJ)
| Heating | 10348490 | 11917180 | 10812070 | 12236830 | 12205970 | 10575660 | 14524110 | 13994810 | 9723790 | 13979600 | 14721350 | 10749220 | 15972940 | 12866870 | 17169630 | 24431560
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 456540 | 547640 | 495260 | 635430 | 618410 | 558340 | 693520 | 704410 | 691320 | 740330 | 764980 | 761820 | 817310 | 826810 | 903630 | 1008110
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 36981510 | 37427210 | 35221110 | 36151980 | 34919380 | 34453840 | 36063610 | 37720380 | 32437970 | 35328180 | 37716070 | 33143020 | 38903060 | 34921310 | 39577210 | 47189290
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 287.2469 | 230.0047 | 157.449 | 154.258 | 130.6002 | 112.5093 | 83.4346 | 130.1681 | 76.6676 | 67.8327 | 95.3741 | 61.0051 | 85.7296 | 49.1021 | 53.1539 | 36.417
| Interior Lighting (elec) | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157 | 185.2157
| Exterior Lighting (elec) | 2.2741 | 2.2696 | 2.2692 | 2.2727 | 2.2727 | 2.2705 | 2.2678 | 2.2701 | 2.2696 | 2.2665 | 2.2669 | 2.2674 | 2.2687 | 2.2661 | 2.2656 | 2.2522
| Interior Equipment (elec) | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554
| Exterior Equipment (elec) | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719
| Fans (elec) | 99.0476 | 97.9304 | 102.3123 | 95.7001 | 93.6325 | 97.9336 | 99.5717 | 94.8242 | 98.7729 | 93.1776 | 94.6355 | 97.6678 | 94.4678 | 95.5217 | 95.2924 | 103.4477
| Pumps (elec) | 69.9747 | 66.7297 | 58.5276 | 58.8492 | 51.564 | 49.4951 | 44.3238 | 58.359 | 41.2314 | 43.138 | 54.8719 | 39.2592 | 50.3402 | 36.082 | 42.2407 | 28.9525
| Heat Rejection (elec) | 49.7207 | 46.9204 | 43.4747 | 39.7529 | 38.1746 | 34.5032 | 33.8204 | 35.1379 | 23.8812 | 30.8256 | 28.9788 | 20.9337 | 25.8774 | 18.3875 | 19.9748 | 13.5954
| Humidification (elec) | 0.93122 | 11.5782 | 44.5856 | 29.8726 | 11.5492 | 85.6868 | 8.9322 | 48.6401 | 82.1069 | 24.7009 | 58.1311 | 86.552 | 70.4314 | 88.4064 | 89.2542 | 128.6334
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 9.2123 | 8.8278 | 8.876 | 8.5112 | 8.5866 | 8.6066 | 8.3243 | 8.2855 | 8.2316 | 8.1312 | 8.1299 | 8.0442 | 8.0585 | 7.9305 | 7.8373 | 7.6776
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas (MJ/m2)
| Heating (gas) | 461.5279 | 531.4893 | 482.2029 | 545.7452 | 544.3689 | 471.6594 | 647.7546 | 624.1486 | 433.6672 | 623.4703 | 656.5513 | 479.3999 | 712.3704 | 573.8441 | 765.7411 | 1089.6128
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.361 | 24.424 | 22.0879 | 28.3393 | 27.5802 | 24.9012 | 30.93 | 31.4157 | 30.8319 | 33.0177 | 34.117 | 33.9761 | 36.4509 | 36.8745 | 40.3006 | 44.9603
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1649.3227 | 1669.2003 | 1570.8114 | 1612.3269 | 1557.3547 | 1536.5922 | 1608.3857 | 1682.2753 | 1446.6873 | 1575.5866 | 1682.0831 | 1478.1315 | 1735.0211 | 1557.4407 | 1765.0873 | 2104.5752
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1135.2631 | 1098.7445 | 1071.2577 | 1025.5607 | 1039.7065 | 1046.8039 | 1000.4346 | 1035.1116 | 1013.8424 | 964.5272 | 977.7365 | 1015.079 | 968.5808 | 955.3734 | 971.5354 | 983.6979
| Feb | 1141.9151 | 1060.8369 | 1104.5926 | 1033.3809 | 1012.0005 | 1045.7795 | 979.9769 | 996.6812 | 1044.5651 | 974.8892 | 962.0374 | 1003.6553 | 970.1958 | 985.2822 | 972.2714 | 986.6925
| Mar | 1154.9489 | 1089.0784 | 1143.5443 | 1068.935 | 1053.5029 | 1068.1776 | 982.5315 | 1042.1363 | 1059.9727 | 976.0212 | 991.9812 | 1072.5993 | 994.0632 | 1018.2922 | 979.6765 | 988.4941
| Apr | 1166.3832 | 1121.0985 | 1127.8869 | 1051.5574 | 1105.292 | 1066.937 | 1017.3953 | 1037.6725 | 1105.9494 | 967.9582 | 1032.0679 | 1033.8846 | 996.6307 | 1019.9752 | 989.8788 | 995.3321
| May | 1224.8623 | 1225.1085 | 1159.1252 | 1120.3538 | 1033.7611 | 1154.6701 | 1009.6761 | 1122.1922 | 1097.5962 | 995.237 | 1081.0243 | 1057.4002 | 1051.7614 | 1026.4902 | 1032.28 | 1053.7977
| Jun | 1272.694 | 1215.1371 | 1208.966 | 1161.3742 | 1052.4411 | 1159.3784 | 998.8952 | 1214.2857 | 1132.2872 | 998.9419 | 1185.185 | 1101.6329 | 1156.0785 | 1053.6448 | 1082.2693 | 1063.1862
| Jul | 1251.9575 | 1277.6776 | 1186.1413 | 1187.7892 | 1057.4485 | 1142.2824 | 1012.9101 | 1225.7723 | 1109.7127 | 1029.3045 | 1178.5319 | 1064.0885 | 1196.1977 | 1058.7225 | 1101.5537 | 1024.251
| Aug | 1242.5943 | 1246.0631 | 1190.2497 | 1180.3984 | 1089.188 | 1113.2846 | 1009.4903 | 1269.9743 | 1047.774 | 1027.3429 | 1230.8128 | 1069.6093 | 1186.9554 | 1049.2014 | 1096.5718 | 1009.7638
| Sep | 1226.8088 | 1256.7535 | 1143.766 | 1140.3212 | 1071.1784 | 1125.4892 | 1041.4588 | 1104.4352 | 1076.7659 | 1027.0256 | 1088.0837 | 1091.6426 | 1070.1678 | 1004.1075 | 1075.8133 | 978.2756
| Oct | 1220.4688 | 1168.6399 | 1114.6821 | 1072.4039 | 1058.1297 | 1090.798 | 1001.7253 | 1076.0553 | 1048.8246 | 971.0259 | 1046.8097 | 1063.6759 | 979.849 | 1017.1977 | 980.3132 | 974.594
| Nov | 1170.7229 | 1129.2649 | 1087.2643 | 1039.318 | 1025.6973 | 1033.9906 | 973.8088 | 1032.9988 | 1023.1113 | 957.8696 | 1055.4095 | 1036.7818 | 996.6661 | 978.0091 | 985.945 | 975.4617
| Dec | 1140.8973 | 1090.8171 | 1098.5829 | 1026.4638 | 1043.9034 | 1044.2113 | 995.5859 | 1006.8389 | 993.3994 | 928.2548 | 960.6541 | 1001.049 | 970.5898 | 961.5102 | 964.0986 | 983.9317
Time of Peak Electrical Demand
| Jan | 06-JAN-11:45 | 03-JAN-11:45 | 25-JAN-16:15 | 30-JAN-16:15 | 26-JAN-13:00 | 30-JAN-16:00 | 20-JAN-14:00 | 05-JAN-16:15 | 20-JAN-16:15 | 03-JAN-17:00 | 26-JAN-16:00 | 24-JAN-16:15 | 03-JAN-17:00 | 10-JAN-17:00 | 31-JAN-17:00 | 25-JAN-16:15
| Feb | 23-FEB-11:45 | 15-FEB-16:15 | 28-FEB-17:00 | 06-FEB-16:15 | 10-FEB-10:00 | 17-FEB-17:30 | 15-FEB-16:30 | 16-FEB-16:15 | 13-FEB-16:45 | 22-FEB-11:45 | 08-FEB-11:45 | 07-FEB-14:00 | 08-FEB-17:00 | 03-FEB-17:30 | 15-FEB-17:45 | 17-FEB-17:45
| Mar | 14-MAR-10:45 | 24-MAR-16:30 | 30-MAR-15:00 | 22-MAR-16:00 | 31-MAR-15:00 | 21-MAR-15:00 | 13-MAR-12:00 | 17-MAR-16:00 | 02-MAR-16:15 | 23-MAR-15:00 | 31-MAR-16:00 | 30-MAR-15:15 | 31-MAR-15:00 | 29-MAR-16:00 | 06-MAR-17:00 | 22-MAR-15:15
| Apr | 04-APR-16:00 | 20-APR-15:15 | 26-APR-16:00 | 14-APR-16:00 | 11-APR-16:00 | 26-APR-16:15 | 13-APR-15:00 | 20-APR-15:00 | 21-APR-16:00 | 14-APR-16:00 | 27-APR-16:00 | 27-APR-12:00 | 06-APR-16:00 | 06-APR-16:00 | 27-APR-15:15 | 21-APR-16:00
| May | 19-MAY-15:15 | 18-MAY-16:00 | 19-MAY-16:00 | 31-MAY-16:00 | 31-MAY-15:15 | 11-MAY-15:00 | 24-MAY-16:00 | 31-MAY-15:00 | 12-MAY-16:00 | 05-MAY-15:00 | 30-MAY-16:00 | 19-MAY-16:00 | 31-MAY-16:00 | 04-MAY-16:00 | 12-MAY-16:00 | 24-MAY-15:15
| Jun | 27-JUN-15:00 | 29-JUN-16:30 | 08-JUN-15:00 | 08-JUN-15:00 | 23-JUN-16:45 | 29-JUN-15:00 | 16-JUN-15:30 | 30-JUN-16:00 | 26-JUN-16:00 | 27-JUN-16:00 | 08-JUN-12:00 | 15-JUN-16:00 | 29-JUN-16:00 | 30-JUN-15:00 | 14-JUN-15:15 | 15-JUN-16:45
| Jul | 13-JUL-15:45 | 18-JUL-12:30 | 11-JUL-16:15 | 25-JUL-15:00 | 28-JUL-09:15 | 31-JUL-16:00 | 03-JUL-12:00 | 25-JUL-10:45 | 31-JUL-16:00 | 27-JUL-16:00 | 14-JUL-10:45 | 12-JUL-15:00 | 13-JUL-16:00 | 21-JUL-16:00 | 07-JUL-16:00 | 20-JUL-16:00
| Aug | 21-AUG-15:15 | 03-AUG-15:15 | 11-AUG-16:00 | 17-AUG-15:15 | 08-AUG-16:45 | 02-AUG-16:00 | 15-AUG-12:15 | 09-AUG-16:00 | 01-AUG-16:00 | 18-AUG-16:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-15:00 | 18-AUG-16:00
| Sep | 12-SEP-15:00 | 15-SEP-15:15 | 12-SEP-15:15 | 01-SEP-15:45 | 01-SEP-16:15 | 20-SEP-16:00 | 28-SEP-15:00 | 27-SEP-15:15 | 20-SEP-16:00 | 01-SEP-16:30 | 06-SEP-16:00 | 13-SEP-15:00 | 22-SEP-12:45 | 01-SEP-16:00 | 08-SEP-16:00 | 07-SEP-15:00
| Oct | 06-OCT-15:00 | 30-OCT-15:15 | 02-OCT-16:00 | 20-OCT-16:00 | 19-OCT-15:45 | 31-OCT-15:45 | 30-OCT-13:15 | 03-OCT-10:45 | 13-OCT-15:15 | 17-OCT-16:00 | 31-OCT-09:00 | 05-OCT-15:00 | 19-OCT-15:15 | 19-OCT-16:00 | 25-OCT-15:15 | 27-OCT-16:45
| Nov | 02-NOV-10:45 | 27-NOV-17:00 | 15-NOV-16:00 | 03-NOV-15:15 | 29-NOV-11:45 | 22-NOV-16:30 | 20-NOV-11:45 | 03-NOV-13:00 | 13-NOV-17:00 | 28-NOV-17:00 | 02-NOV-09:15 | 10-NOV-13:00 | 01-NOV-15:15 | 21-NOV-11:45 | 03-NOV-16:00 | 29-NOV-17:30
| Dec | 15-DEC-17:30 | 06-DEC-16:15 | 06-DEC-16:45 | 28-DEC-14:00 | 18-DEC-11:45 | 05-DEC-16:30 | 29-DEC-16:00 | 06-DEC-16:45 | 05-DEC-16:15 | 07-DEC-17:00 | 05-DEC-16:00 | 29-DEC-14:00 | 20-DEC-16:30 | 12-DEC-16:45 | 13-DEC-14:00 | 13-DEC-17:00
Source Energy
| Total Source Energy (GJ) | 95603.99 | 100824.62 | 85173.62 | 89283.18 | 79667.36 | 92197.72 | 78415.06 | 95000.91 | 81421.3 | 51090.76 | 92404.18 | 81321.14 | 91151.21 | 85502.29 | 90459.57 | 102100.88
| Total Source Energy (MJ/m2) | 4263.8 | 4496.63 | 3798.62 | 3981.9 | 3553.05 | 4111.89 | 3497.2 | 4236.91 | 3631.27 | 2278.58 | 4121.09 | 3626.81 | 4065.21 | 3813.28 | 4034.37 | 4553.55
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 29251.65 | 23441.53 | 30419.11 | 18159.58 | 15381.99 | 25339.33 | 9926.84 | 15583.5 | 15428.91 | 8713.17 | 12288.43 | 12108.36 | 10930.18 | 9177.05 | 7005.41 | 5215.67
| Water Systems | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61
| Total Building | 33297.03 | 27575.71 | 34828.61 | 22446.35 | 19515.93 | 30091.66 | 14038.95 | 20026.81 | 20151.38 | 12956.81 | 16810.91 | 16867.9 | 15555.26 | 13952.07 | 11787.49 | 10326.22
Emissions
| Carbon Equivalent (kg) | 2109990 | 2436320 | 2119760 | 2132330 | 928920.4695 | 2282780 | 931530.6252 | 1913400 | 2557140 | 679392.9174 | 3394740 | 2532550 | 2300630 | 2288360 | 2265870 | 2077080
| CO2 (kg) | 5011620 | 6208120 | 5107800 | 4998540 | 2536160 | 5524090 | 2552600 | 4478110 | 6077080 | 1762830 | 8009340 | 6030830 | 5494910 | 5475340 | 5428290 | 5388780
| NOX (kg) | 8296.2293 | 7867.2152 | 8116.7935 | 8893.6009 | 2208.879 | 8582.6523 | 2229.4398 | 8040.3742 | 10143.1209 | 2246.9777 | 13782.8959 | 10013.6334 | 9160.191 | 9039.1529 | 8977.329 | 6269.5107
| SO2 (kg) | 29511.9321 | 31278.979 | 25197.739 | 21377.0875 | 16765.187 | 33560.398 | 15756.2432 | 21970.3251 | 25069.1194 | 4137.2479 | 39075.6388 | 24595.2871 | 13611.4471 | 14741.0321 | 13212.6148 | 28840.3361
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1358 | 0.0894 | 0.0697 | 0.0795 | 0.0091 | 0.0642 | 0.0089 | 0.0902 | 0.0989 | 0.0178 | 0.1196 | 0.0972 | 0.1012 | 0.1038 | 0.0984 | 0.1004
| Water for Electricity (m3) | 3652.1 | 10668.5 | 186109 | 38018.8 | 101136 | 167358 | 95043.9 | 1366.18 | 26064.7 | 54631 | 8994.62 | 25571.7 | 8944.22 | 349611 | 8681.83 | 5787.02

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 36981.51 | 1649.32 | 1649.32
Net Site Energy | 36981.51 | 1649.32 | 1649.32
Total Source Energy | 95603.99 | 4263.8 | 4263.8
Net Source Energy | 95603.99 | 4263.8 | 4263.8
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10348.49 | 0 | 0 | 0 | 0
Cooling | 6440.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2220.87 | 0 | 0 | 0 | 0 | 0
Pumps | 1568.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1114.85 | 0 | 0 | 0 | 0 | 29251.65
Humidification | 20.88 | 0 | 0 | 0 | 0 | 7.77
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 456.54 | 0 | 0 | 0 | 4037.61
Refrigeration | 206.56 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24818.06 | 12163.45 | 0 | 0 | 0 | 33297.03
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.251 | 0.11 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.251 | 0.11 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.251 | 0.11 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.251 | 0.11 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.251 | 0.11 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 186.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2893605.15 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 2867409.32 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2694373.32
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 525506.01 | 340458.76 | 185047.25 | 0.65 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 310450.24 | 219141.48 | 91308.76 | 0.71 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 814214.74 | 536422.77 | 277791.97 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1364545.12 | 891973.78 | 472571.34 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 64827.03 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11838.64 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16735.32 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 14860.65 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37191.87 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46498.19 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16393.61 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16393.61 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 181743.09 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25926.68 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30734.53 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11567.13 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50324.53 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 121608.96 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77806.32 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77806.32 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51016.85 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26710.38 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27320.5 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41549.43 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40982.35 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204911.76 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40982.35 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 163939.7 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32656.75 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6261.36 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3203.73 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 27458.62 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6453.22 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5868.08 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10246.7 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10246.7 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59436.67 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59436.67 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10246.7 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10246.7 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10010.58 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9941.41 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 72747.11 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 72243.99 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10442.14 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10369.31 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 43033.68 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107584.19 | -
CAV_1_HEATC | Coil:Heating:Water | 24199.49 | -
CAV_2_HEATC | Coil:Heating:Water | 122412.22 | -
VAV_1_HEATC | Coil:Heating:Water | 65009.33 | -
VAV_2_HEATC | Coil:Heating:Water | 113465.52 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.94 | 27008.01 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.17 | 20627.44 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 26.1 | 43935.67 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 42.65 | 70649.88 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26515.89 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15789.17 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 38027.32 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 406500.7321 | 662.9917 | 2315.6134 | 0 | 0.0107 | 286548.693 | 170149.9701
February | 365456.7833 | 598.0867 | 2097.8378 | 0 | 0.0097 | 259601.5507 | 153174.1751
March | 413711.2607 | 680.0909 | 2398.7094 | 0 | 0.0111 | 296836.2222 | 173703.0664
April | 398467.1254 | 658.4383 | 2337.1385 | 0 | 0.0108 | 289219.8685 | 167643.9568
May | 437091.0917 | 727.2911 | 2603.2653 | 0 | 0.012 | 322157.2483 | 184397.8622
June | 430971.0325 | 720.0274 | 2589.7948 | 0 | 0.0119 | 320492.7195 | 182108.5142
July | 447475.189 | 749.0827 | 2700.6336 | 0 | 0.0124 | 334210.4986 | 189230.8761
August | 453099.2656 | 759.3078 | 2740.954 | 0 | 0.0126 | 339200.9218 | 191690.409
September | 430654.5001 | 718.3971 | 2579.2236 | 0 | 0.0119 | 319183.5916 | 181864.3977
October | 429252.2674 | 712.9012 | 2545.9796 | 0 | 0.0117 | 315066.9399 | 180955.9292
November | 400455.6172 | 659.2323 | 2329.1893 | 0 | 0.0107 | 288234.0349 | 168230.8792
December | 398486.4424 | 650.3821 | 2273.5927 | 0 | 0.0105 | 281349.1978 | 166841.6533
Annual Sum or Average | 5011620 | 8296.2293 | 29511.9321 | 0 | 0.1358 | 3652100 | 2109990
Minimum of Months | 365456.7833 | 598.0867 | 2097.8378 | 0 | 0.0097 | 259601.5507 | 153174.1751
Maximum of Months | 453099.2656 | 759.3078 | 2740.954 | 0 | 0.0126 | 339200.9218 | 191690.409
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1947260000000 | 1135263.149 | 06-JAN-11:45 | 242482.867 | 310109.712 | 75386.68 | 0 | 245930.938 | 0 | 51967.817 | 35363.65 | 162962.637 | 0 | 0 | 0 | 11058.847 | 0 | 0
February | 1764140000000 | 1141915.093 | 23-FEB-11:45 | 242482.867 | 310109.712 | 78984.183 | 0 | 248650.098 | 0 | 52142.163 | 35363.65 | 162962.637 | 0 | 0 | 0 | 11219.784 | 0 | 0
March | 2017170000000 | 1154948.868 | 14-MAR-10:45 | 242482.867 | 310109.712 | 76469.506 | 0 | 263812.606 | 0 | 52637.389 | 35363.65 | 162962.637 | 0 | 0 | 0 | 11110.501 | 0 | 0
April | 1965410000000 | 1166383.235 | 04-APR-16:00 | 242482.867 | 310109.712 | 87587.35 | 0 | 268032.419 | 0 | 53273.214 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6571.387 | 0 | 0
May | 2189240000000 | 1224862.335 | 19-MAY-15:15 | 242482.867 | 310109.712 | 88933.261 | 0 | 323616.329 | 0 | 54804.629 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6589.25 | 0 | 0
June | 2177930000000 | 1272694.013 | 27-JUN-15:00 | 242482.867 | 310109.712 | 87824.405 | 0 | 371482.501 | 0 | 55735.946 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6732.294 | 0 | 0
July | 2271150000000 | 1251957.489 | 13-JUL-15:45 | 242482.867 | 310109.712 | 90443.226 | 0 | 348443.8 | 0 | 55452.104 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6699.492 | 0 | 0
August | 2305060000000 | 1242594.319 | 21-AUG-15:15 | 242482.867 | 310109.712 | 82159.909 | 0 | 348140.228 | 0 | 54674.034 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6701.282 | 0 | 0
September | 2169030000000 | 1226808.809 | 12-SEP-15:00 | 242482.867 | 310109.712 | 87515.137 | 0 | 326791.759 | 0 | 54963.46 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6619.587 | 0 | 0
October | 2141050000000 | 1220468.834 | 06-OCT-15:00 | 242482.867 | 310109.712 | 89912.427 | 0 | 318137.008 | 0 | 54882.213 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6618.32 | 0 | 0
November | 1958710000000 | 1170722.87 | 02-NOV-10:45 | 242482.867 | 310109.712 | 79570.554 | 0 | 275988.737 | 0 | 53020.287 | 35363.65 | 162962.637 | 0 | 0 | 0 | 11224.426 | 0 | 0
December | 1911920000000 | 1140897.327 | 15-DEC-17:30 | 242482.867 | 310109.712 | 82393.961 | 0 | 245508.612 | 3239 | 52496.083 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6340.805 | 0 | 0
Annual Sum or Average | 24818100000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1764140000000 | 1135263.149 |  | 242482.867 | 310109.712 | 75386.68 | 0 | 245508.612 | 0 | 51967.817 | 35363.65 | 162962.637 | 0 | 0 | 0 | 6340.805 | 0 | 0
Maximum of Months | 2305060000000 | 1272694.013 |  | 242482.867 | 310109.712 | 90443.226 | 0 | 371482.501 | 3239 | 55735.946 | 35363.65 | 162962.637 | 0 | 0 | 0 | 11224.426 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 518424.9 | 139277.44 | 0 | 657702.34
Cost per Total Building Area ($/m2) | 23.12 | 6.21 | 0 | 29.33
Cost per Net Conditioned Building Area ($/m2) | 23.12 | 6.21 | 0 | 29.33

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 37427.21 | 1669.2 | 1669.2
Net Site Energy | 37427.21 | 1669.2 | 1669.2
Total Source Energy | 100824.62 | 4496.63 | 4496.63
Net Source Energy | 100824.62 | 4496.63 | 4496.63
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11917.18 | 0 | 0 | 0 | 0
Cooling | 5157.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2195.82 | 0 | 0 | 0 | 0 | 0
Pumps | 1496.23 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1052.06 | 0 | 0 | 0 | 0 | 23441.53
Humidification | 259.61 | 0 | 0 | 0 | 0 | 96.57
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 547.64 | 0 | 0 | 0 | 4037.61
Refrigeration | 197.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 23603.98 | 13823.23 | 0 | 0 | 0 | 27575.71
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.251 | 0.11 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.251 | 0.11 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.251 | 0.11 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.251 | 0.11 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.251 | 0.11 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 186.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2863852.1 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 2986142.62 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2666668.84
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 524268.12 | 339062.37 | 185205.74 | 0.65 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 282595.11 | 205630.82 | 76964.3 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 812161.27 | 532982 | 279179.27 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1374472.94 | 895624.73 | 478848.21 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 61689.59 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11791.56 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16674.1 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 15399.47 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 38539.7 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46432.97 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16333.64 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16333.64 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 181078.23 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25926.83 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30622.1 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11652.35 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51454.16 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 130216.29 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77521.69 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77521.69 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51733.59 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26713.6 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27323.8 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 42942.11 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40832.43 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204162.14 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40832.43 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 163339.97 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33073.1 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6568.09 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3411.97 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 28236.04 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6568.09 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5876.45 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10209.22 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10209.22 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59219.24 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59219.24 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10209.22 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10209.22 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10512.93 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10429.75 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74444.41 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 73834.45 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10520.11 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10440.7 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42876.25 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107190.62 | -
CAV_1_HEATC | Coil:Heating:Water | 18866.59 | -
CAV_2_HEATC | Coil:Heating:Water | 76705.22 | -
VAV_1_HEATC | Coil:Heating:Water | 113063.63 | -
VAV_2_HEATC | Coil:Heating:Water | 206359.66 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.05 | 27186.65 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.19 | 20659.64 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 26.08 | 43906.14 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 43.14 | 71463.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26243.24 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16442.97 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 37636.31 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 507235.2846 | 633.718 | 2428.564 | 0 | 0.007 | 828276.5191 | 197890.0322
February | 444458.6947 | 554.308 | 2114.2797 | 0 | 0.0061 | 721082.8961 | 173272.444
March | 510435.2573 | 642.719 | 2513.9563 | 0 | 0.0072 | 857425.7754 | 199783.3479
April | 496015.9558 | 628.231 | 2494.3145 | 0 | 0.0071 | 850744.9457 | 194612.4881
May | 537980.908 | 685.6161 | 2764.6463 | 0 | 0.0079 | 942968.6943 | 211623.2777
June | 542485.5639 | 694.9278 | 2837.8069 | 0 | 0.0081 | 967939.4971 | 213855.5322
July | 568000.9743 | 728.7459 | 2987.1446 | 0 | 0.0085 | 1018880 | 224060.0684
August | 573612.773 | 735.6804 | 3012.9388 | 0 | 0.0086 | 1027680 | 226239.539
September | 525046.0438 | 670.7084 | 2720.2587 | 0 | 0.0077 | 927836.4768 | 206738.3912
October | 518117.9699 | 657.6424 | 2625.3181 | 0 | 0.0075 | 895433.7343 | 203467.0137
November | 487943.363 | 615.0662 | 2412.5375 | 0 | 0.0069 | 822838.5557 | 191066.1767
December | 496782.9418 | 619.852 | 2367.2136 | 0 | 0.0068 | 807348.4386 | 193708.1558
Annual Sum or Average | 6208120 | 7867.2152 | 31278.979 | 0 | 0.0894 | 10668500 | 2436320
Minimum of Months | 444458.6947 | 554.308 | 2114.2797 | 0 | 0.0061 | 721082.8961 | 173272.444
Maximum of Months | 573612.773 | 735.6804 | 3012.9388 | 0 | 0.0086 | 1027680 | 226239.539
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1832560000000 | 1098744.518 | 03-JAN-11:45 | 242482.867 | 310109.712 | 67502.266 | 0 | 219517.771 | 0 | 50282.675 | 35000.029 | 162962.637 | 0 | 0 | 0 | 10886.561 | 0 | 0
February | 1595400000000 | 1060836.878 | 15-FEB-16:15 | 242482.867 | 310109.712 | 70623.212 | 0 | 184448.97 | 0 | 49082.419 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6127.032 | 0 | 0
March | 1897060000000 | 1089078.393 | 24-MAR-16:30 | 242482.867 | 310109.712 | 74336.148 | 0 | 207742.544 | 0 | 50149.978 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6294.479 | 0 | 0
April | 1882270000000 | 1121098.497 | 20-APR-15:15 | 242482.867 | 310109.712 | 79714.129 | 0 | 233369.58 | 0 | 51108.693 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6350.851 | 0 | 0
May | 2086320000000 | 1225108.482 | 18-MAY-16:00 | 242482.867 | 310109.712 | 88752.821 | 0 | 324790.777 | 0 | 54370.821 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6638.817 | 0 | 0
June | 2141570000000 | 1215137.13 | 29-JUN-16:30 | 242482.867 | 310109.712 | 88691.663 | 0 | 315210.264 | 0 | 54013.169 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6666.79 | 0 | 0
July | 2254280000000 | 1277677.626 | 18-JUL-12:30 | 242482.867 | 302612.437 | 84834.816 | 0 | 386887.274 | 0 | 55290.319 | 35000.029 | 162962.637 | 0 | 0 | 0 | 7607.246 | 0 | 0
August | 2273740000000 | 1246063.089 | 03-AUG-15:15 | 242482.867 | 310109.712 | 88636.769 | 0 | 345402.548 | 0 | 54798.744 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6669.782 | 0 | 0
September | 2052840000000 | 1256753.473 | 15-SEP-15:15 | 242482.867 | 310109.712 | 85537.244 | 0 | 359290.921 | 0 | 54748.116 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6621.947 | 0 | 0
October | 1981150000000 | 1168639.861 | 30-OCT-15:15 | 242482.867 | 310109.712 | 75505.537 | 0 | 283928.579 | 0 | 52300.902 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6349.597 | 0 | 0
November | 1820530000000 | 1129264.915 | 27-NOV-17:00 | 242482.867 | 310109.712 | 71921.523 | 0 | 245921.634 | 3239 | 51321.531 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6305.981 | 0 | 0
December | 1786260000000 | 1090817.136 | 06-DEC-16:15 | 242482.867 | 310109.712 | 71340.842 | 0 | 212613.382 | 0 | 50228.179 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6079.488 | 0 | 0
Annual Sum or Average | 23604000000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1595400000000 | 1060836.878 |  | 242482.867 | 302612.437 | 67502.266 | 0 | 184448.97 | 0 | 49082.419 | 35000.029 | 162962.637 | 0 | 0 | 0 | 6079.488 | 0 | 0
Maximum of Months | 2273740000000 | 1277677.626 |  | 242482.867 | 310109.712 | 88752.821 | 0 | 386887.274 | 3239 | 55290.319 | 35000.029 | 162962.637 | 0 | 0 | 0 | 10886.561 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 639244.3 | 113020.53 | 0 | 752264.83
Cost per Total Building Area ($/m2) | 28.51 | 5.04 | 0 | 33.55
Cost per Net Conditioned Building Area ($/m2) | 28.51 | 5.04 | 0 | 33.55

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 35221.11 | 1570.81 | 1570.81
Net Site Energy | 35221.11 | 1570.81 | 1570.81
Total Source Energy | 85173.62 | 3798.62 | 3798.62
Net Source Energy | 85173.62 | 3798.62 | 3798.62
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10812.07 | 0 | 0 | 0 | 0
Cooling | 3530.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.88 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2294.07 | 0 | 0 | 0 | 0 | 0
Pumps | 1312.32 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 974.8 | 0 | 0 | 0 | 0 | 30419.11
Humidification | 999.71 | 0 | 0 | 0 | 0 | 371.89
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 495.26 | 0 | 0 | 0 | 4037.61
Refrigeration | 199.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 22555.37 | 12665.75 | 0 | 0 | 0 | 34828.61
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.251 | 0.11 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.251 | 0.11 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.251 | 0.11 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.251 | 0.11 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.251 | 0.11 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 186.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2607714.06 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 2943142.86 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2428166.53
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 510134.34 | 326836.35 | 183297.99 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 285299.95 | 202028.41 | 83271.54 | 0.71 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 754106.94 | 487936.74 | 266170.21 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1351994.35 | 870624.64 | 481369.7 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 34254.8 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13514.52 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16079.49 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 16397.76 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41491.33 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47501.03 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15751.17 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15751.17 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 174620.8 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25932.73 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29530.08 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12961.6 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 55356.18 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 136796.87 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74757.19 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74757.19 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 55713.64 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26811.01 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27415.96 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 44827.85 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39376.3 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 196881.52 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39376.3 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 157515.11 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35471.29 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7429.2 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4105.48 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30099.43 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7248.2 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6579.99 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59060.17 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59060.17 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11967.96 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11920.28 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 62623.14 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 62269.02 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11313.3 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11275.88 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59060.17 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59060.17 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12212.58 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12132.48 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 80738.87 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 80140.29 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11836.27 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11762.63 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41347.24 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 103368.1 | -
CAV_1_HEATC | Coil:Heating:Water | 27340.97 | -
CAV_2_HEATC | Coil:Heating:Water | 131654.77 | -
VAV_1_HEATC | Coil:Heating:Water | 78766.35 | -
VAV_2_HEATC | Coil:Heating:Water | 159712.65 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.68 | 28075.98 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.42 | 21045.4 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 25.44 | 42818.1 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 44.93 | 74426.95 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23896.09 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16206.2 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 34270.18 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 425259.199 | 658.5525 | 1973.2722 | 0 | 0.0055 | 14573500 | 174742.6551
February | 387406.6579 | 602.5582 | 1816.611 | 0 | 0.0051 | 13416700 | 159454.0466
March | 432368.6298 | 681.6843 | 2093.9541 | 0 | 0.0058 | 15465500 | 178889.8088
April | 418378.3254 | 665.5252 | 2068.8683 | 0 | 0.0057 | 15280600 | 173697.8629
May | 437193.6126 | 700.707 | 2199.9013 | 0 | 0.0061 | 16248700 | 182040.469
June | 429462.3245 | 695.499 | 2212.9627 | 0 | 0.0061 | 16345600 | 179547.6714
July | 446041.1222 | 724.7485 | 2315.7578 | 0 | 0.0064 | 17105000 | 186721.6244
August | 450585.6281 | 731.6405 | 2335.7919 | 0 | 0.0064 | 17252900 | 188574.279
September | 418870.4751 | 675.2293 | 2135.8387 | 0 | 0.0059 | 15775700 | 174804.3223
October | 425015.8718 | 675.9218 | 2100.5196 | 0 | 0.0058 | 15514400 | 176437.1971
November | 407976.7461 | 640.6581 | 1957.2377 | 0 | 0.0054 | 14455600 | 168538.0012
December | 429245.0755 | 664.0693 | 1987.0238 | 0 | 0.0056 | 14675100 | 176314.179
Annual Sum or Average | 5107800 | 8116.7935 | 25197.739 | 0 | 0.0697 | 186109000 | 2119760
Minimum of Months | 387406.6579 | 602.5582 | 1816.611 | 0 | 0.0051 | 13416700 | 159454.0466
Maximum of Months | 450585.6281 | 731.6405 | 2335.7919 | 0 | 0.0064 | 17252900 | 188574.279
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1766230000000 | 1071257.704 | 25-JAN-16:15 | 242482.867 | 310109.712 | 75221.399 | 0 | 87231.955 | 0 | 41425.359 | 31869.686 | 162962.637 | 0 | 0 | 0 | 5686.339 | 0 | 0
February | 1626020000000 | 1104592.571 | 28-FEB-17:00 | 242482.867 | 310109.712 | 77700.721 | 0 | 120562.238 | 0 | 42703.49 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6181.868 | 0 | 0
March | 1874330000000 | 1143544.253 | 30-MAR-15:00 | 242482.867 | 310109.712 | 84915.804 | 0 | 142025.995 | 0 | 43728.746 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6417.475 | 0 | 0
April | 1851920000000 | 1127886.865 | 26-APR-16:00 | 242482.867 | 310109.712 | 89544.965 | 0 | 157393.462 | 0 | 44310.014 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6566.296 | 0 | 0
May | 1969250000000 | 1159125.206 | 19-MAY-16:00 | 242482.867 | 310109.712 | 94939.702 | 0 | 179308.897 | 0 | 45148.46 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6680.384 | 0 | 0
June | 1980990000000 | 1208965.98 | 08-JUN-15:00 | 242482.867 | 310109.712 | 102723.138 | 0 | 230019.826 | 0 | 46739.639 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6759.487 | 0 | 0
July | 2073020000000 | 1186141.257 | 11-JUL-16:15 | 242482.867 | 310109.712 | 101197.136 | 0 | 281847.941 | 0 | 48783.281 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6887.997 | 0 | 0
August | 2090950000000 | 1190249.674 | 11-AUG-16:00 | 242482.867 | 310109.712 | 100137.558 | 0 | 285652.344 | 0 | 50154.925 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6879.944 | 0 | 0
September | 1911930000000 | 1143765.97 | 12-SEP-15:15 | 242482.867 | 310109.712 | 98158.506 | 0 | 243855.259 | 0 | 47532.981 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6794.322 | 0 | 0
October | 1880250000000 | 1114682.099 | 02-OCT-16:00 | 242482.867 | 310109.712 | 87098.438 | 0 | 160363.811 | 0 | 44202.812 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6609.116 | 0 | 0
November | 1751940000000 | 1087264.305 | 15-NOV-16:00 | 242482.867 | 310109.712 | 80643.651 | 0 | 131668.789 | 0 | 43171.224 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6275.45 | 0 | 0
December | 1778530000000 | 1098582.853 | 06-DEC-16:45 | 242482.867 | 310109.712 | 75568.237 | 0 | 98881.336 | 0 | 41994.33 | 31869.686 | 162962.637 | 0 | 0 | 0 | 5849.112 | 0 | 0
Annual Sum or Average | 22555400000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1626020000000 | 1071257.704 |  | 242482.867 | 310109.712 | 75221.399 | 0 | 87231.955 | 0 | 41425.359 | 31869.686 | 162962.637 | 0 | 0 | 0 | 5686.339 | 0 | 0
Maximum of Months | 2090950000000 | 1208965.98 |  | 242482.867 | 310109.712 | 102723.138 | 0 | 285652.344 | 0 | 50154.925 | 31869.686 | 162962.637 | 0 | 0 | 0 | 6887.997 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 426815.18 | 108399.09 | 0 | 535214.27
Cost per Total Building Area ($/m2) | 19.04 | 4.83 | 0 | 23.87
Cost per Net Conditioned Building Area ($/m2) | 19.04 | 4.83 | 0 | 23.87

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 36151.98 | 1612.33 | 1612.33
Net Site Energy | 36151.98 | 1612.33 | 1612.33
Total Source Energy | 89283.18 | 3981.9 | 3981.9
Net Source Energy | 89283.18 | 3981.9 | 3981.9
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12236.83 | 0 | 0 | 0 | 0
Cooling | 3458.81 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2145.81 | 0 | 0 | 0 | 0 | 0
Pumps | 1319.53 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 891.35 | 0 | 0 | 0 | 0 | 18159.58
Humidification | 669.81 | 0 | 0 | 0 | 0 | 249.17
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 635.43 | 0 | 0 | 0 | 4037.61
Refrigeration | 190.84 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21921.31 | 14230.68 | 0 | 0 | 0 | 22446.35
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.252 | 0.162 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.252 | 0.162 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.252 | 0.162 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.252 | 0.162 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.252 | 0.162 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.252 | 0.162 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.252 | 0.162 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.252 | 0.162 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.252 | 0.162 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.252 | 0.162 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.252 | 0.162 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.252 | 0.162 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.328 | 0.244
North Total or Average |  |  | 186.18 | 3.24 | 0.343 | 0.26
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.324 | 0.239
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2619947.46 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3121575.52 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2439557.64
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 502611.54 | 319841.41 | 182770.13 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 268930.26 | 193694.09 | 75236.17 | 0.72 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 750245.99 | 483581.38 | 266664.61 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1303911.94 | 836746.21 | 467165.73 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 57160.97 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9869.95 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16125.49 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 14213.31 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34395.07 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44165.16 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15796.23 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15796.23 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 175120.4 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25933.69 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29614.57 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8931.83 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40593.36 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 122107.44 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74971.08 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74971.08 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42216.12 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26620.33 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27236.38 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41090.22 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39488.96 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 197444.81 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39488.96 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 157965.77 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31332.34 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5310.74 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2790.4 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 23665.91 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5235.84 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4724.07 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9873.32 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9873.32 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 57270.81 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 57270.81 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9873.32 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9873.32 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9292.51 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9260.77 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 68390.15 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 68149.47 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9155.42 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9124.57 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41465.54 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 103663.85 | -
CAV_1_HEATC | Coil:Heating:Water | 90250.56 | -
CAV_2_HEATC | Coil:Heating:Water | 161563.76 | -
VAV_1_HEATC | Coil:Heating:Water | 132223.04 | -
VAV_2_HEATC | Coil:Heating:Water | 236840 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.85 | 26859.73 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.09 | 20479.72 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 24.67 | 41526 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 42.27 | 70031.97 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24008.19 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17188.72 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 34430.95 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 415116.8401 | 719.6006 | 1682.2159 | 0 | 0.0063 | 2991600 | 175331.1185
February | 376585.2687 | 656.39 | 1543.637 | 0 | 0.0058 | 2745190 | 159387.6412
March | 418172.2448 | 738.2802 | 1760.2022 | 0 | 0.0066 | 3130430 | 177857.5788
April | 397016.548 | 705.0304 | 1691.2528 | 0 | 0.0063 | 3007850 | 169238.2993
May | 421605.8426 | 755.8745 | 1831.1873 | 0 | 0.0068 | 3256800 | 180383.0006
June | 425269.0251 | 769.6088 | 1882.2298 | 0 | 0.007 | 3347650 | 182612.1547
July | 447918.2738 | 813.5298 | 1996.851 | 0 | 0.0074 | 3551550 | 192608.671
August | 455007.9234 | 826.9599 | 2031.1709 | 0 | 0.0075 | 3612590 | 195708.4071
September | 424677.0318 | 767.1393 | 1872.7557 | 0 | 0.0069 | 3330790 | 182228.8253
October | 410524.013 | 730.0704 | 1753.9558 | 0 | 0.0065 | 3119380 | 175093.4553
November | 396469.2209 | 697.0597 | 1654.6128 | 0 | 0.0062 | 2942620 | 168358.6315
December | 410173.7909 | 714.0575 | 1677.0162 | 0 | 0.0063 | 2982380 | 173522.7636
Annual Sum or Average | 4998540 | 8893.6009 | 21377.0875 | 0 | 0.0795 | 38018800 | 2132330
Minimum of Months | 376585.2687 | 656.39 | 1543.637 | 0 | 0.0058 | 2745190 | 159387.6412
Maximum of Months | 455007.9234 | 826.9599 | 2031.1709 | 0 | 0.0075 | 3612590 | 195708.4071
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1724930000000 | 1025560.68 | 30-JAN-16:15 | 242482.867 | 310109.712 | 67664.476 | 0 | 65457.384 | 0 | 39732.692 | 32019.194 | 162962.637 | 0 | 0 | 0 | 5364.967 | 0 | 0
February | 1582850000000 | 1033380.87 | 06-FEB-16:15 | 242482.867 | 310109.712 | 67920.201 | 0 | 78222.356 | 0 | 40575.752 | 32019.194 | 162962.637 | 0 | 0 | 0 | 5622.239 | 0 | 0
March | 1804980000000 | 1068934.968 | 22-MAR-16:00 | 242482.867 | 310109.712 | 75530.503 | 0 | 104919.083 | 0 | 42069.011 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6092.202 | 0 | 0
April | 1734300000000 | 1051557.407 | 14-APR-16:00 | 242482.867 | 310109.712 | 78273.557 | 0 | 173906.116 | 0 | 45346.295 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6457.029 | 0 | 0
May | 1877840000000 | 1120353.842 | 31-MAY-16:00 | 242482.867 | 310109.712 | 80291.408 | 0 | 237764.599 | 0 | 48138.383 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6585.041 | 0 | 0
June | 1930230000000 | 1161374.213 | 08-JUN-15:00 | 242482.867 | 310109.712 | 84362.216 | 0 | 273441.484 | 0 | 49448.763 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6547.339 | 0 | 0
July | 2047790000000 | 1187789.244 | 25-JUL-15:00 | 242482.867 | 310109.712 | 81695.155 | 0 | 301672.345 | 0 | 50290.665 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6556.669 | 0 | 0
August | 2082990000000 | 1180398.43 | 17-AUG-15:15 | 242482.867 | 310109.712 | 84986.036 | 0 | 291361.236 | 0 | 49785.566 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6691.181 | 0 | 0
September | 1920500000000 | 1140321.161 | 01-SEP-15:45 | 242482.867 | 310109.712 | 84518.474 | 0 | 252886.979 | 0 | 48881.808 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6459.49 | 0 | 0
October | 1798610000000 | 1072403.872 | 20-OCT-16:00 | 242482.867 | 310109.712 | 77859.697 | 0 | 194023.085 | 0 | 46667.243 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6279.436 | 0 | 0
November | 1696690000000 | 1039318.027 | 03-NOV-15:15 | 242482.867 | 310109.712 | 71627.465 | 0 | 73415.303 | 0 | 40442.869 | 32019.194 | 162962.637 | 0 | 0 | 0 | 5504.837 | 0 | 0
December | 1719610000000 | 1026463.764 | 28-DEC-14:00 | 242482.867 | 302612.437 | 70535.073 | 0 | 68804.176 | 0 | 40078.786 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6301.095 | 0 | 0
Annual Sum or Average | 21921300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1582850000000 | 1025560.68 |  | 242482.867 | 302612.437 | 67664.476 | 0 | 65457.384 | 0 | 39732.692 | 32019.194 | 162962.637 | 0 | 0 | 0 | 5364.967 | 0 | 0
Maximum of Months | 2082990000000 | 1187789.244 |  | 242482.867 | 310109.712 | 84986.036 | 0 | 301672.345 | 0 | 50290.665 | 32019.194 | 162962.637 | 0 | 0 | 0 | 6691.181 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 596948.62 | 153606.22 | 0 | 750554.84
Cost per Total Building Area ($/m2) | 26.62 | 6.85 | 0 | 33.47
Cost per Net Conditioned Building Area ($/m2) | 26.62 | 6.85 | 0 | 33.47

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 34919.38 | 1557.35 | 1557.35
Net Site Energy | 34919.38 | 1557.35 | 1557.35
Total Source Energy | 79667.36 | 3553.05 | 3553.05
Net Source Energy | 79667.36 | 3553.05 | 3553.05
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12205.97 | 0 | 0 | 0 | 0
Cooling | 2928.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2099.45 | 0 | 0 | 0 | 0 | 0
Pumps | 1156.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 855.96 | 0 | 0 | 0 | 0 | 15381.99
Humidification | 258.96 | 0 | 0 | 0 | 0 | 96.33
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 618.41 | 0 | 0 | 0 | 4037.61
Refrigeration | 192.53 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20736.59 | 14182.79 | 0 | 0 | 0 | 19515.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.252 | 0.162 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.252 | 0.162 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.252 | 0.162 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.252 | 0.162 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.252 | 0.162 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.252 | 0.162 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.252 | 0.162 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.252 | 0.162 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.252 | 0.162 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.252 | 0.162 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.252 | 0.162 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.252 | 0.162 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.328 | 0.244
North Total or Average |  |  | 186.18 | 3.24 | 0.343 | 0.26
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.324 | 0.239
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2226423.62 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 2851945.86 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2073128.88
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 459417.46 | 306260.31 | 153157.16 | 0.67 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 270280.5 | 198754.98 | 71525.51 | 0.74 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 674420.58 | 455027.43 | 219393.15 | 0.67 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1177344.43 | 790279.89 | 387064.54 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 57624.8 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8977.28 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16676.07 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12560.9 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 31593.26 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43391.73 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16335.57 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16335.57 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 181099.64 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25927.82 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30625.72 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8167.81 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37435.31 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 112782.77 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77530.86 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77530.86 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 39347.17 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26567.99 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27185.87 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 38205.9 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40837.26 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204186.29 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40837.26 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 163359.29 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30965.05 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4728.4 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2823.01 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 21498.15 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4436.41 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 3778.79 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10210.43 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10210.43 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59226.24 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59226.24 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10210.43 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10210.43 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8525.79 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8480.38 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 63852.53 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63572.09 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8167.81 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8167.81 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42881.32 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107203.3 | -
CAV_1_HEATC | Coil:Heating:Water | 55555.64 | -
CAV_2_HEATC | Coil:Heating:Water | 148048.16 | -
VAV_1_HEATC | Coil:Heating:Water | 74534.97 | -
VAV_2_HEATC | Coil:Heating:Water | 122967.22 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.49 | 26248.02 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12 | 20337.7 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 23.58 | 39693.63 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 40.54 | 67157.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20402.09 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15704.03 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29259.32 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 214649.9608 | 187.2653 | 1362.5083 | 0 | 0.0008 | 8219030 | 78447.6716
February | 190130.0787 | 165.8532 | 1210.5216 | 0 | 0.0007 | 7302220 | 69497.5939
March | 213974.8864 | 186.532 | 1384.0652 | 0 | 0.0008 | 8349200 | 78279.7964
April | 203433.9278 | 177.3077 | 1322.1815 | 0 | 0.0007 | 7975920 | 74442.7482
May | 214175.4881 | 186.5195 | 1418.8745 | 0 | 0.0008 | 8559340 | 78455.4267
June | 210574.0473 | 183.2552 | 1417.9076 | 0 | 0.0008 | 8553610 | 77206.0121
July | 216897.5742 | 188.6426 | 1481.1909 | 0 | 0.0008 | 8935470 | 79587.6703
August | 222893.8869 | 193.7274 | 1545.4805 | 0 | 0.0008 | 9323410 | 81859.1493
September | 211071.9492 | 183.5773 | 1441.1652 | 0 | 0.0008 | 8694010 | 77449.2948
October | 216999.7814 | 188.8888 | 1453.7487 | 0 | 0.0008 | 8769790 | 79539.3193
November | 207477.902 | 180.796 | 1354.9698 | 0 | 0.0007 | 8173740 | 75942.4104
December | 213884.2826 | 186.5139 | 1372.5732 | 0 | 0.0008 | 8279820 | 78213.3767
Annual Sum or Average | 2536160 | 2208.879 | 16765.187 | 0 | 0.0091 | 101136000 | 928920.4695
Minimum of Months | 190130.0787 | 165.8532 | 1210.5216 | 0 | 0.0007 | 7302220 | 69497.5939
Maximum of Months | 222893.8869 | 193.7274 | 1545.4805 | 0 | 0.0008 | 9323410 | 81859.1493
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1685210000000 | 1039706.484 | 26-JAN-13:00 | 242482.867 | 302612.437 | 72410.961 | 0 | 115987.851 | 0 | 37680.996 | 27209.817 | 162962.637 | 0 | 0 | 0 | 7103.756 | 0 | 0
February | 1497230000000 | 1012000.475 | 10-FEB-10:00 | 242482.867 | 310109.712 | 69853.784 | 0 | 96375.998 | 0 | 37028.655 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6857.103 | 0 | 0
March | 1711900000000 | 1053502.867 | 31-MAR-15:00 | 242482.867 | 310109.712 | 76735.984 | 0 | 105730.264 | 0 | 37430.092 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6114.494 | 0 | 0
April | 1635360000000 | 1105291.951 | 11-APR-16:00 | 242482.867 | 310109.712 | 74813.586 | 0 | 127918.627 | 0 | 38057.92 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6431.112 | 0 | 0
May | 1754990000000 | 1033761.123 | 31-MAY-15:15 | 242482.867 | 310109.712 | 73873.845 | 0 | 169284.817 | 0 | 41685.179 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6152.249 | 0 | 0
June | 1753810000000 | 1052441.105 | 23-JUN-16:45 | 242482.867 | 310109.712 | 78519.251 | 0 | 182241.682 | 0 | 42703.402 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6211.738 | 0 | 0
July | 1832110000000 | 1057448.531 | 28-JUL-09:15 | 242482.867 | 310109.712 | 73841.784 | 0 | 191320.006 | 0 | 42637.797 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6883.911 | 0 | 0
August | 1911650000000 | 1089188.042 | 08-AUG-16:45 | 242482.867 | 310109.712 | 82189.458 | 0 | 214527.725 | 0 | 43272.623 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6433.203 | 0 | 0
September | 1782600000000 | 1071178.427 | 01-SEP-16:15 | 242482.867 | 310109.712 | 81993.903 | 0 | 196554.865 | 0 | 43669.079 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6195.547 | 0 | 0
October | 1798140000000 | 1058129.68 | 19-OCT-15:45 | 242482.867 | 310109.712 | 78587.413 | 0 | 187491.968 | 0 | 43129.805 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6155.462 | 0 | 0
November | 1675920000000 | 1025697.264 | 29-NOV-11:45 | 242482.867 | 310109.712 | 69709.156 | 0 | 85062.865 | 0 | 36538.475 | 27209.817 | 162962.637 | 0 | 0 | 0 | 10238.207 | 0 | 0
December | 1697670000000 | 1043903.413 | 18-DEC-11:45 | 242482.867 | 310109.712 | 66952.873 | 0 | 102101.756 | 0 | 37049.158 | 27209.817 | 162962.637 | 0 | 0 | 0 | 10880.936 | 0 | 0
Annual Sum or Average | 20736600000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1497230000000 | 1012000.475 |  | 242482.867 | 302612.437 | 66952.873 | 0 | 85062.865 | 0 | 36538.475 | 27209.817 | 162962.637 | 0 | 0 | 0 | 6114.494 | 0 | 0
Maximum of Months | 1911650000000 | 1105291.951 |  | 242482.867 | 310109.712 | 82189.458 | 0 | 214527.725 | 0 | 43669.079 | 27209.817 | 162962.637 | 0 | 0 | 0 | 10880.936 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 254982.64 | 119131.14 | 0 | 374113.78
Cost per Total Building Area ($/m2) | 11.37 | 5.31 | 0 | 16.68
Cost per Net Conditioned Building Area ($/m2) | 11.37 | 5.31 | 0 | 16.68

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 34453.84 | 1536.59 | 1536.59
Net Site Energy | 34453.84 | 1536.59 | 1536.59
Total Source Energy | 92197.72 | 4111.89 | 4111.89
Net Source Energy | 92197.72 | 4111.89 | 4111.89
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10575.66 | 0 | 0 | 0 | 0
Cooling | 2522.71 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2195.89 | 0 | 0 | 0 | 0 | 0
Pumps | 1109.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 773.64 | 0 | 0 | 0 | 0 | 25339.33
Humidification | 1921.29 | 0 | 0 | 0 | 0 | 714.72
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 558.34 | 0 | 0 | 0 | 4037.61
Refrigeration | 192.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21961.42 | 12492.42 | 0 | 0 | 0 | 30091.66
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.252 | 0.162 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.252 | 0.162 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.252 | 0.162 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.252 | 0.162 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.252 | 0.162 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.252 | 0.162 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.252 | 0.162 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.252 | 0.162 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.252 | 0.162 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.252 | 0.162 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.252 | 0.162 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.252 | 0.162 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.252 | 0.162 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.328 | 0.244
North Total or Average |  |  | 186.18 | 3.24 | 0.343 | 0.26
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.324 | 0.239
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2228829.33 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 2882360.55 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2075368.95
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 460940.6 | 294851.25 | 166089.34 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 244108.91 | 177978.24 | 66130.67 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 656067.7 | 422390.14 | 233677.56 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1220532.6 | 783130.51 | 437402.09 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 30295.33 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10297.36 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15466.93 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 14042.73 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34657.98 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44506.6 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15151.12 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15151.12 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 167968.59 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25939.6 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28405.13 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9415.2 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41810.35 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 124379.16 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 71909.3 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 71909.3 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43558.3 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26639.33 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27254.67 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 40656.2 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37876.26 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 189381.29 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37876.26 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 151514.54 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32086.9 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5538.05 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3033.55 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 23965.59 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5432.71 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4939.24 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 56810.26 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 56810.26 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9470.1 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9470.1 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 55076.87 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 54931.91 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9470.1 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9470.1 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 56810.26 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 56810.26 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9887.32 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9851.62 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 70784 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 70517.12 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9676.6 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9646.41 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 39772.11 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 99430.28 | -
CAV_1_HEATC | Coil:Heating:Water | 71598.23 | -
CAV_2_HEATC | Coil:Heating:Water | 144384.99 | -
VAV_1_HEATC | Coil:Heating:Water | 96546.11 | -
VAV_2_HEATC | Coil:Heating:Water | 187773.7 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.15 | 27184.58 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.16 | 20600.22 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 23.43 | 39437.25 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 43.15 | 71486.59 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20424.14 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15871.5 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29290.94 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 459804.732 | 702.3084 | 2679.9055 | 0 | 0.0052 | 13363600 | 188754.7494
February | 414321.6371 | 636.9101 | 2453.0952 | 0 | 0.0047 | 12232800 | 170506.77
March | 469001.1466 | 723.3143 | 2798.9171 | 0 | 0.0054 | 13957400 | 193253.2995
April | 457366.6773 | 711.3097 | 2785.3037 | 0 | 0.0053 | 13889700 | 189076.5319
May | 480422.6507 | 750.4783 | 2956.8347 | 0 | 0.0056 | 14745200 | 198952.0901
June | 475924.5587 | 749.3605 | 2984.6887 | 0 | 0.0057 | 14884400 | 197703.4887
July | 471972.5318 | 743.4166 | 2962.5243 | 0 | 0.0056 | 14773800 | 196090.7528
August | 479650.5784 | 755.4792 | 3010.4243 | 0 | 0.0057 | 15012700 | 199277.5017
September | 455431.3125 | 713.9469 | 2826.5963 | 0 | 0.0054 | 14095900 | 188863.3934
October | 458421.4305 | 711.6556 | 2779.559 | 0 | 0.0053 | 13861000 | 189378.0151
November | 440383.4373 | 677.8976 | 2616.089 | 0 | 0.005 | 13045600 | 181328.1209
December | 461393.5514 | 706.5752 | 2706.4602 | 0 | 0.0052 | 13496100 | 189598.2196
Annual Sum or Average | 5524090 | 8582.6523 | 33560.398 | 0 | 0.0642 | 167358000 | 2282780
Minimum of Months | 414321.6371 | 636.9101 | 2453.0952 | 0 | 0.0047 | 12232800 | 170506.77
Maximum of Months | 480422.6507 | 755.4792 | 3010.4243 | 0 | 0.0057 | 15012700 | 199277.5017
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1753630000000 | 1046803.913 | 30-JAN-16:00 | 242482.867 | 310109.712 | 69933.124 | 0 | 64331.107 | 3239 | 35008.617 | 27239.217 | 162962.637 | 0 | 0 | 0 | 5597.105 | 0 | 0
February | 1605230000000 | 1045779.464 | 17-FEB-17:30 | 242482.867 | 310109.712 | 74263.416 | 0 | 69139.318 | 3239 | 35281.597 | 27239.217 | 162962.637 | 0 | 0 | 0 | 5671.436 | 0 | 0
March | 1831540000000 | 1068177.567 | 21-MAR-15:00 | 242482.867 | 310109.712 | 74250.83 | 0 | 86559.566 | 0 | 36473.294 | 27239.217 | 162962.637 | 0 | 0 | 0 | 5903.629 | 0 | 0
April | 1822660000000 | 1066937.046 | 26-APR-16:15 | 242482.867 | 310109.712 | 80861.606 | 0 | 92075.127 | 0 | 36871.785 | 27239.217 | 162962.637 | 0 | 0 | 0 | 5950.929 | 0 | 0
May | 1934930000000 | 1154670.1 | 11-MAY-15:00 | 242482.867 | 310109.712 | 87864.561 | 0 | 143146.577 | 0 | 39042.821 | 27239.217 | 162962.637 | 0 | 0 | 0 | 6593.779 | 0 | 0
June | 1953190000000 | 1159378.411 | 29-JUN-15:00 | 242482.867 | 310109.712 | 93833.588 | 0 | 182676.802 | 0 | 40230.622 | 27239.217 | 162962.637 | 0 | 0 | 0 | 6721.033 | 0 | 0
July | 1938680000000 | 1142282.39 | 31-JUL-16:00 | 242482.867 | 310109.712 | 85400.93 | 0 | 143878.562 | 0 | 38839.934 | 27239.217 | 162962.637 | 0 | 0 | 0 | 6638.728 | 0 | 0
August | 1970030000000 | 1113284.604 | 02-AUG-16:00 | 242482.867 | 310109.712 | 91830.522 | 0 | 229626.659 | 0 | 42166.711 | 27239.217 | 162962.637 | 0 | 0 | 0 | 6866.278 | 0 | 0
September | 1849720000000 | 1125489.16 | 20-SEP-16:00 | 242482.867 | 310109.712 | 89956.747 | 0 | 156987.448 | 0 | 39289.849 | 27239.217 | 162962.637 | 0 | 0 | 0 | 6683.052 | 0 | 0
October | 1818900000000 | 1090798.013 | 31-OCT-15:45 | 242482.867 | 310109.712 | 78880.839 | 0 | 98329.658 | 0 | 37068.223 | 27239.217 | 162962.637 | 0 | 0 | 0 | 6020.691 | 0 | 0
November | 1711900000000 | 1033990.58 | 22-NOV-16:30 | 242482.867 | 310109.712 | 73737.524 | 0 | 72361.487 | 3239 | 35480.461 | 27239.217 | 162962.637 | 0 | 0 | 0 | 5690.819 | 0 | 0
December | 1771010000000 | 1044211.269 | 05-DEC-16:30 | 242482.867 | 310109.712 | 71923.295 | 0 | 86053.765 | 3239 | 36123.176 | 27239.217 | 162962.637 | 0 | 0 | 0 | 5818.513 | 0 | 0
Annual Sum or Average | 21961400000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1605230000000 | 1033990.58 |  | 242482.867 | 310109.712 | 69933.124 | 0 | 64331.107 | 0 | 35008.617 | 27239.217 | 162962.637 | 0 | 0 | 0 | 5597.105 | 0 | 0
Maximum of Months | 1970030000000 | 1159378.411 |  | 242482.867 | 310109.712 | 93833.588 | 0 | 229626.659 | 3239 | 42166.711 | 27239.217 | 162962.637 | 0 | 0 | 0 | 6866.278 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 531891.2 | 101808.13 | 0 | 633699.34
Cost per Total Building Area ($/m2) | 23.72 | 4.54 | 0 | 28.26
Cost per Net Conditioned Building Area ($/m2) | 23.72 | 4.54 | 0 | 28.26

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 36063.61 | 1608.39 | 1608.39
Net Site Energy | 36063.61 | 1608.39 | 1608.39
Total Source Energy | 78415.06 | 3497.2 | 3497.2
Net Source Energy | 78415.06 | 3497.2 | 3497.2
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14524.11 | 0 | 0 | 0 | 0
Cooling | 1870.79 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.85 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2232.62 | 0 | 0 | 0 | 0 | 0
Pumps | 993.84 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 758.33 | 0 | 0 | 0 | 0 | 9926.84
Humidification | 200.28 | 0 | 0 | 0 | 0 | 74.51
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 693.52 | 0 | 0 | 0 | 4037.61
Refrigeration | 186.65 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19487.57 | 16576.04 | 0 | 0 | 0 | 14038.95
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.39 | 0.223 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.39 | 0.223 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.39 | 0.223 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.39 | 0.223 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.39 | 0.223 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.39 | 0.223 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.39 | 0.223 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.39 | 0.223 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.39 | 0.223 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.39 | 0.223 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.39 | 0.223 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.39 | 0.223 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.39 | 0.223 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.39 | 0.223 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.39 | 0.223 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.39 | 0.223 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.61 | 0.474 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.61 | 0.474 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.61 | 0.474 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.61 | 0.474 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.61 | 0.474 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.61 | 0.474 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.61 | 0.474 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.61 | 0.474 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.61 | 0.474 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.61 | 0.474 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.61 | 0.474 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.61 | 0.474 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.61 | 0.474 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.61 | 0.474 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.61 | 0.474 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.61 | 0.474 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.61 | 0.474 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.516 | 0.367
North Total or Average |  |  | 186.18 | 5.83 | 0.541 | 0.395
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.509 | 0.359
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1985337.76 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3022250.31 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1848642.38
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 473021.57 | 323681.92 | 149339.65 | 0.68 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 250318.96 | 190510.4 | 59808.56 | 0.76 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 605063.25 | 414870.83 | 190192.42 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1107511.2 | 755752.53 | 351758.67 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 26375.88 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8774.93 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16729.39 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 10922.6 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34306.77 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44817.33 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16387.8 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16387.8 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 181678.66 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25927.3 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30723.64 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9090.53 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 47631.79 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 106873.95 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77778.74 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77778.74 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45053.53 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26561.72 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27179.97 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 35343.53 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40967.82 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204839.12 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40967.82 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 163881.59 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36503.17 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6481.01 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5016.28 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 24477.76 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4935.02 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 3450.48 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 81488.44 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 81002.06 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14978.57 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14876.42 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 66030.8 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 65611.57 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10243.07 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10243.07 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61447.27 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61447.27 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15123.71 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14995.77 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 87288.3 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 86570.02 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9970.92 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9882.43 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 43018.42 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107546.05 | -
CAV_1_HEATC | Coil:Heating:Water | 55080.63 | -
CAV_2_HEATC | Coil:Heating:Water | 147661.09 | -
VAV_1_HEATC | Coil:Heating:Water | 84766.69 | -
VAV_2_HEATC | Coil:Heating:Water | 154941.79 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.4 | 29286.39 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.34 | 20910.82 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 22.38 | 37679.15 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 40.41 | 66937.77 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18192.87 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16641.79 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 26091.01 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 222078.8565 | 194.3425 | 1303.019 | 0 | 0.0008 | 7859650 | 80837.3255
February | 195420.4632 | 170.8503 | 1175.8298 | 0 | 0.0007 | 7092620 | 71222.7613
March | 219986.0921 | 192.2651 | 1334.7562 | 0 | 0.0008 | 8051320 | 80209.8453
April | 206869.2809 | 180.7512 | 1264.1106 | 0 | 0.0007 | 7625230 | 75454.5578
May | 215121.8787 | 187.8164 | 1340.5677 | 0 | 0.0008 | 8086560 | 78544.0633
June | 208691.3814 | 182.0819 | 1322.0163 | 0 | 0.0007 | 7974760 | 76261.8577
July | 211808.2341 | 184.7624 | 1348.7282 | 0 | 0.0007 | 8135930 | 77422.1026
August | 217531.67 | 189.6706 | 1400.2746 | 0 | 0.0008 | 8446940 | 79560.2595
September | 207979.8243 | 181.3579 | 1335.9675 | 0 | 0.0007 | 8059010 | 76058.1512
October | 215097.1494 | 187.7407 | 1350.1075 | 0 | 0.0008 | 8144150 | 78564.61
November | 211222.3431 | 184.5926 | 1283.9241 | 0 | 0.0007 | 7744710 | 77021.6101
December | 220792.2302 | 193.2083 | 1296.9418 | 0 | 0.0008 | 7823000 | 80373.4808
Annual Sum or Average | 2552600 | 2229.4398 | 15756.2432 | 0 | 0.0089 | 95043900 | 931530.6252
Minimum of Months | 195420.4632 | 170.8503 | 1175.8298 | 0 | 0.0007 | 7092620 | 71222.7613
Maximum of Months | 222078.8565 | 194.3425 | 1400.2746 | 0 | 0.0008 | 8446940 | 80837.3255
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1611520000000 | 1000434.551 | 20-JAN-14:00 | 242482.867 | 302612.437 | 77132.499 | 0 | 51228.158 | 0 | 31463.516 | 24263.431 | 162962.637 | 0 | 0 | 0 | 6339.007 | 0 | 0
February | 1454250000000 | 979976.939 | 15-FEB-16:30 | 242482.867 | 310109.712 | 79522.485 | 0 | 119032.265 | 0 | 35478.745 | 24263.431 | 162962.637 | 0 | 0 | 0 | 6124.797 | 0 | 0
March | 1650820000000 | 982531.488 | 13-MAR-12:00 | 242482.867 | 302612.437 | 71798.513 | 0 | 63444.592 | 0 | 32276.693 | 24263.431 | 162962.637 | 0 | 0 | 0 | 6486.071 | 0 | 0
April | 1563460000000 | 1017395.253 | 13-APR-15:00 | 242482.867 | 310109.712 | 84135.53 | 0 | 101958.62 | 0 | 34680.934 | 24263.431 | 162962.637 | 0 | 0 | 0 | 6075.59 | 0 | 0
May | 1658050000000 | 1009676.075 | 24-MAY-16:00 | 242482.867 | 310109.712 | 81182.389 | 0 | 144511.869 | 0 | 37999.487 | 24263.431 | 162962.637 | 0 | 0 | 0 | 6163.682 | 0 | 0
June | 1635130000000 | 998895.169 | 16-JUN-15:30 | 242482.867 | 310109.712 | 85332.292 | 0 | 131671.391 | 0 | 35713.628 | 24263.431 | 162962.637 | 0 | 0 | 0 | 6359.211 | 0 | 0
July | 1668170000000 | 1012910.121 | 03-JUL-12:00 | 242482.867 | 302612.437 | 76830.808 | 0 | 159603.486 | 0 | 36718.518 | 24263.431 | 162962.637 | 0 | 0 | 0 | 7435.938 | 0 | 0
August | 1731940000000 | 1009490.269 | 15-AUG-12:15 | 242482.867 | 302612.437 | 77167.476 | 0 | 155835.79 | 0 | 36810.264 | 24263.431 | 162962.637 | 0 | 0 | 0 | 7355.367 | 0 | 0
September | 1652400000000 | 1041458.83 | 28-SEP-15:00 | 242482.867 | 310109.712 | 89865.34 | 0 | 167792.793 | 0 | 37259.372 | 24263.431 | 162962.637 | 0 | 0 | 0 | 6722.677 | 0 | 0
October | 1669860000000 | 1001725.252 | 30-OCT-13:15 | 242482.867 | 302612.437 | 74123.147 | 0 | 105698.908 | 0 | 34471.843 | 24263.431 | 162962.637 | 0 | 0 | 0 | 7008.776 | 0 | 0
November | 1587960000000 | 973808.775 | 20-NOV-11:45 | 242482.867 | 310109.712 | 70939.191 | 0 | 50994.748 | 0 | 31263.198 | 24263.431 | 162962.637 | 0 | 0 | 0 | 9337.654 | 0 | 0
December | 1604010000000 | 995585.871 | 29-DEC-16:00 | 242482.867 | 310109.712 | 75118.122 | 0 | 33780.646 | 3239 | 29923.252 | 24263.431 | 162962.637 | 0 | 0 | 0 | 5394.214 | 0 | 0
Annual Sum or Average | 19487600000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1454250000000 | 973808.775 |  | 242482.867 | 302612.437 | 70939.191 | 0 | 33780.646 | 0 | 29923.252 | 24263.431 | 162962.637 | 0 | 0 | 0 | 5394.214 | 0 | 0
Maximum of Months | 1731940000000 | 1041458.83 |  | 242482.867 | 310109.712 | 89865.34 | 0 | 167792.793 | 3239 | 37999.487 | 24263.431 | 162962.637 | 0 | 0 | 0 | 9337.654 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 705957.54 | 139307.07 | 0 | 845264.62
Cost per Total Building Area ($/m2) | 31.48 | 6.21 | 0 | 37.7
Cost per Net Conditioned Building Area ($/m2) | 31.48 | 6.21 | 0 | 37.7

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 37720.38 | 1682.28 | 1682.28
Net Site Energy | 37720.38 | 1682.28 | 1682.28
Total Source Energy | 95000.91 | 4236.91 | 4236.91
Net Source Energy | 95000.91 | 4236.91 | 4236.91
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13994.81 | 0 | 0 | 0 | 0
Cooling | 2918.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2126.17 | 0 | 0 | 0 | 0 | 0
Pumps | 1308.54 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 787.87 | 0 | 0 | 0 | 0 | 15583.5
Humidification | 1090.62 | 0 | 0 | 0 | 0 | 405.71
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 704.41 | 0 | 0 | 0 | 4037.61
Refrigeration | 185.78 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21662.74 | 16057.64 | 0 | 0 | 0 | 20026.81
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2670466.32 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3295700.69 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2486598.14
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 511908.56 | 330935.07 | 180973.49 | 0.65 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 265741.07 | 196756.72 | 68984.35 | 0.74 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 759091.87 | 497295.92 | 261795.95 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1324604.26 | 863505.73 | 461098.53 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 53596.53 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10004.14 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16646.51 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 13771.53 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34401.6 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45690.51 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16306.61 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16306.61 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 180778.62 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25928.44 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30571.43 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10260.67 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 47794.41 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 119906.11 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77393.42 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77393.42 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46068.86 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26609.94 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27225.95 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 40290.73 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40764.87 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 203824.34 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40764.87 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 163069.71 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31842.09 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6041.15 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3055.72 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 26580.27 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5888.93 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4814.06 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10192.33 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10192.33 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59121.26 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59121.26 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10192.33 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10192.33 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9475.33 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9434.23 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 68677.84 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 68400.27 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9128.9 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9093.7 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42805.31 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107013.27 | -
CAV_1_HEATC | Coil:Heating:Water | 108762.63 | -
CAV_2_HEATC | Coil:Heating:Water | 174114.21 | -
VAV_1_HEATC | Coil:Heating:Water | 145762.7 | -
VAV_2_HEATC | Coil:Heating:Water | 271132.79 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.76 | 26694.97 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.1 | 20504.46 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 24.41 | 41091.75 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 41.92 | 69448.11 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24471.13 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18147.53 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 35094.86 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 387018.434 | 668.2698 | 1751.8151 | 0 | 0.0073 | 108923.6736 | 162930.8863
February | 342865.7636 | 597.9291 | 1584.5283 | 0 | 0.0065 | 98524.4857 | 144882.3727
March | 376932.3472 | 669.9048 | 1811.3512 | 0 | 0.0075 | 112632.9263 | 160426.6927
April | 355802.5622 | 635.5505 | 1727.4734 | 0 | 0.0071 | 107418.4394 | 151726.0914
May | 372516.7015 | 674.4297 | 1858.4478 | 0 | 0.0076 | 115566.0245 | 159678.6561
June | 377071.3222 | 694.4305 | 1946.075 | 0 | 0.008 | 121019.2148 | 162705.8075
July | 393296.2353 | 728.4593 | 2052.7177 | 0 | 0.0084 | 127652.3518 | 170086.1523
August | 403623.371 | 748.9648 | 2114.2249 | 0 | 0.0086 | 131477.766 | 174678.2324
September | 362672.5748 | 661.0898 | 1834.0875 | 0 | 0.0075 | 114052.7894 | 155868.8652
October | 370114.9086 | 666.2141 | 1825.1124 | 0 | 0.0075 | 113491.7207 | 158295.5247
November | 360691.015 | 640.9421 | 1732.7637 | 0 | 0.0071 | 107746.1878 | 153505.2611
December | 375504.7952 | 654.1897 | 1731.7282 | 0 | 0.0072 | 107676.9836 | 158614.1575
Annual Sum or Average | 4478110 | 8040.3742 | 21970.3251 | 0 | 0.0902 | 1366180 | 1913400
Minimum of Months | 342865.7636 | 597.9291 | 1584.5283 | 0 | 0.0065 | 98524.4857 | 144882.3727
Maximum of Months | 403623.371 | 748.9648 | 2114.2249 | 0 | 0.0086 | 131477.766 | 174678.2324
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1727140000000 | 1035111.602 | 05-JAN-16:15 | 242482.867 | 310109.712 | 69916.865 | 0 | 65790.208 | 0 | 40443.025 | 32636.601 | 162962.637 | 0 | 0 | 0 | 5293.738 | 0 | 0
February | 1562240000000 | 996681.24 | 16-FEB-16:15 | 242482.867 | 310109.712 | 70687.097 | 0 | 48623.837 | 0 | 39550.315 | 22774.824 | 162962.637 | 0 | 0 | 0 | 5201.984 | 0 | 0
March | 1785950000000 | 1042136.304 | 17-MAR-16:00 | 242482.867 | 310109.712 | 71634.741 | 0 | 86454.616 | 0 | 41760.616 | 32636.601 | 162962.637 | 0 | 0 | 0 | 5741.633 | 0 | 0
April | 1703270000000 | 1037672.532 | 20-APR-15:00 | 242482.867 | 310109.712 | 70756.896 | 0 | 78937.344 | 0 | 41478.441 | 32636.601 | 162962.637 | 0 | 0 | 0 | 5653.727 | 0 | 0
May | 1832460000000 | 1122192.172 | 31-MAY-15:00 | 242482.867 | 310109.712 | 72704.263 | 0 | 246009.682 | 0 | 48872.182 | 32636.601 | 162962.637 | 0 | 0 | 0 | 6414.228 | 0 | 0
June | 1918930000000 | 1214285.71 | 30-JUN-16:00 | 242482.867 | 310109.712 | 86427.161 | 0 | 321504.618 | 0 | 51347.13 | 32636.601 | 162962.637 | 0 | 0 | 0 | 6814.984 | 0 | 0
July | 2024110000000 | 1225772.339 | 25-JUL-10:45 | 242482.867 | 310109.712 | 78368.172 | 0 | 336138.101 | 0 | 51204.272 | 32636.601 | 162962.637 | 0 | 0 | 0 | 11869.976 | 0 | 0
August | 2084760000000 | 1269974.276 | 09-AUG-16:00 | 242482.867 | 310109.712 | 85424.743 | 0 | 377145.407 | 0 | 52553.423 | 32636.601 | 162962.637 | 0 | 0 | 0 | 6658.886 | 0 | 0
September | 1808470000000 | 1104435.176 | 27-SEP-15:15 | 242482.867 | 310109.712 | 75010.903 | 0 | 226749.614 | 0 | 48231.407 | 32636.601 | 162962.637 | 0 | 0 | 0 | 6251.435 | 0 | 0
October | 1799570000000 | 1076055.308 | 03-OCT-10:45 | 242482.867 | 310109.712 | 69693.399 | 0 | 200175.92 | 0 | 47001.85 | 32636.601 | 162962.637 | 0 | 0 | 0 | 10992.322 | 0 | 0
November | 1708470000000 | 1032998.773 | 03-NOV-13:00 | 242482.867 | 302612.437 | 72300.475 | 0 | 167172.847 | 0 | 45739.279 | 32636.601 | 162962.637 | 0 | 0 | 0 | 7091.631 | 0 | 0
December | 1707370000000 | 1006838.879 | 06-DEC-16:45 | 242482.867 | 310109.712 | 69599.107 | 0 | 48045.147 | 3239 | 39547.188 | 20578.177 | 162962.637 | 0 | 0 | 0 | 5190.966 | 0 | 0
Annual Sum or Average | 21662700000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1562240000000 | 996681.24 |  | 242482.867 | 302612.437 | 69599.107 | 0 | 48045.147 | 0 | 39547.188 | 20578.177 | 162962.637 | 0 | 0 | 0 | 5190.966 | 0 | 0
Maximum of Months | 2084760000000 | 1269974.276 |  | 242482.867 | 310109.712 | 86427.161 | 0 | 377145.407 | 3239 | 52553.423 | 32636.601 | 162962.637 | 0 | 0 | 0 | 11869.976 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 333846.45 | 162057.28 | 0 | 495903.73
Cost per Total Building Area ($/m2) | 14.89 | 7.23 | 0 | 22.12
Cost per Net Conditioned Building Area ($/m2) | 14.89 | 7.23 | 0 | 22.12

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 32437.97 | 1446.69 | 1446.69
Net Site Energy | 32437.97 | 1446.69 | 1446.69
Total Source Energy | 81421.3 | 3631.27 | 3631.27
Net Source Energy | 81421.3 | 3631.27 | 3631.27
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9723.79 | 0 | 0 | 0 | 0
Cooling | 1719.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2214.71 | 0 | 0 | 0 | 0 | 0
Pumps | 924.5 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 535.47 | 0 | 0 | 0 | 0 | 15428.91
Humidification | 1841.02 | 0 | 0 | 0 | 0 | 684.86
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 691.32 | 0 | 0 | 0 | 4037.61
Refrigeration | 184.57 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20664.44 | 11773.53 | 0 | 0 | 0 | 20151.38
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1872287.04 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 2772561.12 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1743375.48
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 405913.57 | 249500.73 | 156412.84 | 0.61 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 197141.92 | 144434.16 | 52707.76 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 631416.71 | 393540.99 | 237875.72 | 0.62 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1103817.31 | 681774.11 | 422043.2 | 0.62 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 40311.85 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9385.58 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13775.78 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12176.5 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 31657.76 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44424.33 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13494.5 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13494.5 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 149602.94 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25951.74 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25299.32 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9071.33 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 44549.22 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 125768.27 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64046.75 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64046.75 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42787.66 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26596.43 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27211.54 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 38180.73 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33734.87 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 168674.37 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33734.87 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 134947.97 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30018.34 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5321.95 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2499.73 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 24825.61 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5245.76 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4116.15 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8434.64 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8434.64 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 48925.66 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 48925.66 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8434.64 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8434.64 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8112.5 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8069.4 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 63406.86 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63115.87 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7933.66 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 7894.19 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35423.44 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88558.59 | -
CAV_1_HEATC | Coil:Heating:Water | 82846.68 | -
CAV_2_HEATC | Coil:Heating:Water | 141273.73 | -
VAV_1_HEATC | Coil:Heating:Water | 115454.2 | -
VAV_2_HEATC | Coil:Heating:Water | 216233.73 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.15 | 27182.92 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.14 | 20565.72 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 26.07 | 43882.28 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 44.49 | 73703.82 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17156.92 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15266.9 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 24605.31 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 521953.5017 | 857.9758 | 2081.6834 | 0 | 0.0082 | 2164260 | 218334.3191
February | 466640.8759 | 770.8646 | 1881.707 | 0 | 0.0074 | 1956380 | 195570.6939
March | 528977.4553 | 878.5697 | 2158.6697 | 0 | 0.0085 | 2244370 | 222159.9788
April | 507029.994 | 847.6434 | 2099.0147 | 0 | 0.0083 | 2182390 | 213484.5149
May | 531787.2772 | 895.1435 | 2234.5829 | 0 | 0.0088 | 2323380 | 224507.9993
June | 502441.4154 | 848.1759 | 2124.4207 | 0 | 0.0084 | 2208860 | 212357.183
July | 504315.073 | 851.9834 | 2135.8315 | 0 | 0.0084 | 2220730 | 213212.3075
August | 516315.0303 | 872.5997 | 2188.5133 | 0 | 0.0086 | 2275510 | 218319.322
September | 480014.5915 | 806.5339 | 2009.1198 | 0 | 0.0079 | 2088950 | 202507.3918
October | 503859.7636 | 841.1702 | 2079.5402 | 0 | 0.0082 | 2162130 | 212034.6071
November | 499327.009 | 827.0104 | 2025.1496 | 0 | 0.008 | 2105530 | 209480.4589
December | 514416.3396 | 845.4502 | 2050.8866 | 0 | 0.0081 | 2132250 | 215168.1564
Annual Sum or Average | 6077080 | 10143.1209 | 25069.1194 | 0 | 0.0989 | 26064700 | 2557140
Minimum of Months | 466640.8759 | 770.8646 | 1881.707 | 0 | 0.0074 | 1956380 | 195570.6939
Maximum of Months | 531787.2772 | 895.1435 | 2234.5829 | 0 | 0.0088 | 2323380 | 224507.9993
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1715860000000 | 1013842.357 | 20-JAN-16:15 | 242482.867 | 310109.712 | 74855.549 | 0 | 41890.526 | 0 | 28823.356 | 22881.803 | 162962.637 | 0 | 0 | 0 | 5352.228 | 0 | 0
February | 1551040000000 | 1044565.129 | 13-FEB-16:45 | 242482.867 | 310109.712 | 72870.174 | 0 | 72734.472 | 0 | 30967.906 | 22881.803 | 162962.637 | 0 | 0 | 0 | 5789.397 | 0 | 0
March | 1779360000000 | 1059972.725 | 02-MAR-16:15 | 242482.867 | 310109.712 | 78527.989 | 0 | 80474.523 | 0 | 31592.492 | 22881.803 | 162962.637 | 0 | 0 | 0 | 5849.332 | 0 | 0
April | 1730220000000 | 1105949.363 | 21-APR-16:00 | 242482.867 | 310109.712 | 87469.271 | 0 | 103811.323 | 0 | 33048.535 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6282.606 | 0 | 0
May | 1842010000000 | 1097596.193 | 12-MAY-16:00 | 242482.867 | 310109.712 | 89012.131 | 0 | 105262.781 | 0 | 33093.45 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6263.296 | 0 | 0
June | 1751210000000 | 1132287.198 | 26-JUN-16:00 | 242482.867 | 310109.712 | 88005.895 | 0 | 118375.77 | 0 | 33687.407 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6519.73 | 0 | 0
July | 1760620000000 | 1109712.745 | 31-JUL-16:00 | 242482.867 | 310109.712 | 91499.448 | 0 | 139704.002 | 0 | 34311.433 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6665.881 | 0 | 0
August | 1804050000000 | 1047774.011 | 01-AUG-16:00 | 242482.867 | 310109.712 | 93388.743 | 0 | 173227.571 | 0 | 35935.616 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6785.062 | 0 | 0
September | 1656140000000 | 1076765.94 | 20-SEP-16:00 | 242482.867 | 310109.712 | 93127.323 | 0 | 121729.139 | 0 | 33756.821 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6458.689 | 0 | 0
October | 1714160000000 | 1048824.638 | 13-OCT-15:15 | 242482.867 | 310109.712 | 83444.491 | 0 | 99953.658 | 0 | 32566.786 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6156.814 | 0 | 0
November | 1669290000000 | 1023111.293 | 13-NOV-17:00 | 242482.867 | 310109.712 | 70745.274 | 0 | 47535.989 | 3239 | 29071.254 | 22881.803 | 162962.637 | 0 | 0 | 0 | 5453.549 | 0 | 0
December | 1690470000000 | 993399.428 | 05-DEC-16:15 | 242482.867 | 310109.712 | 73646.085 | 0 | 49093.116 | 0 | 29270.438 | 22881.803 | 162962.637 | 0 | 0 | 0 | 5441.091 | 0 | 0
Annual Sum or Average | 20664400000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1551040000000 | 993399.428 |  | 242482.867 | 310109.712 | 70745.274 | 0 | 41890.526 | 0 | 28823.356 | 22881.803 | 162962.637 | 0 | 0 | 0 | 5352.228 | 0 | 0
Maximum of Months | 1842010000000 | 1132287.198 |  | 242482.867 | 310109.712 | 93388.743 | 0 | 173227.571 | 3239 | 35935.616 | 22881.803 | 162962.637 | 0 | 0 | 0 | 6785.062 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 212162.4 | 84650.49 | 0 | 296812.89
Cost per Total Building Area ($/m2) | 9.46 | 3.78 | 0 | 13.24
Cost per Net Conditioned Building Area ($/m2) | 9.46 | 3.78 | 0 | 13.24

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 35328.18 | 1575.59 | 1575.59
Net Site Energy | 35328.18 | 1575.59 | 1575.59
Total Source Energy | 51090.76 | 2278.58 | 2278.58
Net Source Energy | 51090.76 | 2278.58 | 2278.58
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13979.6 | 0 | 0 | 0 | 0
Cooling | 1520.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2089.25 | 0 | 0 | 0 | 0 | 0
Pumps | 967.25 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 691.18 | 0 | 0 | 0 | 0 | 8713.17
Humidification | 553.85 | 0 | 0 | 0 | 0 | 206.03
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 740.33 | 0 | 0 | 0 | 4037.61
Refrigeration | 182.32 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19249.83 | 16078.34 | 0 | 0 | 0 | 12956.81
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1993251.14 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3071423.35 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1856010.9
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 433871.9 | 291361.8 | 142510.09 | 0.67 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 230356.06 | 177332.28 | 53023.78 | 0.77 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 619887.09 | 419067.19 | 200819.9 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1136324.87 | 764930.74 | 371394.13 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 34478.36 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9386.55 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16499.34 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12228.52 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 33465.39 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44676.24 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16162.45 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16162.45 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 179180.41 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25929.79 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30301.16 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9065.7 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 45157.55 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 111849.65 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76709.21 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76709.21 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43609.39 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26591.64 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27208.63 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37760.09 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40404.48 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 202022.39 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40404.48 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 161628.06 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34393.3 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5881.18 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4129.36 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 24552.27 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5154.22 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 3967.26 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10102.22 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10102.22 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58598.58 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58598.58 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10102.22 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10102.22 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9583.15 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9539.19 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64440.03 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64168.2 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8081.25 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8081.25 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42426.88 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 106067.2 | -
CAV_1_HEATC | Coil:Heating:Water | 88457.64 | -
CAV_2_HEATC | Coil:Heating:Water | 158986.68 | -
VAV_1_HEATC | Coil:Heating:Water | 118936.53 | -
VAV_2_HEATC | Coil:Heating:Water | 218010.86 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.58 | 26401.1 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.06 | 20426.33 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 22.7 | 38215.08 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 41.1 | 68092.3 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18265.39 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16912.56 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 26195 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 160418.9104 | 199.5823 | 345.2416 | 0 | 0.0015 | 4557900 | 61301.1145
February | 141470.4528 | 177.5369 | 314.2251 | 0 | 0.0014 | 4148720 | 54224.0777
March | 155109.4352 | 196.0434 | 353.3959 | 0 | 0.0015 | 4666170 | 59600.6529
April | 144595.775 | 183.5571 | 334.5623 | 0 | 0.0014 | 4417650 | 55646.6799
May | 144096.4137 | 185.3544 | 348.93 | 0 | 0.0015 | 4607820 | 55714.8928
June | 138027.433 | 179.6711 | 347.7916 | 0 | 0.0015 | 4593170 | 53595.7408
July | 140236.0437 | 183.6857 | 360.6327 | 0 | 0.0015 | 4762950 | 54575.3899
August | 143065.5004 | 188.7393 | 376.513 | 0 | 0.0016 | 4972910 | 55820.8491
September | 138403.3418 | 179.2748 | 343.0843 | 0 | 0.0015 | 4530850 | 53646.8553
October | 147557.9428 | 187.3445 | 341.589 | 0 | 0.0015 | 4510440 | 56789.5488
November | 151547.1402 | 189.9978 | 335.4267 | 0 | 0.0015 | 4428610 | 58066.567
December | 158300.2459 | 196.1905 | 335.8557 | 0 | 0.0015 | 4433830 | 60410.5485
Annual Sum or Average | 1762830 | 2246.9777 | 4137.2479 | 0 | 0.0178 | 54631000 | 679392.9174
Minimum of Months | 138027.433 | 177.5369 | 314.2251 | 0 | 0.0014 | 4148720 | 53595.7408
Maximum of Months | 160418.9104 | 199.5823 | 376.513 | 0 | 0.0016 | 4972910 | 61301.1145
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1606020000000 | 964527.156 | 03-JAN-17:00 | 242482.867 | 310109.712 | 66985.025 | 0 | 21735.793 | 3239 | 28945.346 | 5768.256 | 162962.637 | 0 | 0 | 0 | 5111.632 | 0 | 0
February | 1461850000000 | 974889.203 | 22-FEB-11:45 | 242482.867 | 310109.712 | 66449.379 | 0 | 59442.072 | 0 | 31744.197 | 24360.143 | 162962.637 | 0 | 0 | 0 | 9669.692 | 0 | 0
March | 1644180000000 | 976021.172 | 23-MAR-15:00 | 242482.867 | 310109.712 | 72070.256 | 0 | 56074.716 | 0 | 31456.647 | 24360.143 | 162962.637 | 0 | 0 | 0 | 5628.887 | 0 | 0
April | 1556610000000 | 967958.233 | 14-APR-16:00 | 242482.867 | 310109.712 | 72813.681 | 0 | 83541.244 | 0 | 33247.733 | 24360.143 | 162962.637 | 0 | 0 | 0 | 5958.356 | 0 | 0
May | 1623620000000 | 995237.027 | 05-MAY-15:00 | 242482.867 | 310109.712 | 75987.854 | 0 | 136913.329 | 0 | 36084.867 | 24360.143 | 162962.637 | 0 | 0 | 0 | 6335.618 | 0 | 0
June | 1618450000000 | 998941.931 | 27-JUN-16:00 | 242482.867 | 310109.712 | 78007.03 | 0 | 121252.148 | 0 | 34854.461 | 24360.143 | 162962.637 | 0 | 0 | 0 | 6411.616 | 0 | 0
July | 1678280000000 | 1029304.456 | 27-JUL-16:00 | 242482.867 | 310109.712 | 82492.827 | 0 | 162649.419 | 0 | 37830.56 | 24360.143 | 162962.637 | 0 | 0 | 0 | 6416.291 | 0 | 0
August | 1752260000000 | 1027342.851 | 18-AUG-16:00 | 242482.867 | 310109.712 | 82362.165 | 0 | 161111.014 | 0 | 37474.473 | 24360.143 | 162962.637 | 0 | 0 | 0 | 6479.84 | 0 | 0
September | 1596490000000 | 1027025.587 | 01-SEP-16:30 | 242482.867 | 310109.712 | 79737.391 | 0 | 163681.988 | 0 | 37166.429 | 24360.143 | 162962.637 | 0 | 0 | 0 | 6524.419 | 0 | 0
October | 1589300000000 | 971025.852 | 17-OCT-16:00 | 242482.867 | 310109.712 | 72085.701 | 0 | 96611.396 | 0 | 33635.94 | 24360.143 | 162962.637 | 0 | 0 | 0 | 6066.953 | 0 | 0
November | 1560470000000 | 957869.634 | 28-NOV-17:00 | 242482.867 | 310109.712 | 68286.838 | 0 | 17375.339 | 3239 | 28499.381 | 2699.552 | 162962.637 | 0 | 0 | 0 | 5039.756 | 0 | 0
December | 1562310000000 | 928254.766 | 07-DEC-17:00 | 242482.867 | 310109.712 | 69487.045 | 0 | 24353.262 | 3239 | 29184.702 | 24201.609 | 162962.637 | 0 | 0 | 0 | 5275.701 | 0 | 0
Annual Sum or Average | 19249800000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1461850000000 | 928254.766 |  | 242482.867 | 310109.712 | 66449.379 | 0 | 17375.339 | 0 | 28499.381 | 2699.552 | 162962.637 | 0 | 0 | 0 | 5039.756 | 0 | 0
Maximum of Months | 1752260000000 | 1029304.456 |  | 242482.867 | 310109.712 | 82492.827 | 0 | 163681.988 | 3239 | 37830.56 | 24360.143 | 162962.637 | 0 | 0 | 0 | 9669.692 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 351646.18 | 133231.97 | 0 | 484878.15
Cost per Total Building Area ($/m2) | 15.68 | 5.94 | 0 | 21.62
Cost per Net Conditioned Building Area ($/m2) | 15.68 | 5.94 | 0 | 21.62

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 37716.07 | 1682.08 | 1682.08
Net Site Energy | 37716.07 | 1682.08 | 1682.08
Total Source Energy | 92404.18 | 4121.09 | 4121.09
Net Source Energy | 92404.18 | 4121.09 | 4121.09
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14721.35 | 0 | 0 | 0 | 0
Cooling | 2138.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2121.94 | 0 | 0 | 0 | 0 | 0
Pumps | 1230.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 649.77 | 0 | 0 | 0 | 0 | 12288.43
Humidification | 1303.43 | 0 | 0 | 0 | 0 | 484.88
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 764.98 | 0 | 0 | 0 | 4037.61
Refrigeration | 182.29 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20871.33 | 16844.74 | 0 | 0 | 0 | 16810.91
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2623318.23 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3439422 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2442696.32
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 504166.46 | 324305.01 | 179861.44 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 248448.39 | 187128.1 | 61320.29 | 0.75 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 743496.31 | 484860.13 | 258636.18 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1302835.94 | 845116.68 | 457719.26 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 49818.25 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9690.83 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16366.83 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 13167.38 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 33431.89 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45552.88 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16032.64 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16032.64 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 177741.31 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25931.22 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30057.79 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10071.14 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 47068.81 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 119881.16 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76093.12 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76093.12 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45396.09 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26600.45 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27217.16 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 39115.9 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40079.97 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 200399.83 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40079.97 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 160329.94 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31997.05 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5902.92 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3076.53 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 25931.94 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5732.95 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4652.55 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10021.08 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10021.08 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58127.94 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58127.94 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10021.08 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10021.08 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9333.64 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9294.71 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 67542.99 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67274.53 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8943.3 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8911.31 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42086.12 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 105215.31 | -
CAV_1_HEATC | Coil:Heating:Water | 130182.4 | -
CAV_2_HEATC | Coil:Heating:Water | 176482.78 | -
VAV_1_HEATC | Coil:Heating:Water | 179742.39 | -
VAV_2_HEATC | Coil:Heating:Water | 330681.04 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.76 | 26697.55 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.1 | 20503.12 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 24.29 | 40886.48 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 41.85 | 69328.47 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24039.08 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18938.92 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 34475.25 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 688584.1178 | 1156.5585 | 3189.2261 | 0 | 0.0098 | 734069.8028 | 289139.7678
February | 612947.3124 | 1037.5006 | 2886.7652 | 0 | 0.0089 | 664464.0899 | 258142.7768
March | 673589.2629 | 1151.1881 | 3238.5635 | 0 | 0.0099 | 745456.2679 | 284737.905
April | 625358.2106 | 1074.5786 | 3041.5562 | 0 | 0.0093 | 700117.5057 | 264906.1651
May | 662748.241 | 1148.1981 | 3279.585 | 0 | 0.01 | 754921.5987 | 281640.7843
June | 683554.2137 | 1194.4622 | 3443.7976 | 0 | 0.0105 | 792736.0655 | 291459.4314
July | 714895.5833 | 1252.7211 | 3622.6321 | 0 | 0.011 | 833907.3533 | 305156.9058
August | 733599.6547 | 1285.4862 | 3717.3505 | 0 | 0.0113 | 855710.9086 | 313139.8488
September | 658224.9205 | 1144.9707 | 3284.8324 | 0 | 0.01 | 756136.1104 | 280159.2472
October | 653316.3834 | 1125.9838 | 3197.7 | 0 | 0.0098 | 736064.2205 | 277071.036
November | 630709.9383 | 1077.9271 | 3032.5309 | 0 | 0.0093 | 698031.4765 | 266614.106
December | 671815.5118 | 1133.321 | 3141.0993 | 0 | 0.0097 | 722999.9128 | 282569.6564
Annual Sum or Average | 8009340 | 13782.8959 | 39075.6388 | 0 | 0.1196 | 8994620 | 3394740
Minimum of Months | 612947.3124 | 1037.5006 | 2886.7652 | 0 | 0.0089 | 664464.0899 | 258142.7768
Maximum of Months | 733599.6547 | 1285.4862 | 3717.3505 | 0 | 0.0113 | 855710.9086 | 313139.8488
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1703350000000 | 977736.526 | 26-JAN-16:00 | 242482.867 | 310109.712 | 69105.54 | 0 | 133.236 | 3239 | 35108.644 | 0 | 162962.637 | 0 | 0 | 0 | 4921.214 | 0 | 0
February | 1541840000000 | 962037.409 | 08-FEB-11:45 | 242482.867 | 310109.712 | 68171.417 | 0 | 6042.163 | 0 | 35754.889 | 0 | 162962.637 | 0 | 0 | 0 | 8611.835 | 0 | 0
March | 1729780000000 | 991981.195 | 31-MAR-16:00 | 242482.867 | 310109.712 | 71920.838 | 0 | 101090.365 | 0 | 41327.316 | 32060.389 | 162962.637 | 0 | 0 | 0 | 5977.135 | 0 | 0
April | 1624570000000 | 1032067.91 | 27-APR-16:00 | 242482.867 | 310109.712 | 73402.812 | 0 | 75840.584 | 0 | 40356.222 | 32060.389 | 162962.637 | 0 | 0 | 0 | 5742.298 | 0 | 0
May | 1751740000000 | 1081024.257 | 30-MAY-16:00 | 242482.867 | 310109.712 | 69750.841 | 0 | 210715.953 | 0 | 46486.607 | 32060.389 | 162962.637 | 0 | 0 | 0 | 6455.25 | 0 | 0
June | 1839480000000 | 1185185.001 | 08-JUN-12:00 | 242482.867 | 302612.437 | 79576.35 | 0 | 308082.57 | 0 | 49846.257 | 32060.389 | 162962.637 | 0 | 0 | 0 | 7561.494 | 0 | 0
July | 1935020000000 | 1178531.917 | 14-JUL-10:45 | 242482.867 | 310109.712 | 81356.886 | 0 | 288359.622 | 0 | 49366.166 | 32060.389 | 162962.637 | 0 | 0 | 0 | 11833.638 | 0 | 0
August | 1985610000000 | 1230812.795 | 04-AUG-15:00 | 242482.867 | 310109.712 | 86106.082 | 0 | 339273.315 | 0 | 51180.742 | 32060.389 | 162962.637 | 0 | 0 | 0 | 6637.05 | 0 | 0
September | 1754560000000 | 1088083.699 | 06-SEP-16:00 | 242482.867 | 310109.712 | 77569.84 | 0 | 209207.334 | 0 | 47303.453 | 32060.389 | 162962.637 | 0 | 0 | 0 | 6387.467 | 0 | 0
October | 1707980000000 | 1046809.685 | 31-OCT-09:00 | 242482.867 | 310109.712 | 68877.965 | 0 | 177276.142 | 0 | 46164.281 | 32060.389 | 162962.637 | 0 | 0 | 0 | 6875.692 | 0 | 0
November | 1619730000000 | 1055409.522 | 02-NOV-09:15 | 242482.867 | 310109.712 | 69393.034 | 0 | 184957.017 | 0 | 46646.169 | 32060.389 | 162962.637 | 0 | 0 | 0 | 6797.697 | 0 | 0
December | 1677670000000 | 960654.053 | 05-DEC-16:00 | 242482.867 | 310109.712 | 68489.962 | 0 | 13035.737 | 3239 | 36286.88 | 0 | 162962.637 | 0 | 0 | 0 | 4964.322 | 0 | 0
Annual Sum or Average | 20871300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1541840000000 | 960654.053 |  | 242482.867 | 302612.437 | 68171.417 | 0 | 133.236 | 0 | 35108.644 | 0 | 162962.637 | 0 | 0 | 0 | 4921.214 | 0 | 0
Maximum of Months | 1985610000000 | 1230812.795 |  | 242482.867 | 310109.712 | 86106.082 | 0 | 339273.315 | 3239 | 51180.742 | 32060.389 | 162962.637 | 0 | 0 | 0 | 11833.638 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 569027.46 | 150051.94 | 0 | 719079.4
Cost per Total Building Area ($/m2) | 25.38 | 6.69 | 0 | 32.07
Cost per Net Conditioned Building Area ($/m2) | 25.38 | 6.69 | 0 | 32.07

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 33143.02 | 1478.13 | 1478.13
Net Site Energy | 33143.02 | 1478.13 | 1478.13
Total Source Energy | 81321.14 | 3626.81 | 3626.81
Net Source Energy | 81321.14 | 3626.81 | 3626.81
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10749.22 | 0 | 0 | 0 | 0
Cooling | 1367.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2189.93 | 0 | 0 | 0 | 0 | 0
Pumps | 880.28 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 469.38 | 0 | 0 | 0 | 0 | 12108.36
Humidification | 1940.69 | 0 | 0 | 0 | 0 | 721.94
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 761.82 | 0 | 0 | 0 | 4037.61
Refrigeration | 180.37 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20273.57 | 12869.45 | 0 | 0 | 0 | 16867.9
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1848414.3 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 2950173.1 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1721146.43
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 408131.25 | 247639.75 | 160491.5 | 0.61 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 181129.35 | 135702.1 | 45427.26 | 0.75 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 632220.77 | 389021.43 | 243199.34 | 0.62 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1100246.37 | 670941.84 | 429304.53 | 0.61 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 39713.72 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9111.57 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13750.47 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 11517.94 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30287.85 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44175.96 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13469.71 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13469.71 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 149328.08 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25951.97 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25252.84 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8709.38 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 43473.83 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 123892.14 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 63929.09 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63929.09 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41737.31 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26586.58 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27202.45 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 36629.05 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33672.9 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 168364.48 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33672.9 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 134700.04 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29997.33 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5109.61 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2462.54 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 23866.01 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4957.94 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 3780.07 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8419.14 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8419.14 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 48835.77 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 48835.77 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8419.14 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8419.14 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7897.98 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 7857.11 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61630.68 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61332.53 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7565.46 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 7525.61 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35358.35 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88395.89 | -
CAV_1_HEATC | Coil:Heating:Water | 114857.35 | -
CAV_2_HEATC | Coil:Heating:Water | 153551.15 | -
VAV_1_HEATC | Coil:Heating:Water | 147240.09 | -
VAV_2_HEATC | Coil:Heating:Water | 272675.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.04 | 27183.63 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.11 | 20520.9 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 25.82 | 43471.97 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 43.85 | 72649 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16938.16 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16244.91 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 24291.58 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 533696.8268 | 870.9199 | 2094.0989 | 0 | 0.0083 | 2177130 | 222622.7958
February | 473304.4085 | 776.6841 | 1880.4957 | 0 | 0.0075 | 1955090 | 197854.4855
March | 529275.1597 | 875.3669 | 2139.8731 | 0 | 0.0085 | 2224800 | 221922.3457
April | 490908.883 | 816.413 | 2009.1135 | 0 | 0.0079 | 2088880 | 206276.9649
May | 498940.3257 | 832.758 | 2058.1571 | 0 | 0.0081 | 2139900 | 209944.8434
June | 481721.2316 | 808.1708 | 2009.6021 | 0 | 0.0079 | 2089440 | 203106.6715
July | 500449.1069 | 843.6692 | 2109.8078 | 0 | 0.0083 | 2193660 | 211402.9688
August | 505880.6742 | 851.9879 | 2128.1705 | 0 | 0.0084 | 2212740 | 213615.2058
September | 482064.9309 | 807.869 | 2006.2814 | 0 | 0.0079 | 2085980 | 203165.4195
October | 504500.8215 | 840.1016 | 2070.6092 | 0 | 0.0082 | 2152830 | 212094.5754
November | 499699.3602 | 824.2619 | 2008.4457 | 0 | 0.0079 | 2088140 | 209306.5801
December | 530388.2154 | 865.4312 | 2080.6322 | 0 | 0.0083 | 2163130 | 221233.8825
Annual Sum or Average | 6030830 | 10013.6334 | 24595.2871 | 0 | 0.0972 | 25571700 | 2532550
Minimum of Months | 473304.4085 | 776.6841 | 1880.4957 | 0 | 0.0075 | 1955090 | 197854.4855
Maximum of Months | 533696.8268 | 875.3669 | 2139.8731 | 0 | 0.0085 | 2224800 | 222622.7958
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1726050000000 | 1015078.996 | 24-JAN-16:15 | 242482.867 | 310109.712 | 72982.498 | 0 | 56435.272 | 0 | 29429.446 | 22590.047 | 162962.637 | 0 | 0 | 0 | 5548.741 | 0 | 0
February | 1550020000000 | 1003655.349 | 07-FEB-14:00 | 242482.867 | 302612.437 | 73291.333 | 0 | 52420.225 | 0 | 29312.72 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6375.687 | 0 | 0
March | 1763850000000 | 1072599.253 | 30-MAR-15:15 | 242482.867 | 310109.712 | 78168.854 | 0 | 81046.205 | 0 | 31265.243 | 22590.047 | 162962.637 | 0 | 0 | 0 | 5919.207 | 0 | 0
April | 1656090000000 | 1033884.56 | 27-APR-12:00 | 242482.867 | 302612.437 | 77416.9 | 0 | 72837.742 | 0 | 30723.607 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6669.167 | 0 | 0
May | 1696540000000 | 1057400.218 | 19-MAY-16:00 | 242482.867 | 310109.712 | 81410.858 | 0 | 86883.343 | 0 | 31490.072 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6045.39 | 0 | 0
June | 1656540000000 | 1101632.881 | 15-JUN-16:00 | 242482.867 | 310109.712 | 88313.503 | 0 | 103030.978 | 0 | 32457.452 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6264.432 | 0 | 0
July | 1739160000000 | 1064088.459 | 12-JUL-15:00 | 242482.867 | 310109.712 | 91103.589 | 0 | 128272.973 | 0 | 33288.522 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6556.797 | 0 | 0
August | 1754290000000 | 1069609.31 | 29-AUG-15:00 | 242482.867 | 310109.712 | 92858.378 | 0 | 134283.37 | 0 | 33671.677 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6630.697 | 0 | 0
September | 1653790000000 | 1091642.595 | 13-SEP-15:00 | 242482.867 | 310109.712 | 84052.119 | 0 | 103228.143 | 0 | 32341.473 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6264.981 | 0 | 0
October | 1706790000000 | 1063675.872 | 05-OCT-15:00 | 242482.867 | 310109.712 | 83426.375 | 0 | 105424.533 | 0 | 32285.536 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6280.519 | 0 | 0
November | 1655500000000 | 1036781.759 | 10-NOV-13:00 | 242482.867 | 302612.437 | 74775.766 | 0 | 76777.001 | 0 | 30908.543 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6704.628 | 0 | 0
December | 1714950000000 | 1001049.038 | 29-DEC-14:00 | 242482.867 | 302612.437 | 73341.13 | 0 | 47600.833 | 0 | 29018.168 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6313.991 | 0 | 0
Annual Sum or Average | 20273600000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1550020000000 | 1001049.038 |  | 242482.867 | 302612.437 | 72982.498 | 0 | 47600.833 | 0 | 29018.168 | 22590.047 | 162962.637 | 0 | 0 | 0 | 5548.741 | 0 | 0
Maximum of Months | 1763850000000 | 1101632.881 |  | 242482.867 | 310109.712 | 92858.378 | 0 | 134283.37 | 0 | 33671.677 | 22590.047 | 162962.637 | 0 | 0 | 0 | 6704.628 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 208152.97 | 92429.26 | 0 | 300582.23
Cost per Total Building Area ($/m2) | 9.28 | 4.12 | 0 | 13.41
Cost per Net Conditioned Building Area ($/m2) | 9.28 | 4.12 | 0 | 13.41

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 38903.06 | 1735.02 | 1735.02
Net Site Energy | 38903.06 | 1735.02 | 1735.02
Total Source Energy | 91151.21 | 4065.21 | 4065.21
Net Source Energy | 91151.21 | 4065.21 | 4065.21
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15972.94 | 0 | 0 | 0 | 0
Cooling | 1922.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.87 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2118.18 | 0 | 0 | 0 | 0 | 0
Pumps | 1128.74 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 580.23 | 0 | 0 | 0 | 0 | 10930.18
Humidification | 1579.23 | 0 | 0 | 0 | 0 | 587.47
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 817.31 | 0 | 0 | 0 | 4037.61
Refrigeration | 180.69 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20754.4 | 18148.67 | 0 | 0 | 0 | 15555.26
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2526393.67 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3541080.06 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2352445.26
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 498855.55 | 317550.45 | 181305.1 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 241464.7 | 180946.63 | 60518.07 | 0.75 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 734749.42 | 473882.58 | 260866.83 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1284914.35 | 824553.09 | 460361.26 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 48250.05 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9520.5 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16240.97 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12585.28 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 32608.5 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45411.32 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15909.35 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15909.35 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 176374.49 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25932.41 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29826.65 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9814.37 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 46240.76 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 119751.76 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 75507.97 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 75507.97 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44549.33 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26592.38 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27209.44 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37994.02 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39771.75 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198858.77 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39771.75 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 159097.01 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32311.85 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5748.88 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3225.25 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 25230.52 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5535.76 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4481.27 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9944.02 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9944.02 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 57680.94 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 57680.94 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9944.02 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9944.02 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9160.8 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9121.63 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 66080.4 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 65810.86 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8677.44 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8645.89 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41762.48 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 104406.21 | -
CAV_1_HEATC | Coil:Heating:Water | 149689.05 | -
CAV_2_HEATC | Coil:Heating:Water | 183839.71 | -
VAV_1_HEATC | Coil:Heating:Water | 196939.57 | -
VAV_2_HEATC | Coil:Heating:Water | 361671.24 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.71 | 26613.46 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.09 | 20482.96 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 24.16 | 40663.13 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 41.56 | 68849.48 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23150.9 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19498.69 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 33201.48 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 508721.1087 | 805.095 | 1120.2706 | 0 | 0.0084 | 735950.2069 | 208886.6451
February | 444148.336 | 716.6446 | 1022.8177 | 0 | 0.0077 | 671998.3964 | 183685.8477
March | 466375.6823 | 771.6896 | 1136.4599 | 0 | 0.0085 | 746753.9527 | 194711.7992
April | 429026.1941 | 719.817 | 1077.7736 | 0 | 0.008 | 708236.8215 | 180067.3583
May | 447734.4233 | 760.1141 | 1153.7789 | 0 | 0.0085 | 758221.2905 | 188770.9613
June | 452835.6429 | 776.6351 | 1192.52 | 0 | 0.0088 | 783714.1244 | 191673.0791
July | 471579.0748 | 811.5443 | 1250.8779 | 0 | 0.0092 | 822078.043 | 199870.8101
August | 482724.036 | 831.0619 | 1281.5412 | 0 | 0.0095 | 842231.3847 | 204626.7319
September | 428460.724 | 727.1406 | 1103.289 | 0 | 0.0082 | 725040.0548 | 180620.7449
October | 437779.9963 | 733.843 | 1097.6116 | 0 | 0.0081 | 721270.0698 | 183678.2371
November | 437374.1088 | 722.0452 | 1060.3939 | 0 | 0.0079 | 696764.4196 | 182445.265
December | 488150.146 | 784.5606 | 1114.1129 | 0 | 0.0084 | 731965.2297 | 201589.0229
Annual Sum or Average | 5494910 | 9160.191 | 13611.4471 | 0 | 0.1012 | 8944220 | 2300630
Minimum of Months | 428460.724 | 716.6446 | 1022.8177 | 0 | 0.0077 | 671998.3964 | 180067.3583
Maximum of Months | 508721.1087 | 831.0619 | 1281.5412 | 0 | 0.0095 | 842231.3847 | 208886.6451
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1707720000000 | 968580.803 | 03-JAN-17:00 | 242482.867 | 310109.712 | 67035.446 | 0 | 873.604 | 3239 | 33949.879 | 0 | 162962.637 | 0 | 0 | 0 | 4928.579 | 0 | 0
February | 1559320000000 | 970195.765 | 08-FEB-17:00 | 242482.867 | 310109.712 | 68930.167 | 0 | 466.706 | 3239 | 33861.704 | 0 | 162962.637 | 0 | 0 | 0 | 4926.203 | 0 | 0
March | 1732790000000 | 994063.188 | 31-MAR-15:00 | 242482.867 | 310109.712 | 70673.053 | 0 | 37349.444 | 0 | 37138.173 | 30875.844 | 162962.637 | 0 | 0 | 0 | 5406.348 | 0 | 0
April | 1643410000000 | 996630.664 | 06-APR-16:00 | 242482.867 | 310109.712 | 72430.986 | 0 | 78920.137 | 0 | 39238.242 | 30875.844 | 162962.637 | 0 | 0 | 0 | 5796.677 | 0 | 0
May | 1759400000000 | 1051761.384 | 31-MAY-16:00 | 242482.867 | 310109.712 | 75134.048 | 0 | 178861.607 | 0 | 45140.576 | 30875.844 | 162962.637 | 0 | 0 | 0 | 6194.092 | 0 | 0
June | 1818550000000 | 1156078.46 | 29-JUN-16:00 | 242482.867 | 310109.712 | 86431.667 | 0 | 268623.556 | 0 | 47875.025 | 30875.844 | 162962.637 | 0 | 0 | 0 | 6717.151 | 0 | 0
July | 1907570000000 | 1196197.717 | 13-JUL-16:00 | 242482.867 | 310109.712 | 84677.937 | 0 | 309360.296 | 0 | 49087.759 | 30875.844 | 162962.637 | 0 | 0 | 0 | 6640.665 | 0 | 0
August | 1954330000000 | 1186955.436 | 25-AUG-16:00 | 242482.867 | 310109.712 | 85986.551 | 0 | 298936.793 | 0 | 48959.619 | 30875.844 | 162962.637 | 0 | 0 | 0 | 6641.412 | 0 | 0
September | 1682400000000 | 1070167.832 | 22-SEP-12:45 | 242482.867 | 302612.437 | 72303.902 | 0 | 205751.65 | 0 | 46256.85 | 30875.844 | 162962.637 | 0 | 0 | 0 | 6921.646 | 0 | 0
October | 1673650000000 | 979849.02 | 19-OCT-15:15 | 242482.867 | 310109.712 | 71251.77 | 0 | 39373.632 | 0 | 37202.537 | 30875.844 | 162962.637 | 0 | 0 | 0 | 5385.428 | 0 | 0
November | 1616790000000 | 996666.116 | 01-NOV-15:15 | 242482.867 | 310109.712 | 70099.382 | 0 | 66594.488 | 0 | 38531.849 | 30875.844 | 162962.637 | 0 | 0 | 0 | 5548.665 | 0 | 0
December | 1698470000000 | 970589.76 | 20-DEC-16:30 | 242482.867 | 310109.712 | 68780.899 | 0 | 104.624 | 3239 | 33812.398 | 0 | 162962.637 | 0 | 0 | 0 | 4910.953 | 0 | 0
Annual Sum or Average | 20754400000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1559320000000 | 968580.803 |  | 242482.867 | 302612.437 | 67035.446 | 0 | 104.624 | 0 | 33812.398 | 0 | 162962.637 | 0 | 0 | 0 | 4910.953 | 0 | 0
Maximum of Months | 1954330000000 | 1196197.717 |  | 242482.867 | 310109.712 | 86431.667 | 0 | 309360.296 | 3239 | 49087.759 | 30875.844 | 162962.637 | 0 | 0 | 0 | 6921.646 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 297797.36 | 144764.72 | 0 | 442562.08
Cost per Total Building Area ($/m2) | 13.28 | 6.46 | 0 | 19.74
Cost per Net Conditioned Building Area ($/m2) | 13.28 | 6.46 | 0 | 19.74

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 34921.31 | 1557.44 | 1557.44
Net Site Energy | 34921.31 | 1557.44 | 1557.44
Total Source Energy | 85502.29 | 3813.28 | 3813.28
Net Source Energy | 85502.29 | 3813.28 | 3813.28
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12866.87 | 0 | 0 | 0 | 0
Cooling | 1100.98 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2141.81 | 0 | 0 | 0 | 0 | 0
Pumps | 809.04 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 412.29 | 0 | 0 | 0 | 0 | 9177.05
Humidification | 1982.27 | 0 | 0 | 0 | 0 | 737.4
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 826.81 | 0 | 0 | 0 | 4037.61
Refrigeration | 177.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19869.22 | 15052.1 | 0 | 0 | 0 | 13952.07
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1777652.29 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3226944.39 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1655256.56
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 400797.95 | 253585.4 | 147212.55 | 0.63 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 169182.06 | 134329.12 | 34852.94 | 0.79 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 608128.81 | 388292.18 | 219836.63 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1079640 | 683956.32 | 395683.69 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 37419.34 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8644.93 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14519.34 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 11841.64 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30986.17 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44349.05 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14222.87 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14222.87 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 157677.82 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25945.82 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26664.86 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8815.51 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 43687.25 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 113122.25 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 67503.7 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67503.7 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41905.86 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26581.75 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27198.89 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 36758.67 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35555.73 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 177778.65 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35555.73 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 142231.85 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31426.32 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5287.42 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2979.04 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 23903.77 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5009.3 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 3999.76 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8889.9 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8889.9 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 51566.45 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 51566.45 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8889.9 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8889.9 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8276.58 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8239.3 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61947.59 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61681.27 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 7665.4 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 7630.62 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 37335.43 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 93338.58 | -
CAV_1_HEATC | Coil:Heating:Water | 137908.97 | -
CAV_2_HEATC | Coil:Heating:Water | 165153.73 | -
VAV_1_HEATC | Coil:Heating:Water | 182080.27 | -
VAV_2_HEATC | Coil:Heating:Water | 333864.23 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.87 | 26887.6 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.09 | 20484.67 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 24.69 | 41564.1 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 42.9 | 71077.03 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16289.72 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17768.93 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 23361.64 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 503023.2726 | 803.8809 | 1258.2412 | 0 | 0.0089 | 29837200 | 207666.8808
February | 441340.3923 | 711.3709 | 1125.8857 | 0 | 0.008 | 26699600 | 182788.1761
March | 483451.2931 | 796.9241 | 1297.242 | 0 | 0.0091 | 30766300 | 201937.805
April | 445182.9407 | 738.1115 | 1209.9964 | 0 | 0.0085 | 28697800 | 186365.7773
May | 447748.5959 | 746.7471 | 1232.8164 | 0 | 0.0087 | 29239800 | 187863.3876
June | 435849.5359 | 732.1777 | 1219.1332 | 0 | 0.0085 | 28916100 | 183380.8206
July | 440427.323 | 743.2747 | 1244.2588 | 0 | 0.0087 | 29512600 | 185636.2114
August | 447072.5006 | 753.7763 | 1260.454 | 0 | 0.0088 | 29896600 | 188368.1841
September | 427050.3615 | 714.9911 | 1185.8232 | 0 | 0.0083 | 28125600 | 179446.1557
October | 456975.3125 | 758.7833 | 1246.0987 | 0 | 0.0088 | 29554200 | 191410.6612
November | 454858.3231 | 747.2568 | 1211.3528 | 0 | 0.0085 | 28728900 | 189749.5203
December | 492356.3946 | 791.8584 | 1249.7297 | 0 | 0.0089 | 29636200 | 203748.8572
Annual Sum or Average | 5475340 | 9039.1529 | 14741.0321 | 0 | 0.1038 | 349611000 | 2288360
Minimum of Months | 427050.3615 | 711.3709 | 1125.8857 | 0 | 0.008 | 26699600 | 179446.1557
Maximum of Months | 503023.2726 | 803.8809 | 1297.242 | 0 | 0.0091 | 30766300 | 207666.8808
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1695720000000 | 955373.374 | 10-JAN-17:00 | 242482.867 | 310109.712 | 69498.009 | 0 | 11311.089 | 3239 | 25111.073 | 319.693 | 162962.637 | 0 | 0 | 0 | 5008.539 | 0 | 0
February | 1517400000000 | 985282.189 | 03-FEB-17:30 | 242482.867 | 310109.712 | 72759.711 | 0 | 38296.218 | 3239 | 27157.082 | 21725.242 | 162962.637 | 0 | 0 | 0 | 5452.553 | 0 | 0
March | 1748520000000 | 1018292.239 | 29-MAR-16:00 | 242482.867 | 310109.712 | 75638.729 | 0 | 73220.123 | 0 | 29895.044 | 21725.242 | 162962.637 | 0 | 0 | 0 | 5873.268 | 0 | 0
April | 1630970000000 | 1019975.19 | 06-APR-16:00 | 242482.867 | 310109.712 | 75415.332 | 0 | 76312.156 | 0 | 30021.666 | 21725.242 | 162962.637 | 0 | 0 | 0 | 5904.266 | 0 | 0
May | 1661770000000 | 1026490.235 | 04-MAY-16:00 | 242482.867 | 310109.712 | 80430.685 | 0 | 90543.25 | 0 | 30859.704 | 21725.242 | 162962.637 | 0 | 0 | 0 | 6138.415 | 0 | 0
June | 1643370000000 | 1053644.831 | 30-JUN-15:00 | 242482.867 | 310109.712 | 84895.579 | 0 | 149247.661 | 0 | 32905.62 | 21725.242 | 162962.637 | 0 | 0 | 0 | 6792.109 | 0 | 0
July | 1677270000000 | 1058722.544 | 21-JUL-16:00 | 242482.867 | 310109.712 | 92486.507 | 0 | 146077.826 | 0 | 33368.69 | 21725.242 | 162962.637 | 0 | 0 | 0 | 6770.434 | 0 | 0
August | 1699090000000 | 1049201.399 | 18-AUG-16:00 | 242482.867 | 310109.712 | 88702.117 | 0 | 126960.465 | 0 | 32435.58 | 21725.242 | 162962.637 | 0 | 0 | 0 | 6573.251 | 0 | 0
September | 1598450000000 | 1004107.541 | 01-SEP-16:00 | 242482.867 | 310109.712 | 84777.76 | 0 | 126350.881 | 0 | 32254.801 | 21725.242 | 162962.637 | 0 | 0 | 0 | 6569.021 | 0 | 0
October | 1679640000000 | 1017197.749 | 19-OCT-16:00 | 242482.867 | 310109.712 | 73566.494 | 0 | 73353.365 | 0 | 29757.659 | 21725.242 | 162962.637 | 0 | 0 | 0 | 5854.244 | 0 | 0
November | 1632730000000 | 978009.065 | 21-NOV-11:45 | 242482.867 | 310109.712 | 69088.771 | 0 | 48594.768 | 0 | 28014.243 | 21725.242 | 162962.637 | 0 | 0 | 0 | 9518.52 | 0 | 0
December | 1684300000000 | 961510.162 | 12-DEC-16:45 | 242482.867 | 310109.712 | 68467.058 | 0 | 426.539 | 3239 | 24041.483 | 0 | 162962.637 | 0 | 0 | 0 | 4912.774 | 0 | 0
Annual Sum or Average | 19869200000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1517400000000 | 955373.374 |  | 242482.867 | 310109.712 | 68467.058 | 0 | 426.539 | 0 | 24041.483 | 0 | 162962.637 | 0 | 0 | 0 | 4912.774 | 0 | 0
Maximum of Months | 1748520000000 | 1058722.544 |  | 242482.867 | 310109.712 | 92486.507 | 0 | 149247.661 | 3239 | 33368.69 | 21725.242 | 162962.637 | 0 | 0 | 0 | 9518.52 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 381623.74 | 130885.59 | 0 | 512509.33
Cost per Total Building Area ($/m2) | 17.02 | 5.84 | 0 | 22.86
Cost per Net Conditioned Building Area ($/m2) | 17.02 | 5.84 | 0 | 22.86

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 39577.21 | 1765.09 | 1765.09
Net Site Energy | 39577.21 | 1765.09 | 1765.09
Total Source Energy | 90459.57 | 4034.37 | 4034.37
Net Source Energy | 90459.57 | 4034.37 | 4034.37
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 17169.63 | 0 | 0 | 0 | 0
Cooling | 1191.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2136.67 | 0 | 0 | 0 | 0 | 0
Pumps | 947.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 447.88 | 0 | 0 | 0 | 0 | 7005.41
Humidification | 2001.28 | 0 | 0 | 0 | 0 | 744.47
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 903.63 | 0 | 0 | 0 | 4037.61
Refrigeration | 175.73 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20145.53 | 19431.68 | 0 | 0 | 0 | 11787.49
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.487 | 0.409 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 3.241 | 0.487 | 0.409 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 3.241 | 0.487 | 0.409 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 3.241 | 0.487 | 0.409 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 3.241 | 0.487 | 0.409 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 3.241 | 0.487 | 0.409 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 3.241 | 0.487 | 0.409 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 3.241 | 0.487 | 0.409 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.487 | 0.409 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.487 | 0.409 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 3.241 | 0.487 | 0.409 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 3.241 | 0.487 | 0.409 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 3.241 | 0.487 | 0.409 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 3.241 | 0.487 | 0.409 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 3.241 | 0.487 | 0.409 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.487 | 0.409 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.487 | 0.409 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.487 | 0.409 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.487 | 0.409 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.487 | 0.409 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.487 | 0.409 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.487 | 0.409 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 3.241 | 0.487 | 0.409 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.487 | 0.409 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 3.241 | 0.487 | 0.409 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.487 | 0.409 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.487 | 0.409 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.487 | 0.409 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 3.241 | 0.487 | 0.409 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.487 | 0.409 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 3.241 | 0.487 | 0.409 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 3.241 | 0.487 | 0.409 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 186.18 | 3.24 | 0.487 | 0.409
Non-North Total or Average |  |  | 659.24 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2238539.58 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 3555133.06 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2084410.62
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 476828.25 | 307238.25 | 169590 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 207123.24 | 163253.68 | 43869.56 | 0.79 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 667386.83 | 434651.8 | 232735.03 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1212019.8 | 786039.12 | 425980.68 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 32660.87 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8776.93 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15902.22 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12040.32 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 32209.75 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46017.99 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15577.52 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15577.52 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 172695.77 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25936.03 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29204.54 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10069.97 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49888.62 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 113227.78 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 73933.06 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 73933.06 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45407.9 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26563.45 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27181.89 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37078.96 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38942.22 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 194711.08 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38942.22 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 155778.65 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33180.73 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6035.26 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3646.85 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 26779.1 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5691.48 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4185.13 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 57883.03 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 57714.37 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9712.37 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9670.54 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 71966.68 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 71702.12 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8923.13 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8890.41 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 40891.43 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 102228.56 | -
CAV_1_HEATC | Coil:Heating:Water | 157011.55 | -
CAV_2_HEATC | Coil:Heating:Water | 185025.36 | -
VAV_1_HEATC | Coil:Heating:Water | 201438.84 | -
VAV_2_HEATC | Coil:Heating:Water | 372385 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.13 | 27325.27 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.13 | 20553.24 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 23.32 | 39253.3 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 41.82 | 69272.99 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20513.12 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19576.07 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29418.55 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 514430.8223 | 813.4778 | 1130.7168 | 0 | 0.0085 | 742809.4906 | 211168.6702
February | 455194.1445 | 725.7662 | 1019.9226 | 0 | 0.0077 | 670054.5849 | 187422.3369
March | 482644.5511 | 790.2841 | 1148.9967 | 0 | 0.0086 | 754954.0465 | 200708.3062
April | 430665.2593 | 718.259 | 1067.8635 | 0 | 0.0079 | 701705.6972 | 180343.5029
May | 436549.0331 | 735.071 | 1105.243 | 0 | 0.0082 | 726299.355 | 183476.3901
June | 422150.3305 | 718.2449 | 1092.9453 | 0 | 0.0081 | 718250.348 | 178133.9158
July | 446132.892 | 763.7879 | 1170.4675 | 0 | 0.0086 | 769215.7605 | 188706.7884
August | 445790.8507 | 761.0564 | 1162.5828 | 0 | 0.0086 | 764025.0601 | 188356.9951
September | 410758.9471 | 692.0783 | 1041.359 | 0 | 0.0077 | 684320.5134 | 172678.5326
October | 436413.3165 | 729.4281 | 1087.2693 | 0 | 0.0081 | 714464.498 | 182901.8061
November | 450137.3183 | 736.7826 | 1070.7168 | 0 | 0.008 | 703518.563 | 187163.9404
December | 497422.3936 | 793.0926 | 1114.5316 | 0 | 0.0084 | 732209.5096 | 204809.1992
Annual Sum or Average | 5428290 | 8977.329 | 13212.6148 | 0 | 0.0984 | 8681830 | 2265870
Minimum of Months | 410758.9471 | 692.0783 | 1019.9226 | 0 | 0.0077 | 670054.5849 | 172678.5326
Maximum of Months | 514430.8223 | 813.4778 | 1170.4675 | 0 | 0.0086 | 769215.7605 | 211168.6702
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1723630000000 | 971535.408 | 31-JAN-17:00 | 242482.867 | 310109.712 | 68847.186 | 0 | 227.961 | 3239 | 30057.684 | 0 | 162962.637 | 0 | 0 | 0 | 4920.991 | 0 | 0
February | 1554810000000 | 972271.391 | 15-FEB-17:45 | 242482.867 | 310109.712 | 70047.261 | 0 | 1782.847 | 3239 | 30234.482 | 0 | 162962.637 | 0 | 0 | 0 | 4925.825 | 0 | 0
March | 1751810000000 | 979676.52 | 06-MAR-17:00 | 242482.867 | 310109.712 | 67934.148 | 0 | 2478.232 | 3239 | 30296.222 | 0 | 162962.637 | 0 | 0 | 0 | 4931.724 | 0 | 0
April | 1628260000000 | 989878.804 | 27-APR-15:15 | 242482.867 | 310109.712 | 73337.064 | 0 | 40166.282 | 0 | 33456.635 | 27357.889 | 162962.637 | 0 | 0 | 0 | 5443.843 | 0 | 0
May | 1685320000000 | 1032280.017 | 12-MAY-16:00 | 242482.867 | 310109.712 | 77743.631 | 0 | 68476.55 | 0 | 35195.315 | 27357.889 | 162962.637 | 0 | 0 | 0 | 5759.277 | 0 | 0
June | 1666650000000 | 1082269.285 | 14-JUN-15:15 | 242482.867 | 310109.712 | 80138.147 | 0 | 210369.92 | 0 | 42416.701 | 27357.889 | 162962.637 | 0 | 0 | 0 | 6431.411 | 0 | 0
July | 1784910000000 | 1101553.718 | 07-JUL-16:00 | 242482.867 | 310109.712 | 87056.39 | 0 | 222000.059 | 0 | 42982.851 | 27357.889 | 162962.637 | 0 | 0 | 0 | 6601.312 | 0 | 0
August | 1772860000000 | 1096571.782 | 11-AUG-15:00 | 242482.867 | 310109.712 | 84120.508 | 0 | 220143.267 | 0 | 42858.019 | 27357.889 | 162962.637 | 0 | 0 | 0 | 6536.881 | 0 | 0
September | 1587910000000 | 1075813.343 | 08-SEP-16:00 | 242482.867 | 310109.712 | 77422.654 | 0 | 206085.495 | 0 | 43221.324 | 27357.889 | 162962.637 | 0 | 0 | 0 | 6170.764 | 0 | 0
October | 1657860000000 | 980313.201 | 25-OCT-15:15 | 242482.867 | 310109.712 | 72453.149 | 0 | 53845.821 | 0 | 34150.643 | 27357.889 | 162962.637 | 0 | 0 | 0 | 5488.26 | 0 | 0
November | 1632460000000 | 985944.99 | 03-NOV-16:00 | 242482.867 | 310109.712 | 72086.743 | 0 | 29070.596 | 3239 | 32536.674 | 27357.889 | 162962.637 | 0 | 0 | 0 | 5366.654 | 0 | 0
December | 1699040000000 | 964098.592 | 13-DEC-14:00 | 242482.867 | 302612.437 | 69689.283 | 0 | 239.989 | 0 | 30030.938 | 0 | 162962.637 | 0 | 0 | 0 | 5780.246 | 0 | 0
Annual Sum or Average | 20145500000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1554810000000 | 964098.592 |  | 242482.867 | 302612.437 | 67934.148 | 0 | 227.961 | 0 | 30030.938 | 0 | 162962.637 | 0 | 0 | 0 | 4920.991 | 0 | 0
Maximum of Months | 1784910000000 | 1101553.718 |  | 242482.867 | 310109.712 | 87056.39 | 0 | 222000.059 | 3239 | 43221.324 | 27357.889 | 162962.637 | 0 | 0 | 0 | 6601.312 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 289359.07 | 154880.23 | 0 | 444239.3
Cost per Total Building Area ($/m2) | 12.91 | 6.91 | 0 | 19.81
Cost per Net Conditioned Building Area ($/m2) | 12.91 | 6.91 | 0 | 19.81

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 47189.29 | 2104.58 | 2104.58
Net Site Energy | 47189.29 | 2104.58 | 2104.58
Total Source Energy | 102100.88 | 4553.55 | 4553.55
Net Source Energy | 102100.88 | 4553.55 | 4553.55
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 24431.56 | 0 | 0 | 0 | 0
Cooling | 816.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4152.95 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 50.5 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2319.53 | 0 | 0 | 0 | 0 | 0
Pumps | 649.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 304.84 | 0 | 0 | 0 | 0 | 5215.67
Humidification | 2884.25 | 0 | 0 | 0 | 0 | 1072.94
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1008.11 | 0 | 0 | 0 | 4037.61
Refrigeration | 172.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20391.2 | 26798.09 | 0 | 0 | 0 | 10326.22
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 11.84 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 10.76 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 10.76 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 9.68 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 29.05 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 12.05 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 29.05 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 29.05 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 8.61 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 10.76 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 8.61 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 8.61 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 12.91 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 15.06 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.82 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 12.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 12.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 23.67 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 23.67 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 23.67 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 23.67 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 12.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 11.84 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 11.84 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 11.84 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 7.53 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 9.68 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 4.3 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 12.016 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 2.615 | 0.702 | 0.633 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 30.42 | 30.42 | 2.615 | 0.702 | 0.633 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 25.03 | 25.03 | 2.615 | 0.702 | 0.633 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 24.53 | 2.615 | 0.702 | 0.633 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 6.54 | 6.54 | 2.615 | 0.702 | 0.633 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 4.91 | 29.43 | 2.615 | 0.702 | 0.633 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-90.1-2004-NONRES-FIXED | 62.63 | 62.63 | 2.615 | 0.702 | 0.633 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 35.76 | 35.76 | 2.615 | 0.702 | 0.633 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 2.615 | 0.702 | 0.633 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 2.615 | 0.702 | 0.633 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 11.86 | 2.615 | 0.702 | 0.633 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 40.87 | 2.615 | 0.702 | 0.633 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 9.81 | 9.81 | 2.615 | 0.702 | 0.633 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 8.17 | 8.17 | 2.615 | 0.702 | 0.633 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 17.77 | 2.615 | 0.702 | 0.633 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 2.615 | 0.702 | 0.633 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 2.615 | 0.702 | 0.633 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 2.615 | 0.702 | 0.633 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 2.615 | 0.702 | 0.633 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 2.615 | 0.702 | 0.633 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 2.615 | 0.702 | 0.633 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 2.615 | 0.702 | 0.633 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 8.17 | 8.17 | 2.615 | 0.702 | 0.633 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 2.615 | 0.702 | 0.633 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 49.05 | 2.615 | 0.702 | 0.633 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 2.615 | 0.702 | 0.633 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 2.615 | 0.702 | 0.633 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 2.615 | 0.702 | 0.633 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.74 | 47.41 | 2.615 | 0.702 | 0.633 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 2.615 | 0.702 | 0.633 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-90.1-2004-RES-FIXED | 6.54 | 6.54 | 2.615 | 0.702 | 0.633 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-RES-FIXED | 4.91 | 4.91 | 2.615 | 0.702 | 0.633 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 186.18 | 2.61 | 0.702 | 0.633
Non-North Total or Average |  |  | 659.24 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1839029.81 | 6.1
HEATSYS1 BOILER | Boiler:HotWater | 4123194.61 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1712408.09
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 470494.28 | 322263.24 | 148231.04 | 0.68 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 178169.44 | 150915.64 | 27253.81 | 0.85 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 596115.87 | 408885.94 | 187229.94 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1081137.89 | 736740.45 | 344397.43 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 17126.25 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9082.07 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16468.09 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 11110.04 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37774.01 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49133.18 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16131.83 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16131.83 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 178840.95 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25930.04 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30243.75 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11737.74 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 59986.81 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 119382.3 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76563.89 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76563.89 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49830.48 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26552.12 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 27171.8 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 32490.14 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40327.93 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 201639.66 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40327.93 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 161321.86 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40807.57 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8052.48 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6596.1 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 29116.03 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6228.12 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4497.22 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 86755.52 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 86595.18 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16532.56 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16494.95 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 78041.42 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77881.2 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10083.08 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10083.08 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60487.5 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60487.5 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14815.7 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14781.3 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 88515.69 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88349.63 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10593.46 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10570.09 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42346.5 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 105866.25 | -
CAV_1_HEATC | Coil:Heating:Water | 178227.66 | -
CAV_2_HEATC | Coil:Heating:Water | 218137.89 | -
VAV_1_HEATC | Coil:Heating:Water | 250880.13 | -
VAV_2_HEATC | Coil:Heating:Water | 460898.39 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.03 | 30344.71 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.47 | 21130.86 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 22.93 | 38601.72 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 40.82 | 67625.36 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16852.16 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22704.06 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 24168.25 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 548242.2557 | 614.8801 | 2453.6772 | 0 | 0.0087 | 492255.3318 | 207783.6041
February | 487156.518 | 549.9171 | 2254.5048 | 0 | 0.008 | 452314.5986 | 185178.0545
March | 490706.8783 | 566.9747 | 2543.9535 | 0 | 0.0089 | 510446.7933 | 188535.8197
April | 428109.8081 | 504.9938 | 2435.8692 | 0 | 0.0084 | 488802.6891 | 166077.2328
May | 416829.9612 | 497.7173 | 2497.8232 | 0 | 0.0086 | 501257.8407 | 162629.2157
June | 388977.0465 | 466.0429 | 2364.0452 | 0 | 0.0081 | 474417.2543 | 152005.8788
July | 390731.9677 | 467.7179 | 2365.7645 | 0 | 0.0081 | 474760.7773 | 152625.8681
August | 395945.6293 | 472.5539 | 2367.9398 | 0 | 0.0081 | 475192.2926 | 154446.21
September | 385843.9681 | 457.2215 | 2238.9843 | 0 | 0.0077 | 449301.9787 | 150001.6915
October | 440910.9774 | 516.4796 | 2433.089 | 0 | 0.0084 | 488231.0783 | 170487.0064
November | 487442.2045 | 557.5056 | 2407.8403 | 0 | 0.0085 | 483111.7805 | 186404.7934
December | 527879.9714 | 597.5062 | 2476.845 | 0 | 0.0088 | 496929.617 | 200907.0458
Annual Sum or Average | 5388780 | 6269.5107 | 28840.3361 | 0 | 0.1004 | 5787020 | 2077080
Minimum of Months | 385843.9681 | 457.2215 | 2238.9843 | 0 | 0.0077 | 449301.9787 | 150001.6915
Maximum of Months | 548242.2557 | 614.8801 | 2543.9535 | 0 | 0.0089 | 510446.7933 | 207783.6041
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1734510000000 | 983697.889 | 25-JAN-16:15 | 242482.867 | 310109.712 | 75149.174 | 0 | 50.964 | 3239 | 24839.876 | 0 | 162962.637 | 0 | 0 | 0 | 4908.413 | 0 | 0
February | 1593780000000 | 986692.469 | 17-FEB-17:45 | 242482.867 | 310109.712 | 76395.684 | 0 | 222.852 | 3239 | 24825.987 | 0 | 162962.637 | 0 | 0 | 0 | 4926.013 | 0 | 0
March | 1798610000000 | 988494.051 | 22-MAR-15:15 | 242482.867 | 310109.712 | 78663.51 | 0 | 2440.001 | 0 | 24997.738 | 0 | 162962.637 | 0 | 0 | 0 | 4907.105 | 0 | 0
April | 1722350000000 | 995332.064 | 21-APR-16:00 | 242482.867 | 310109.712 | 82919.083 | 0 | 27821.111 | 0 | 27355.02 | 14265.354 | 162962.637 | 0 | 0 | 0 | 5290.883 | 0 | 0
May | 1766240000000 | 1053797.673 | 24-MAY-15:15 | 242482.867 | 310109.712 | 86160.348 | 0 | 86263.516 | 0 | 32210.657 | 22475.356 | 162962.637 | 0 | 0 | 0 | 5841.569 | 0 | 0
June | 1671660000000 | 1063186.202 | 15-JUN-16:45 | 242482.867 | 310109.712 | 92535.733 | 0 | 113543.866 | 0 | 33738.43 | 22475.356 | 162962.637 | 0 | 0 | 0 | 6179.538 | 0 | 0
July | 1672870000000 | 1024251.006 | 20-JUL-16:00 | 242482.867 | 310109.712 | 90178.75 | 0 | 125790.129 | 0 | 33875.652 | 22475.356 | 162962.637 | 0 | 0 | 0 | 6328.569 | 0 | 0
August | 1674390000000 | 1009763.776 | 18-AUG-16:00 | 242482.867 | 310109.712 | 86779.631 | 0 | 142627.55 | 0 | 36365.994 | 22475.356 | 162962.637 | 0 | 0 | 0 | 5960.029 | 0 | 0
September | 1583160000000 | 978275.604 | 07-SEP-15:00 | 242482.867 | 310109.712 | 79909.892 | 0 | 67775.162 | 0 | 30630.772 | 22475.356 | 162962.637 | 0 | 0 | 0 | 5729.956 | 0 | 0
October | 1720340000000 | 974594.022 | 27-OCT-16:45 | 242482.867 | 310109.712 | 76632.173 | 0 | 1610.522 | 3239 | 24983.356 | 0 | 162962.637 | 0 | 0 | 0 | 4935.893 | 0 | 0
November | 1702300000000 | 975461.661 | 29-NOV-17:30 | 242482.867 | 310109.712 | 75268.598 | 0 | 165.425 | 3239 | 24852.483 | 0 | 162962.637 | 0 | 0 | 0 | 4942.439 | 0 | 0
December | 1750990000000 | 983931.707 | 13-DEC-17:00 | 242482.867 | 310109.712 | 75372.989 | 0 | 472.162 | 3239 | 24901.962 | 0 | 162962.637 | 0 | 0 | 0 | 4924.457 | 0 | 0
Annual Sum or Average | 20391200000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1583160000000 | 974594.022 |  | 242482.867 | 310109.712 | 75149.174 | 0 | 50.964 | 0 | 24825.987 | 0 | 162962.637 | 0 | 0 | 0 | 4907.105 | 0 | 0
Maximum of Months | 1798610000000 | 1063186.202 |  | 242482.867 | 310109.712 | 92535.733 | 0 | 142627.55 | 3239 | 36365.994 | 22475.356 | 162962.637 | 0 | 0 | 0 | 6328.569 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 494639.03 | 111963.29 | 0 | 606602.32
Cost per Total Building Area ($/m2) | 22.06 | 4.99 | 0 | 27.05
Cost per Net Conditioned Building Area ($/m2) | 22.06 | 4.99 | 0 | 27.05

## Picture
DOE Commercial Building Benchmark - Hospital
Second Floor
Third Floor
Forth Floor
Fifth Floor

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ER_Exam1_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam1_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam1_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam1_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Trauma1_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Trauma1_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Trauma1_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Trauma1_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam3_Mult4_Flr_1 humidity sched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ER_Exam3_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam3_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam3_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam3_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Trauma2_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Trauma2_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Trauma2_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Trauma2_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Triage_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Triage_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Triage_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Triage_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR1_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR1_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR1_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR1_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR2_Mult5_Flr_2 humidity sched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OR2_Mult5_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR2_Mult5_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR2_Mult5_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR2_Mult5_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR3_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR3_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR3_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR3_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR4_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR4_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR4_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR4_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PhysTherapy_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PhysTherapy_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PhysTherapy_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PhysTherapy_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Radiology_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Radiology_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Radiology_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Radiology_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_5 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_5 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen_Flr_5 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
CAV_1_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
CAV_2_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 57.4 | 2993
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
CRITICAL_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
ADMIN_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5
|  |  | WinterDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 60.1 | 3133.79
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
CRITICAL_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6 | 130.2 | 6789
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
ADMIN_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
CRITICAL_OCC_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1 | 119.7 | 6241.5
|  |  | SummerDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | WinterDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
ADMIN_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
CRITICAL_HTGSETP_SCH | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CRITICAL_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 532.8 | 3729.6 | 194472
ADMIN_HTGSETP_SCH | Temperature | Through 12/31 | WD | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6
|  |  | WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sat | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sun, Hol, Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
ADMIN_CLGSETP_SCH | Temperature | Through 12/31 | WD | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6
|  |  | WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sat | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sun, Hol, Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6 | 2869 | 149597.86
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6
|  |  | WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | WD | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668 | 4748 | 247574.29
|  |  | SummerDesign | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Sats | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
BLDG_OA_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_SAT_SCH | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_CAV_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6 | 109.2 | 5694
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
BLDG_CAV_SCH_HUMID | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
BLDG_OA_FRAC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 938.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0