## BuildingSummary
Building Summary Large Office new construction
|  | Value | Data Source
Program
| Building Name | Benchmark Large Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 46320 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 12 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.38
| East | 0.38
| North | 0.38
| West | 0.38
| Total | 0.38
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11589.72
| Net Dimensions - Total Area (m2) | 6953.64
| Wall to Skin Ratio | 0.765
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3563
| Net Dimensions - Total Area (m2) | 3563
| Roof to Skin Ratio | 0.235
Window Dimensions (m2)
| South | 1390.85
| East | 927.23
| North | 1390.85
| West | 927.23
| Total Area (m2) | 4636.16
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 3563
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 8523.53
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 92640.76
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.11 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Water cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | boiler
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 1504

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 10.76 | 4.842 | 0 | 0 | 10 | 0 | 958.824 | 0 | 0
Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.25388
Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.25387
Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0
Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.25388
Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.25387
Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.26264
Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0
Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8676 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6757 | 0 | 0.65051
Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.65928
Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.61 | 115.9 | 18.5806 | 16.8681 | 10.76 | 8.0701 | 0 | 0 | 10 | 0 | 168.6811 | 0 | 0.65051
Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.74 | 77.27 | 18.5806 | 10.8705 | 10.76 | 8.0698 | 0 | 0 | 10 | 0 | 108.7046 | 0 | 0.65928
Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.76 | 8.07 | 0 | 80.629 | 10 | 0 | 1362.882 | 0 | 0
Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | [10 empty] | 0.074437
Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | [10 empty] | 0.074437
Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.11 | 0 | [10 empty] | 0.96713
Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.72 | 4636.08 |  | 2397.06 |  |  |  | 967.5482 |  |  | 23970.5998
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 2.7007 | 8.6441 | 1.6122 | 11.8088 |  | 7.5544 | 3.096 | 30.0394 | 0 | 4.0795 | 11.7366 | 3.2113 | 3.5332 | 0 | 0.28645 | 0
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 3871.9305 | 3733.1398 | 3802.1312 | 3497.2213 | 3037.6588 | 3124.1129 | 3032.3275 | 3611.4716 | 2886.1139 | 3067.3416 | 3885.3543 | 2810.5346 | 3589.9919 | 2788.8661 | 3405.4115 | 4069.8471
Heating (kW)
| HEATSYS1 BOILER | 2569.9118 | 2854.6993 | 2845.995 | 2838.0141 | 2389.8558 | 2668.3191 | 2720.9682 | 3094.8153 | 2739.9771 | 2918.5007 | 3578.444 | 2941.5294 | 3509.9911 | 3275.5531 | 3652.8725 | 4905.095
HVAC Efficiency
| Air Conditioning (COP) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
| Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 15.31 | 15.47 | 16.67 | 14.63 | 13.73 | 15.13 | 15.46 | 15.08 | 16.93 | 15.24 | 16.97 | 16.71 | 15.46 | 16.29 | 16.5 | 21.22
| VAV_2_FAN | 163.49 | 164.96 | 186.51 | 160.33 | 150.31 | 170.52 | 170.37 | 165.51 | 188.3 | 170.91 | 186.09 | 186.57 | 171.66 | 182.32 | 183.74 | 242.37
| VAV_3_FAN | 17.47 | 17.67 | 19.97 | 17.53 | 15.25 | 18.38 | 16.71 | 17.73 | 19.2 | 17.09 | 19.64 | 18.73 | 18.07 | 18.44 | 18.36 | 25.11
| VAV_5_FAN | 6.35 | 6.16 | 4.55 | 6.01 | 5.74 | 4.24 | 3.51 | 5.64 | 5.46 | 4.23 | 6.41 | 5.37 | 5.37 | 4.95 | 5.1 | 4.91
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.084021 | 0.10786 | 0.078334 | 0.098506 | 0.055558 | 0.096278 | 0.1487 | 0.069518 | 0.036973 | 0.071979 | 0.088155 | 0.036974 | 0.061192 | 0.077263 | 0.061294 | 0.099157
| Total Cost ($/m2) | 9.9 | 12.06 | 8.45 | 10.09 | 5.32 | 9.44 | 13.31 | 7.02 | 3.43 | 6.29 | 8.34 | 3.32 | 5.66 | 6.76 | 5.41 | 8.84
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011391 | 0.0080543 | 0.008187 | 0.0096038 | 0.0085955 | 0.007679 | 0.0085348 | 0.0097013 | 0.0068961 | 0.0084128 | 0.0083639 | 0.0069085 | 0.0079015 | 0.0080657 | 0.0078832 | 0.0041221
| Total Cost ($/m2) | 0.1 | 0.44 | 0.34 | 0.56 | 0.17 | 0.26 | 0.65 | 0.93 | 0.39 | 0.87 | 1.23 | 0.61 | 1.46 | 1.14 | 1.74 | 1.59
Total Utility Costs
| Cost Intensity ($/m2) | 10 | 12.5 | 8.79 | 10.64 | 5.49 | 9.7 | 13.96 | 7.95 | 3.81 | 7.16 | 9.57 | 3.93 | 7.12 | 7.9 | 7.15 | 10.42
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1204480.5556 | 963350 | 761125 | 610705.5556 | 391294.4444 | 481955.5556 | 176263.8889 | 545975 | 306702.7778 | 147647.2222 | 366655.5556 | 220611.1111 | 304811.1111 | 153827.7778 | 160233.3333 | 117350
| Interior Lighting | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889 | 1427038.8889
| Exterior Lighting | 10922.2222 | 10919.4444 | 10916.6667 | 10913.8889 | 10905.5556 | 10905.5556 | 10911.1111 | 10902.7778 | 10908.3333 | 10886.1111 | 10905.5556 | 10900 | 10897.2222 | 10894.4444 | 10888.8889 | 10822.2222
| Interior Equipment | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222
| Exterior Equipment | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111
| Fans | 160169.4444 | 156480.5556 | 191877.7778 | 141941.6667 | 126902.7778 | 162558.3333 | 141147.2222 | 149091.6667 | 175016.6667 | 141675 | 168108.3333 | 169452.7778 | 163583.3333 | 166286.1111 | 178519.4444 | 249527.7778
| Pumps | 289772.2222 | 277913.8889 | 260897.2222 | 243136.1111 | 191225 | 181702.7778 | 144213.8889 | 253650 | 138291.6667 | 106363.8889 | 172422.2222 | 118025 | 151450 | 102244.4444 | 118147.2222 | 132369.4444
| Heat Rejection | 234102.7778 | 212116.6667 | 212377.7778 | 177780.5556 | 159602.7778 | 146377.7778 | 115066.6667 | 159488.8889 | 103225 | 79522.2222 | 105463.8889 | 79191.6667 | 91872.2222 | 63583.3333 | 60327.7778 | 60125
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5458072.2222 | 5179402.7778 | 4995816.6667 | 4743102.7778 | 4438552.7778 | 4542119.4444 | 4146222.2222 | 4677733.3333 | 4292766.6667 | 4044719.4444 | 4382177.7778 | 4156802.7778 | 4281238.8889 | 4055461.1111 | 4086738.8889 | 4128816.6667
Gas (MJ)
| Heating | 246890 | 2342960 | 1761680 | 2438190 | 686780 | 1345290 | 3252160 | 4196130 | 2334740 | 4519880 | 6526090 | 3832950 | 8259810 | 6226540 | 9884190 | 17439390
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 172410 | 206300 | 186730 | 239030 | 232770 | 210250 | 260760 | 264760 | 259890 | 278200 | 287350 | 286180 | 306860 | 310420 | 339070 | 377990
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 419310 | 2549260 | 1948410 | 2677220 | 919550 | 1555540 | 3512920 | 4460890 | 2594630 | 4798080 | 6813440 | 4119130 | 8566670 | 6536970 | 10223250 | 17817380
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 20068360 | 21195110 | 19933350 | 19752400 | 16898340 | 17907180 | 18439320 | 21300730 | 18048590 | 19359070 | 22589280 | 19083620 | 23979130 | 21136620 | 24935520 | 32681130
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 93.6117 | 74.8711 | 59.1543 | 47.4638 | 30.4112 | 37.4574 | 13.6992 | 42.4329 | 23.8368 | 11.4751 | 28.4963 | 17.1458 | 23.6898 | 11.9554 | 12.4533 | 9.1204
| Interior Lighting (elec) | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088 | 110.9088
| Exterior Lighting (elec) | 0.84887 | 0.84865 | 0.84844 | 0.84822 | 0.84758 | 0.84758 | 0.84801 | 0.84736 | 0.84779 | 0.84606 | 0.84758 | 0.84714 | 0.84693 | 0.84671 | 0.84628 | 0.8411
| Interior Equipment (elec) | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533
| Exterior Equipment (elec) | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124
| Fans (elec) | 12.4483 | 12.1616 | 14.9127 | 11.0316 | 9.8628 | 12.634 | 10.9699 | 11.5873 | 13.6022 | 11.0109 | 13.0653 | 13.1698 | 12.7136 | 12.9237 | 13.8745 | 19.3932
| Pumps (elec) | 22.521 | 21.5993 | 20.2768 | 18.8964 | 14.8619 | 14.1219 | 11.2082 | 19.7136 | 10.748 | 8.2666 | 13.4006 | 9.1729 | 11.7706 | 7.9464 | 9.1824 | 10.2877
| Heat Rejection (elec) | 18.1944 | 16.4856 | 16.5059 | 13.817 | 12.4043 | 11.3764 | 8.9429 | 12.3954 | 8.0226 | 6.1804 | 8.1966 | 6.1547 | 7.1403 | 4.9417 | 4.6886 | 4.6729
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 424.199 | 402.541 | 388.2727 | 368.6319 | 344.9624 | 353.0116 | 322.2426 | 363.5514 | 333.632 | 314.3539 | 340.581 | 323.0649 | 332.736 | 315.1887 | 317.6196 | 320.8899
Gas (MJ/m2)
| Heating (gas) | 5.3301 | 50.5816 | 38.0325 | 52.6375 | 14.8267 | 29.0432 | 70.2101 | 90.5893 | 50.4042 | 97.5786 | 140.8903 | 82.7487 | 178.3191 | 134.4233 | 213.3875 | 376.495
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7221 | 4.4538 | 4.0313 | 5.1604 | 5.0252 | 4.539 | 5.6295 | 5.7158 | 5.6107 | 6.006 | 6.2035 | 6.1783 | 6.6247 | 6.7016 | 7.3201 | 8.1603
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 9.0524 | 55.0354 | 42.0638 | 57.7979 | 19.852 | 33.5822 | 75.8396 | 96.3051 | 56.0149 | 103.5846 | 147.0938 | 88.9269 | 184.9439 | 141.1251 | 220.7074 | 384.6553
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 433.2512 | 457.5763 | 430.3365 | 426.43 | 364.8144 | 386.594 | 398.0822 | 459.8565 | 389.6468 | 417.9385 | 487.6748 | 411.9919 | 517.6799 | 456.3136 | 538.3272 | 705.5454
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1289.4489 | 1242.5799 | 1139.7941 | 1116.7495 | 1094.232 | 1049.958 | 1007.8537 | 1092.7243 | 1025.224 | 968.1083 | 982.956 | 1017.6705 | 978.3655 | 968.856 | 976.5339 | 1000.3126
| Feb | 1314.0431 | 1191.587 | 1160.6648 | 1124.0135 | 1085.9895 | 1082.1309 | 1105.8392 | 1069.1435 | 1082.029 | 1024.4935 | 982.3841 | 967.1561 | 977.1686 | 985.8428 | 976.8645 | 998.5715
| Mar | 1321.8648 | 1231.64 | 1212.1855 | 1140.3994 | 1091.2655 | 1103.333 | 1059.4604 | 1163.2422 | 1082.1759 | 1074.9412 | 1125.5838 | 1073.9298 | 1000.1424 | 1072.0381 | 975.8086 | 994.308
| Apr | 1359.9569 | 1270.3662 | 1220.9954 | 1184.8791 | 1128.9274 | 1162.9317 | 1097.1572 | 1159.6574 | 1120.1274 | 1048.682 | 1181.428 | 1101.0932 | 1111.0537 | 1055.0494 | 1002.0278 | 993.6523
| May | 1445.3086 | 1431.8175 | 1308.1451 | 1285.4214 | 1209.4131 | 1217.3576 | 1108.3074 | 1284.0469 | 1181.1299 | 1130.7072 | 1332.4532 | 1146.5568 | 1232.0824 | 1092.4385 | 1131.501 | 1154.134
| Jun | 1505.3711 | 1415.2257 | 1452.6469 | 1323.6615 | 1167.9713 | 1311.2038 | 1132.5808 | 1397.8346 | 1247.8388 | 1137.3766 | 1362.6303 | 1188.8987 | 1351.7671 | 1195.8218 | 1261.6738 | 1253.4528
| Jul | 1479.4652 | 1519.6817 | 1488.6959 | 1396.0574 | 1205.2435 | 1319.2558 | 1160.6473 | 1436.6376 | 1260.2693 | 1187.6273 | 1363.2087 | 1236.2885 | 1379.2762 | 1207.0919 | 1380.2635 | 1254.2851
| Aug | 1511.7029 | 1475.7716 | 1449.1354 | 1348.6788 | 1292.4952 | 1337.1328 | 1119.9686 | 1478.9658 | 1271.9856 | 1165.1282 | 1430.6828 | 1210.8061 | 1350.8735 | 1185.3937 | 1280.6496 | 1238.8525
| Sep | 1453.4044 | 1443.1265 | 1443.7084 | 1321.3729 | 1204.5271 | 1285.9233 | 1218.857 | 1249.1191 | 1215.1139 | 1173.1296 | 1297.707 | 1171.1515 | 1269.2706 | 1138.0223 | 1271.4568 | 1095.5504
| Oct | 1427.5396 | 1337.9102 | 1281.6643 | 1203.348 | 1153.2613 | 1184.9192 | 1134.2584 | 1226.527 | 1139.5344 | 1095.1665 | 1226.4605 | 1129.2208 | 1133.6295 | 1102.4451 | 1075.6803 | 996.4095
| Nov | 1325.5829 | 1275.9504 | 1198.8102 | 1132.7709 | 1108.9396 | 1086.1535 | 1080.8167 | 1181.8479 | 1068.669 | 1030.6979 | 1235.3344 | 1030.3687 | 1092.0368 | 974.553 | 974.8379 | 997.0834
| Dec | 1280.5726 | 1221.845 | 1141.5178 | 1116.4327 | 1094.0317 | 1074.2925 | 1004.886 | 1052.6074 | 997.5197 | 967.9511 | 982.4939 | 967.892 | 976.7916 | 966.1367 | 976.5168 | 998.6037
Time of Peak Electrical Demand
| Jan | 23-JAN-16:19 | 03-JAN-08:00 | 26-JAN-16:10 | 24-JAN-16:00 | 25-JAN-16:10 | 18-JAN-16:10 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:10 | 30-JAN-08:09 | 09-JAN-08:50 | 27-JAN-16:10 | 02-JAN-08:50 | 10-JAN-08:09 | 27-JAN-08:39 | 03-JAN-08:30
| Feb | 22-FEB-16:10 | 15-FEB-16:10 | 28-FEB-16:10 | 22-FEB-08:09 | 13-FEB-08:00 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:10 | 21-FEB-16:10 | 27-FEB-08:09 | 08-FEB-08:20 | 08-FEB-08:30 | 03-FEB-16:10 | 06-FEB-08:30 | 02-FEB-08:50
| Mar | 27-MAR-15:20 | 29-MAR-07:00 | 17-MAR-15:00 | 29-MAR-15:09 | 31-MAR-15:09 | 31-MAR-15:30 | 20-MAR-15:09 | 09-MAR-16:10 | 02-MAR-16:10 | 29-MAR-15:30 | 31-MAR-15:50 | 30-MAR-15:09 | 23-MAR-15:00 | 30-MAR-15:09 | 09-MAR-08:30 | 03-MAR-08:00
| Apr | 03-APR-15:09 | 25-APR-15:09 | 17-APR-15:09 | 20-APR-15:00 | 11-APR-15:00 | 21-APR-15:30 | 13-APR-15:09 | 04-APR-07:00 | 21-APR-15:00 | 14-APR-15:09 | 10-APR-07:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:30 | 04-APR-15:09 | 07-APR-07:49
| May | 15-MAY-15:00 | 30-MAY-07:00 | 30-MAY-15:00 | 31-MAY-15:00 | 30-MAY-07:00 | 31-MAY-15:00 | 25-MAY-15:50 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-08:00 | 24-MAY-15:00 | 31-MAY-15:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:09
| Jun | 27-JUN-15:39 | 29-JUN-15:00 | 28-JUN-15:00 | 08-JUN-15:00 | 29-JUN-07:00 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:00 | 28-JUN-15:30 | 29-JUN-07:00 | 27-JUN-15:39 | 29-JUN-15:00 | 26-JUN-15:39 | 14-JUN-15:09 | 21-JUN-15:50
| Jul | 05-JUL-07:00 | 18-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 24-JUL-15:09 | 25-JUL-15:00 | 03-JUL-15:09 | 25-JUL-15:39 | 03-JUL-15:30 | 31-JUL-15:00 | 13-JUL-15:09 | 17-JUL-15:09 | 13-JUL-15:00 | 21-JUL-15:00 | 07-JUL-07:00 | 03-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 02-AUG-15:30 | 14-AUG-15:00 | 16-AUG-15:00 | 07-AUG-15:00 | 14-AUG-15:09 | 09-AUG-15:09 | 04-AUG-08:00 | 07-AUG-15:09 | 04-AUG-15:50 | 30-AUG-15:30 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-15:09
| Sep | 11-SEP-15:09 | 15-SEP-15:20 | 05-SEP-07:00 | 05-SEP-15:00 | 08-SEP-07:00 | 01-SEP-15:09 | 28-SEP-15:09 | 05-SEP-15:09 | 05-SEP-15:09 | 01-SEP-15:00 | 07-SEP-15:09 | 01-SEP-15:00 | 22-SEP-15:00 | 01-SEP-15:00 | 07-SEP-15:20 | 07-SEP-15:00
| Oct | 06-OCT-15:30 | 30-OCT-15:09 | 03-OCT-13:09 | 20-OCT-15:00 | 19-OCT-15:30 | 03-OCT-15:09 | 13-OCT-15:09 | 03-OCT-07:00 | 11-OCT-15:39 | 17-OCT-15:09 | 31-OCT-07:00 | 05-OCT-15:39 | 06-OCT-15:09 | 06-OCT-15:20 | 06-OCT-15:09 | 10-OCT-07:10
| Nov | 01-NOV-15:09 | 27-NOV-08:00 | 13-NOV-16:10 | 22-NOV-08:00 | 08-NOV-08:00 | 10-NOV-16:10 | 16-NOV-16:10 | 03-NOV-15:09 | 08-NOV-16:10 | 03-NOV-15:09 | 02-NOV-07:00 | 10-NOV-13:00 | 02-NOV-15:09 | 21-NOV-16:10 | 30-NOV-08:20 | 22-NOV-08:00
| Dec | 15-DEC-16:10 | 20-DEC-08:00 | 11-DEC-16:10 | 26-DEC-16:10 | 18-DEC-08:00 | 05-DEC-16:10 | 12-DEC-08:09 | 08-DEC-08:00 | 05-DEC-16:10 | 14-DEC-08:20 | 11-DEC-08:09 | 01-DEC-08:30 | 20-DEC-08:39 | 01-DEC-08:50 | 18-DEC-08:30 | 28-DEC-08:20
Source Energy
| Total Source Energy (GJ) | 65633.8 | 70505.53 | 59014.03 | 60364.41 | 50458.52 | 60188.45 | 50033.32 | 65090.56 | 54109.57 | 30604.75 | 63381.39 | 54150.26 | 62327.43 | 57886.77 | 61729.84 | 72549.87
| Total Source Energy (MJ/m2) | 1416.95 | 1522.13 | 1274.04 | 1303.19 | 1089.34 | 1299.39 | 1080.16 | 1405.23 | 1168.16 | 660.72 | 1368.33 | 1169.04 | 1345.57 | 1249.7 | 1332.67 | 1566.26
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 19601.49 | 16201.37 | 25891.02 | 12124.71 | 8392.05 | 18765.73 | 4961.94 | 11092.61 | 11038.61 | 4036.61 | 7714.07 | 7971.2 | 6386.8 | 5544.58 | 3673.4 | 3693.09
| Water Systems | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13
| Total Building | 21105.63 | 17705.5 | 27395.15 | 13628.85 | 9896.18 | 20269.87 | 6466.07 | 12596.75 | 12542.75 | 5540.74 | 9218.21 | 9475.33 | 7890.93 | 7048.71 | 5177.54 | 5197.22
Emissions
| Carbon Equivalent (kg) | 1504440 | 1773620 | 1543250 | 1509330 | 535297.1678 | 1559990 | 547899.0922 | 1342750 | 1800370 | 381115.8977 | 2459220 | 1772320 | 1619920 | 1599900 | 1583220 | 1483090
| CO2 (kg) | 3487940 | 4467980 | 3648140 | 3455480 | 1432790 | 3709470 | 1476690 | 3063190 | 4221210 | 949781.0982 | 5745580 | 4171220 | 3824730 | 3787550 | 3757560 | 3838610
| NOX (kg) | 6132.6545 | 5818.7529 | 6086.5404 | 6529.822 | 1228.6419 | 6023.9368 | 1273.2522 | 5870.8706 | 7291.8177 | 1351.3488 | 10138.0012 | 7136.8608 | 6570.1872 | 6427.914 | 6368.4653 | 4488.8381
| SO2 (kg) | 23362.8398 | 24706.4395 | 20089.7 | 16649.0098 | 12915.9056 | 24985.7136 | 12065.9509 | 17076.7943 | 18746.348 | 3127.5307 | 29534.1915 | 18153.0278 | 10106.7041 | 10830.3162 | 9648.0999 | 21022.1053
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1065 | 0.0697 | 0.0547 | 0.061 | 0.0059 | 0.047 | 0.0058 | 0.0693 | 0.0733 | 0.0127 | 0.0897 | 0.0711 | 0.0746 | 0.0758 | 0.0714 | 0.073
| Water for Electricity (m3) | 2891.46 | 8427.5 | 148398 | 29614 | 77931.1 | 124609 | 72798.4 | 1062.02 | 19492.6 | 41324.1 | 6798.68 | 18875.2 | 6642.09 | 256890 | 6340.33 | 4218.33

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20068.36 | 433.25 | 433.25
Net Site Energy | 20068.36 | 433.25 | 433.25
Total Source Energy | 65633.8 | 1416.95 | 1416.95
Net Source Energy | 65633.8 | 1416.95 | 1416.95
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 246.89 | 0 | 0 | 0 | 0
Cooling | 4336.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 576.61 | 0 | 0 | 0 | 0 | 0
Pumps | 1043.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 842.77 | 0 | 0 | 0 | 0 | 19601.49
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 172.41 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19649.06 | 419.31 | 0 | 0 | 0 | 21105.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 1390.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3871930.48 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2569911.83 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3660734.27
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 360264.43 | 250095.74 | 110168.68 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 3833178.23 | 2667406.06 | 1165772.17 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 407433.85 | 284446.06 | 122987.79 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 148482.17 | 102884.41 | 45597.76 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 77875.78 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 111480.19 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1239267.53 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 136166.96 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15905.88 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20272.27 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16897.89 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 23326.8 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 160769.89 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 200323.45 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 170695 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 235027.05 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15981.25 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19608.85 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18502.97 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24057.77 | -
VAV_1_HEATC | Coil:Heating:Water | 6222.13 | -
VAV_2_HEATC | Coil:Heating:Water | 46270.32 | -
VAV_3_HEATC | Coil:Heating:Water | 2896.93 | -
VAV_5_HEATC | Coil:Heating:Water | 26615.28 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.31 | 25942.39 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 163.49 | 269413.67 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.47 | 29401.51 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.35 | 11906.03 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35480.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14555.34 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 51666.16 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 275580.8357 | 480.9373 | 1817.5428 | 0 | 0.0083 | 224941.9853 | 118504.0527
February | 249395.0336 | 437.1487 | 1659.8748 | 0 | 0.0076 | 205430.1905 | 107435.1652
March | 288041.164 | 505.7869 | 1924.1544 | 0 | 0.0088 | 238138.7659 | 124173.2243
April | 273442.0466 | 481.5199 | 1837.4004 | 0 | 0.0084 | 227402.8691 | 118016.7234
May | 307355.106 | 541.3409 | 2066.0793 | 0 | 0.0094 | 255705.0147 | 132663.668
June | 311093.6847 | 548.0536 | 2092.2176 | 0 | 0.0095 | 258940.0817 | 134290.1725
July | 312194.0544 | 550.0365 | 2099.9675 | 0 | 0.0096 | 259899.2656 | 134769.6196
August | 330648.068 | 582.5171 | 2223.8425 | 0 | 0.0101 | 275230.442 | 142732.6944
September | 301322.0877 | 530.7439 | 2025.7521 | 0 | 0.0092 | 250714.0075 | 130062.5332
October | 295869.1934 | 521.0344 | 1988.2675 | 0 | 0.0091 | 246074.7102 | 127698.34
November | 276227.8864 | 486.1448 | 1853.9091 | 0 | 0.0084 | 229445.8307 | 119190.9374
December | 266770.2283 | 467.3905 | 1773.8319 | 0 | 0.0081 | 219533.6476 | 114898.6506
Annual Sum or Average | 3487940 | 6132.6545 | 23362.8398 | 0 | 0.1065 | 2891460 | 1504440
Minimum of Months | 249395.0336 | 437.1487 | 1659.8748 | 0 | 0.0076 | 205430.1905 | 107435.1652
Maximum of Months | 330648.068 | 582.5171 | 2223.8425 | 0 | 0.0101 | 275230.442 | 142732.6944
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1528610000000 | 1289448.913 | 23-JAN-16:19 | 448566.544 | 326066.958 | 39280.846 | 0 | 281078.772 | 0 | 60853.27 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1396010000000 | 1314043.099 | 22-FEB-16:10 | 448566.544 | 326066.958 | 42377.507 | 0 | 301881.179 | 0 | 61548.388 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1618290000000 | 1321864.802 | 27-MAR-15:20 | 448566.544 | 326066.958 | 42991.039 | 0 | 308905.817 | 0 | 61731.921 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1545330000000 | 1359956.937 | 03-APR-15:09 | 448566.544 | 326066.958 | 47816.714 | 0 | 341220.103 | 0 | 62684.096 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1737660000000 | 1445308.632 | 15-MAY-15:00 | 448566.544 | 326066.958 | 51408.6 | 0 | 421021.482 | 0 | 64642.526 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1759640000000 | 1505371.08 | 27-JUN-15:39 | 448566.544 | 326066.958 | 50381.235 | 0 | 481362.178 | 0 | 65391.643 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1766160000000 | 1479465.17 | 05-JUL-07:00 | 448566.544 | 326066.958 | 49587.029 | 0 | 420441.523 | 0 | 64534.001 | 48047.137 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
August | 1870340000000 | 1511702.929 | 21-AUG-15:09 | 448566.544 | 326066.958 | 55841.98 | 0 | 481775.988 | 0 | 65848.937 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1703740000000 | 1453404.38 | 11-SEP-15:09 | 448566.544 | 326066.958 | 54988.647 | 0 | 425328.367 | 0 | 64851.342 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1672210000000 | 1427539.621 | 06-OCT-15:30 | 448566.544 | 326066.958 | 48862.328 | 0 | 406330.77 | 0 | 64110.5 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1559210000000 | 1325582.933 | 01-NOV-15:09 | 448566.544 | 326066.958 | 35031.108 | 0 | 321115.389 | 0 | 61200.412 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1491850000000 | 1280572.636 | 15-DEC-16:10 | 448566.544 | 326066.958 | 32982.071 | 0 | 279105.976 | 0 | 60248.565 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 19649100000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1396010000000 | 1280572.636 |  | 448566.544 | 326066.958 | 32982.071 | 0 | 279105.976 | 0 | 60248.565 | 48047.137 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1870340000000 | 1511702.929 |  | 448566.544 | 326066.958 | 55841.98 | 0 | 481775.988 | 0 | 65848.937 | 48047.137 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 458590.23 | 4776.37 | 0 | 463366.6
Cost per Total Building Area ($/m2) | 9.9 | 0.1 | 0 | 10
Cost per Net Conditioned Building Area ($/m2) | 9.9 | 0.1 | 0 | 10

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21195.11 | 457.58 | 457.58
Net Site Energy | 21195.11 | 457.58 | 457.58
Total Source Energy | 70505.53 | 1522.13 | 1522.13
Net Source Energy | 70505.53 | 1522.13 | 1522.13
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2342.96 | 0 | 0 | 0 | 0
Cooling | 3468.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 563.33 | 0 | 0 | 0 | 0 | 0
Pumps | 1000.49 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 763.62 | 0 | 0 | 0 | 0 | 16201.37
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 206.3 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18645.85 | 2549.26 | 0 | 0 | 0 | 17705.5
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 1390.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3733139.83 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2854699.3 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3529514.02
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 357071.72 | 248318.3 | 108753.43 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 3793131.47 | 2644353.4 | 1148778.07 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 404687.55 | 282938.51 | 121749.04 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 139997.61 | 97500.2 | 42497.41 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 75250.41 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 110967.27 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1229397.07 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 134890.19 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17356.03 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20084.29 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16740.99 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 23988.85 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 175579.85 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 200599.02 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 170007.75 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 241179.27 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18057.15 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19645.78 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18741.85 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24720.41 | -
VAV_1_HEATC | Coil:Heating:Water | 28941.29 | -
VAV_2_HEATC | Coil:Heating:Water | 275192.11 | -
VAV_3_HEATC | Coil:Heating:Water | 25852.2 | -
VAV_5_HEATC | Coil:Heating:Water | 16559.14 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.47 | 26211.48 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 164.96 | 271842.5 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.67 | 29748.72 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.16 | 11546.89 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34209.06 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16168.31 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 49814.17 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 360904.391 | 460.3653 | 1860.543 | 0 | 0.0053 | 634598.1205 | 142021.5571
February | 316923.7667 | 404.2747 | 1633.9603 | 0 | 0.0047 | 557314.8324 | 124715.8445
March | 366687.0125 | 476.0739 | 2007.0515 | 0 | 0.0057 | 684609.3168 | 145371.1285
April | 344604.9909 | 450.9828 | 1936.3015 | 0 | 0.0054 | 660492.45 | 137078.0609
May | 387615.6309 | 508.9125 | 2200.9701 | 0 | 0.0062 | 750780.8349 | 154398.6114
June | 408880.0021 | 537.1174 | 2325.7229 | 0 | 0.0065 | 793336.9382 | 162905.7254
July | 411974.7916 | 541.2094 | 2343.6983 | 0 | 0.0066 | 799468.7166 | 164142.1745
August | 434051.3844 | 570.1936 | 2469.0432 | 0 | 0.0069 | 842225.5516 | 172935.8234
September | 374978.9354 | 492.5461 | 2132.3621 | 0 | 0.006 | 727378.6891 | 149394.0015
October | 365412.6822 | 479.183 | 2066.7934 | 0 | 0.0058 | 705008.8322 | 145479.9514
November | 342087.0929 | 445.9949 | 1898.4463 | 0 | 0.0054 | 647572.2471 | 135858.2947
December | 353856.7143 | 451.8992 | 1831.5468 | 0 | 0.0052 | 624710.5554 | 139315.7038
Annual Sum or Average | 4467980 | 5818.7529 | 24706.4395 | 0 | 0.0697 | 8427500 | 1773620
Minimum of Months | 316923.7667 | 404.2747 | 1633.9603 | 0 | 0.0047 | 557314.8324 | 124715.8445
Maximum of Months | 434051.3844 | 570.1936 | 2469.0432 | 0 | 0.0069 | 842225.5516 | 172935.8234
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1404050000000 | 1242579.914 | 03-JAN-08:00 | 448566.544 | 326066.958 | 29214.949 | 0 | 213450.761 | 0 | 56733.853 | 46324.871 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1233060000000 | 1191586.963 | 15-FEB-16:10 | 448566.544 | 326066.958 | 29215.747 | 0 | 199559.72 | 0 | 56297.738 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1514700000000 | 1231640.024 | 29-MAR-07:00 | 448566.544 | 326066.958 | 29214.949 | 0 | 202776.36 | 0 | 56468.363 | 46324.871 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1461340000000 | 1270366.178 | 25-APR-15:09 | 448566.544 | 326066.958 | 33186.082 | 0 | 272317.417 | 0 | 58348.921 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1661100000000 | 1431817.473 | 30-MAY-07:00 | 448566.544 | 326066.958 | 48369.238 | 0 | 378340.507 | 0 | 61927.376 | 46324.871 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
June | 1755260000000 | 1415225.654 | 29-JUN-15:00 | 448566.544 | 326066.958 | 45618.527 | 0 | 401252.179 | 0 | 61841.19 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1768830000000 | 1519681.738 | 18-JUL-15:00 | 448566.544 | 326066.958 | 56153.383 | 0 | 492571.949 | 0 | 64442.648 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1863430000000 | 1475771.626 | 31-AUG-15:00 | 448566.544 | 326066.958 | 55744.93 | 0 | 449860.808 | 0 | 63652.13 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1609330000000 | 1443126.541 | 15-SEP-15:20 | 448566.544 | 326066.958 | 40610.651 | 0 | 434221.869 | 0 | 61780.263 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1559830000000 | 1337910.185 | 30-OCT-15:09 | 448566.544 | 326066.958 | 33771.992 | 0 | 338091.758 | 0 | 59532.676 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1432750000000 | 1275950.371 | 27-NOV-08:00 | 448566.544 | 326066.958 | 29220.83 | 0 | 246149.202 | 0 | 57399.987 | 46324.871 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1382170000000 | 1221844.991 | 20-DEC-08:00 | 448566.544 | 326066.958 | 29214.949 | 0 | 193122.84 | 0 | 56326.851 | 46324.871 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18645900000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1233060000000 | 1191586.963 |  | 448566.544 | 326066.958 | 29214.949 | 0 | 193122.84 | 0 | 56297.738 | 46324.871 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1863430000000 | 1519681.738 |  | 448566.544 | 326066.958 | 56153.383 | 0 | 492571.949 | 0 | 64442.648 | 46324.871 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 558636.67 | 20532.5 | 0 | 579169.17
Cost per Total Building Area ($/m2) | 12.06 | 0.44 | 0 | 12.5
Cost per Net Conditioned Building Area ($/m2) | 12.06 | 0.44 | 0 | 12.5

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19933.35 | 430.34 | 430.34
Net Site Energy | 19933.35 | 430.34 | 430.34
Total Source Energy | 59014.03 | 1274.04 | 1274.04
Net Source Energy | 59014.03 | 1274.04 | 1274.04
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1761.68 | 0 | 0 | 0 | 0
Cooling | 2740.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 690.76 | 0 | 0 | 0 | 0 | 0
Pumps | 939.23 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 764.56 | 0 | 0 | 0 | 0 | 25891.02
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 186.73 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17984.94 | 1948.41 | 0 | 0 | 0 | 27395.15
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.251 | 0.11 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.251 | 0.11 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 1390.85 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3802131.16 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2845994.99 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3594742.18
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 358622.15 | 245177.26 | 113444.89 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 3986172.07 | 2734614.14 | 1251557.94 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 425261.26 | 292392.79 | 132868.46 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 97287.04 | 65703.8 | 31583.23 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 53592.69 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 110411.11 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1306854.97 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 143710.83 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21005.54 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21321.61 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18389.63 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25456.28 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 219384.25 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 221068.31 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 192462.47 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 259163.9 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22361.72 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21835.86 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 21042.84 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26517.9 | -
VAV_1_HEATC | Coil:Heating:Water | 15071.89 | -
VAV_2_HEATC | Coil:Heating:Water | 122265.73 | -
VAV_3_HEATC | Coil:Heating:Water | 10297.87 | -
VAV_5_HEATC | Coil:Heating:Water | 12608.45 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.67 | 28068.73 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 186.51 | 307358.86 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.97 | 33620.81 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.55 | 8670.64 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 34841.27 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16119.01 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 50734.77 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 272874.9478 | 441.4035 | 1402.4153 | 0 | 0.0039 | 10358600 | 114030.9794
February | 247336.4402 | 402.7717 | 1290.5455 | 0 | 0.0035 | 9532450 | 103629.7091
March | 297148.6657 | 494.8277 | 1629.5943 | 0 | 0.0044 | 12037400 | 125606.4406
April | 281837.2606 | 474.5271 | 1583.2188 | 0 | 0.0043 | 11695100 | 119659.7324
May | 315018.1273 | 531.7355 | 1779.3207 | 0 | 0.0048 | 13143700 | 133883.0559
June | 340646.1132 | 575.249 | 1925.9177 | 0 | 0.0052 | 14226600 | 144800.729
July | 352945.6634 | 596.1044 | 1996.0723 | 0 | 0.0054 | 14744900 | 150037.5977
August | 365479.3972 | 617.2358 | 2066.6863 | 0 | 0.0056 | 15266500 | 155361.9269
September | 322764.4849 | 545.0138 | 1824.5412 | 0 | 0.0049 | 13477800 | 137195.7688
October | 301541.7316 | 507.9397 | 1695.6185 | 0 | 0.0046 | 12525400 | 128049.5688
November | 275244.0792 | 458.4861 | 1510.4446 | 0 | 0.0041 | 11157300 | 116360.9087
December | 275305.564 | 441.2459 | 1385.3247 | 0 | 0.0038 | 10232200 | 114633.1802
Annual Sum or Average | 3648140 | 6086.5404 | 20089.7 | 0 | 0.0547 | 148398000 | 1543250
Minimum of Months | 247336.4402 | 402.7717 | 1290.5455 | 0 | 0.0035 | 9532450 | 103629.7091
Maximum of Months | 365479.3972 | 617.2358 | 2066.6863 | 0 | 0.0056 | 15266500 | 155361.9269
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1255400000000 | 1139794.095 | 26-JAN-16:10 | 448566.544 | 326066.958 | 36278.803 | 0 | 141117.388 | 0 | 55028.026 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1155280000000 | 1160664.847 | 28-FEB-16:10 | 448566.544 | 326066.958 | 37904.957 | 0 | 159899.946 | 0 | 55490.066 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1458860000000 | 1212185.526 | 17-MAR-15:00 | 448566.544 | 326066.958 | 42882.512 | 0 | 205356.171 | 0 | 56576.965 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1417370000000 | 1220995.411 | 17-APR-15:09 | 448566.544 | 326066.958 | 43008.777 | 0 | 208054.881 | 0 | 62561.874 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1592940000000 | 1308145.073 | 30-MAY-15:00 | 448566.544 | 326066.958 | 60051.519 | 0 | 281656.1 | 0 | 59067.576 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1724180000000 | 1452646.946 | 28-JUN-15:00 | 448566.544 | 326066.958 | 82857.464 | 0 | 393815.881 | 0 | 68603.724 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1786990000000 | 1488695.93 | 11-JUL-15:00 | 448566.544 | 326066.958 | 78936.77 | 0 | 435947.071 | 0 | 66442.211 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1850210000000 | 1449135.366 | 02-AUG-15:30 | 448566.544 | 326066.958 | 71389.791 | 0 | 405200.001 | 0 | 65175.696 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1633430000000 | 1443708.436 | 05-SEP-07:00 | 448566.544 | 326066.958 | 54736.979 | 0 | 379715.773 | 0 | 65219.213 | 47180.991 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
October | 1518000000000 | 1281664.261 | 03-OCT-13:09 | 448566.544 | 326066.958 | 38355.096 | 0 | 322951.115 | 0 | 61876.963 | 47180.991 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
November | 1352190000000 | 1198810.188 | 13-NOV-16:10 | 448566.544 | 326066.958 | 41642.935 | 0 | 193516.686 | 0 | 56280.689 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1240080000000 | 1141517.752 | 11-DEC-16:10 | 448566.544 | 326066.958 | 36050.095 | 0 | 143095.302 | 0 | 55002.478 | 47180.991 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17984900000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1155280000000 | 1139794.095 |  | 448566.544 | 326066.958 | 36050.095 | 0 | 141117.388 | 0 | 55002.478 | 47180.991 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1850210000000 | 1488695.93 |  | 448566.544 | 326066.958 | 82857.464 | 0 | 435947.071 | 0 | 68603.724 | 47180.991 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 391344.5 | 15951.57 | 0 | 407296.07
Cost per Total Building Area ($/m2) | 8.45 | 0.34 | 0 | 8.79
Cost per Net Conditioned Building Area ($/m2) | 8.45 | 0.34 | 0 | 8.79

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19752.4 | 426.43 | 426.43
Net Site Energy | 19752.4 | 426.43 | 426.43
Total Source Energy | 60364.41 | 1303.19 | 1303.19
Net Source Energy | 60364.41 | 1303.19 | 1303.19
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2438.19 | 0 | 0 | 0 | 0
Cooling | 2198.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 510.99 | 0 | 0 | 0 | 0 | 0
Pumps | 875.29 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 640.01 | 0 | 0 | 0 | 0 | 12124.71
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 239.03 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17075.17 | 2677.22 | 0 | 0 | 0 | 13628.85
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 1390.85 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3497221.31 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2838014.07 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3306463.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 314022.41 | 214099.21 | 99923.2 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 3422165.17 | 2342104.21 | 1080060.95 | 0.68 | -
VAV_3_COOLC | Coil:Cooling:Water | 373289.81 | 256317.11 | 116972.7 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 127232.98 | 86581.16 | 40651.82 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 71021.84 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 108770.93 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1215110.09 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 134717.14 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14809.49 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16926.11 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13591.54 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 18830.82 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 151856.58 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 178519.37 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 152667.09 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 197551.53 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16829.52 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18013.32 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16939.77 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 20816.02 | -
VAV_1_HEATC | Coil:Heating:Water | 39055.32 | -
VAV_2_HEATC | Coil:Heating:Water | 373173.42 | -
VAV_3_HEATC | Coil:Heating:Water | 35387.17 | -
VAV_5_HEATC | Coil:Heating:Water | 21025.28 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.63 | 24780.61 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 160.33 | 264218.61 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.53 | 29516.56 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.01 | 11268.82 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32047.19 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16073.81 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 46666.12 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 290796.3041 | 520.7123 | 1259.8927 | 0 | 0.0047 | 2240740 | 124357.2887
February | 249784.2114 | 455.779 | 1123.8959 | 0 | 0.0042 | 1998950 | 107604.1459
March | 289151.3564 | 544.4763 | 1383.698 | 0 | 0.0051 | 2461200 | 126120.5385
April | 271491.4553 | 518.0407 | 1332.6122 | 0 | 0.0049 | 2370400 | 119047.4187
May | 294777.7632 | 567.2032 | 1470.0958 | 0 | 0.0054 | 2614990 | 129695.0875
June | 306592.7545 | 591.07 | 1534.5715 | 0 | 0.0056 | 2729690 | 134998.0092
July | 308958.0921 | 595.6424 | 1546.4708 | 0 | 0.0056 | 2750860 | 136040.642
August | 328042.2037 | 632.5097 | 1642.3628 | 0 | 0.006 | 2921430 | 144450.6969
September | 293584.0597 | 565.7494 | 1468.2753 | 0 | 0.0054 | 2611760 | 129247.7442
October | 279967.9139 | 535.6879 | 1381.4397 | 0 | 0.005 | 2457270 | 122900.334
November | 266716.3136 | 500.6811 | 1268.7412 | 0 | 0.0047 | 2256710 | 116191.8212
December | 275619.2557 | 502.27 | 1236.9539 | 0 | 0.0046 | 2200030 | 118673.563
Annual Sum or Average | 3455480 | 6529.822 | 16649.0098 | 0 | 0.061 | 29614000 | 1509330
Minimum of Months | 249784.2114 | 455.779 | 1123.8959 | 0 | 0.0042 | 1998950 | 107604.1459
Maximum of Months | 328042.2037 | 632.5097 | 1642.3628 | 0 | 0.006 | 2921430 | 144450.6969
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1291990000000 | 1116749.473 | 24-JAN-16:00 | 448566.544 | 326066.958 | 28391.489 | 0 | 133160.368 | 0 | 51611.392 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1152580000000 | 1124013.527 | 22-FEB-08:09 | 448566.544 | 326066.958 | 28391.489 | 0 | 104769.995 | 0 | 50599.226 | 43397.337 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1419110000000 | 1140399.357 | 29-MAR-15:09 | 448566.544 | 326066.958 | 28391.489 | 0 | 156173.807 | 0 | 52247.837 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1366750000000 | 1184879.105 | 20-APR-15:00 | 448566.544 | 326066.958 | 32674.454 | 0 | 195063.963 | 0 | 53554.465 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1507780000000 | 1285421.449 | 31-MAY-15:00 | 448566.544 | 326066.958 | 39446.71 | 0 | 286033.467 | 0 | 56355.048 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1573910000000 | 1323661.535 | 08-JUN-15:00 | 448566.544 | 326066.958 | 37130.049 | 0 | 326087.4 | 0 | 56857.862 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1586120000000 | 1396057.431 | 03-JUL-15:00 | 448566.544 | 326066.958 | 51241.787 | 0 | 381918.291 | 0 | 59311.128 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1684470000000 | 1348678.823 | 14-AUG-15:00 | 448566.544 | 326066.958 | 44888.049 | 0 | 342279.791 | 0 | 57924.758 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1505920000000 | 1321372.941 | 05-SEP-15:00 | 448566.544 | 326066.958 | 46212.367 | 0 | 313922.026 | 0 | 57652.323 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1416840000000 | 1203348.019 | 20-OCT-15:00 | 448566.544 | 326066.958 | 30582.34 | 0 | 215281.745 | 0 | 53897.71 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1301200000000 | 1132770.852 | 22-NOV-08:00 | 448566.544 | 326066.958 | 28391.489 | 0 | 113234.506 | 0 | 50892.04 | 43397.337 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1268520000000 | 1116432.732 | 26-DEC-16:10 | 448566.544 | 326066.958 | 28391.489 | 0 | 133080.106 | 0 | 51374.913 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17075200000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1152580000000 | 1116432.732 |  | 448566.544 | 326066.958 | 28391.489 | 0 | 104769.995 | 0 | 50599.226 | 43397.337 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1684470000000 | 1396057.431 |  | 448566.544 | 326066.958 | 51241.787 | 0 | 381918.291 | 0 | 59311.128 | 43397.337 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 467224.45 | 25711.47 | 0 | 492935.93
Cost per Total Building Area ($/m2) | 10.09 | 0.56 | 0 | 10.64
Cost per Net Conditioned Building Area ($/m2) | 10.09 | 0.56 | 0 | 10.64

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16898.34 | 364.81 | 364.81
Net Site Energy | 16898.34 | 364.81 | 364.81
Total Source Energy | 50458.52 | 1089.34 | 1089.34
Net Source Energy | 50458.52 | 1089.34 | 1089.34
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 686.78 | 0 | 0 | 0 | 0
Cooling | 1408.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 456.85 | 0 | 0 | 0 | 0 | 0
Pumps | 688.41 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 574.57 | 0 | 0 | 0 | 0 | 8392.05
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 232.77 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15978.79 | 919.55 | 0 | 0 | 0 | 9896.18
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 1390.85 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3037658.75 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2389855.85 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2871968.27
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 307937.28 | 217024.98 | 90912.3 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 3359362.15 | 2373635.86 | 985726.29 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 340191.12 | 240675.42 | 99515.7 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 127687.06 | 89955.37 | 37731.68 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 70209.5 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 106887.63 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1197403.81 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 120561.89 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15959.49 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15700.91 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11728.26 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 17610.73 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 165163.74 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 164035.86 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 128209.77 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 183071.32 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16592.57 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16379.52 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13957.76 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 18998.26 | -
VAV_1_HEATC | Coil:Heating:Water | 11744.96 | -
VAV_2_HEATC | Coil:Heating:Water | 97969.6 | -
VAV_3_HEATC | Coil:Heating:Water | 9462.75 | -
VAV_5_HEATC | Coil:Heating:Water | 7518.91 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.73 | 23263.76 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 150.31 | 247701.9 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.25 | 25841.54 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.74 | 10772.11 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27835.94 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13535.55 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 40533.83 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 116276.7351 | 99.9684 | 1001.8132 | 0 | 0.0005 | 6044510 | 43300.066
February | 103924.4117 | 89.2867 | 906.444 | 0 | 0.0004 | 5469130 | 38733.9384
March | 121563.3847 | 104.3611 | 1074.6365 | 0 | 0.0005 | 6483990 | 45351.9651
April | 112412.2318 | 96.3945 | 1013.4976 | 0 | 0.0005 | 6115170 | 41998.2035
May | 122184.3655 | 104.7061 | 1113.7788 | 0 | 0.0005 | 6720280 | 45686.3092
June | 122858.8187 | 105.2322 | 1129.2106 | 0 | 0.0005 | 6813420 | 45966.8204
July | 123482.7281 | 105.7263 | 1142.1561 | 0 | 0.0005 | 6891560 | 46222.2527
August | 135604.8947 | 116.1076 | 1253.8788 | 0 | 0.0006 | 7565670 | 50758.6167
September | 121593.4026 | 104.125 | 1121.7544 | 0 | 0.0005 | 6768450 | 45506.1093
October | 121982.4767 | 104.5072 | 1116.584 | 0 | 0.0005 | 6737220 | 45624.9938
November | 115654.1011 | 99.1922 | 1039.5421 | 0 | 0.0005 | 6272300 | 43199.6807
December | 115253.0945 | 99.0346 | 1002.6096 | 0 | 0.0005 | 6049350 | 42948.2119
Annual Sum or Average | 1432790 | 1228.6419 | 12915.9056 | 0 | 0.0059 | 77931100 | 535297.1678
Minimum of Months | 103924.4117 | 89.2867 | 906.444 | 0 | 0.0004 | 5469130 | 38733.9384
Maximum of Months | 135604.8947 | 116.1076 | 1253.8788 | 0 | 0.0006 | 7565670 | 50758.6167
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1239350000000 | 1094232.041 | 25-JAN-16:10 | 448566.544 | 326066.958 | 28812.988 | 0 | 123435.427 | 0 | 44100.157 | 37694.584 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1121380000000 | 1085989.501 | 13-FEB-08:00 | 448566.544 | 326066.958 | 26557.152 | 0 | 81739.496 | 0 | 43142.789 | 37694.584 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1329460000000 | 1091265.462 | 31-MAR-15:09 | 448566.544 | 326066.958 | 29350.834 | 0 | 119950.049 | 0 | 44081.108 | 37694.584 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1253840000000 | 1128927.432 | 11-APR-15:00 | 448566.544 | 326066.958 | 29627.097 | 0 | 153335.628 | 0 | 48081.237 | 37694.584 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1377910000000 | 1209413.125 | 30-MAY-07:00 | 448566.544 | 326066.958 | 29023.466 | 0 | 198094.678 | 0 | 47744.918 | 37694.584 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
June | 1397010000000 | 1167971.315 | 29-JUN-07:00 | 448566.544 | 326066.958 | 27610.69 | 0 | 159364.477 | 0 | 46446.084 | 37694.584 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
July | 1413030000000 | 1205243.464 | 24-JUL-15:09 | 448566.544 | 326066.958 | 32738.693 | 0 | 225973.607 | 0 | 48647.693 | 37694.584 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1551250000000 | 1292495.201 | 16-AUG-15:00 | 448566.544 | 326066.958 | 33346.735 | 0 | 310374.769 | 0 | 50890.227 | 37694.584 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1387790000000 | 1204527.095 | 08-SEP-07:00 | 448566.544 | 326066.958 | 28461.084 | 0 | 193870.249 | 0 | 47645.698 | 37694.584 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
October | 1381380000000 | 1153261.321 | 19-OCT-15:30 | 448566.544 | 326066.958 | 28500.851 | 0 | 179720.239 | 0 | 47156.76 | 37694.584 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1286060000000 | 1108939.622 | 08-NOV-08:00 | 448566.544 | 326066.958 | 26479.813 | 0 | 104170.184 | 0 | 43739.562 | 37694.584 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1240340000000 | 1094031.719 | 18-DEC-08:00 | 448566.544 | 326066.958 | 27720.318 | 0 | 88391.273 | 0 | 43370.064 | 37694.584 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 15978800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1121380000000 | 1085989.501 |  | 448566.544 | 326066.958 | 26479.813 | 0 | 81739.496 | 0 | 43142.789 | 37694.584 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1551250000000 | 1292495.201 |  | 448566.544 | 326066.958 | 33346.735 | 0 | 310374.769 | 0 | 50890.227 | 37694.584 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 246596.9 | 7903.98 | 0 | 254500.88
Cost per Total Building Area ($/m2) | 5.32 | 0.17 | 0 | 5.49
Cost per Net Conditioned Building Area ($/m2) | 5.32 | 0.17 | 0 | 5.49

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17907.18 | 386.59 | 386.59
Net Site Energy | 17907.18 | 386.59 | 386.59
Total Source Energy | 60188.45 | 1299.39 | 1299.39
Net Source Energy | 60188.45 | 1299.39 | 1299.39
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1345.29 | 0 | 0 | 0 | 0
Cooling | 1735.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 585.21 | 0 | 0 | 0 | 0 | 0
Pumps | 654.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 526.96 | 0 | 0 | 0 | 0 | 18765.73
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 210.25 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16351.63 | 1555.54 | 0 | 0 | 0 | 20269.87
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.252 | 0.162 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.252 | 0.162 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 1390.85 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3124112.88 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2668319.06 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2953706.72
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 294432.58 | 200676.22 | 93756.36 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 3300489.76 | 2257207.01 | 1043282.74 | 0.68 | -
VAV_3_COOLC | Coil:Cooling:Water | 353548.57 | 242488.39 | 111060.17 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 81200.82 | 54849.14 | 26351.68 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 48072.89 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 106063.63 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1215146.68 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 133855.01 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15824.26 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16723.43 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13724.16 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 19294.75 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 171227.34 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 182195.78 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 160427.25 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 204816.14 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17268.16 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18560.83 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17425.24 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 21346.02 | -
VAV_1_HEATC | Coil:Heating:Water | 25873.34 | -
VAV_2_HEATC | Coil:Heating:Water | 233821.04 | -
VAV_3_HEATC | Coil:Heating:Water | 21609.9 | -
VAV_5_HEATC | Coil:Heating:Water | 16582.8 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.13 | 25641.76 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 170.52 | 281006.83 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.38 | 30942.53 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.24 | 8085.65 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28628.17 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15112.7 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 41687.45 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 280594.0476 | 443.3399 | 1774.1253 | 0 | 0.0034 | 8847460 | 116720.859
February | 256472.8829 | 412.5957 | 1690.8612 | 0 | 0.0032 | 8432510 | 107452.7398
March | 298450.4323 | 481.6013 | 1981.4731 | 0 | 0.0037 | 9881870 | 125193.108
April | 294202.2754 | 480.8231 | 2010.3881 | 0 | 0.0038 | 10026300 | 124042.7321
May | 324090.9714 | 530.5767 | 2223.1407 | 0 | 0.0042 | 11087400 | 136738.6549
June | 345272.6058 | 565.682 | 2372.4649 | 0 | 0.0044 | 11832100 | 145720.0144
July | 350923.7952 | 575.0244 | 2412.0825 | 0 | 0.0045 | 12029700 | 148113.7611
August | 370592.0652 | 607.2325 | 2547.0815 | 0 | 0.0048 | 12703000 | 156412.9962
September | 325069.1195 | 532.5647 | 2233.4846 | 0 | 0.0042 | 11139000 | 137191.5374
October | 309107.6034 | 505.3383 | 2113.698 | 0 | 0.004 | 10541500 | 130343.2826
November | 279368.2324 | 451.667 | 1862.8479 | 0 | 0.0035 | 9290310 | 117277.7512
December | 275327.3681 | 437.4911 | 1764.0658 | 0 | 0.0033 | 8797390 | 114787.031
Annual Sum or Average | 3709470 | 6023.9368 | 24985.7136 | 0 | 0.047 | 124609000 | 1559990
Minimum of Months | 256472.8829 | 412.5957 | 1690.8612 | 0 | 0.0032 | 8432510 | 107452.7398
Maximum of Months | 370592.0652 | 607.2325 | 2547.0815 | 0 | 0.0048 | 12703000 | 156412.9962
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1161000000000 | 1049958.033 | 18-JAN-16:10 | 448566.544 | 326066.958 | 30628.696 | 0 | 76054.72 | 0 | 44318.33 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1106550000000 | 1082130.929 | 08-FEB-16:10 | 448566.544 | 326066.958 | 31269.084 | 0 | 106790.771 | 0 | 45114.786 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1296740000000 | 1103332.982 | 31-MAR-15:30 | 448566.544 | 326066.958 | 31803.536 | 0 | 126971.896 | 0 | 45601.262 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1315690000000 | 1162931.731 | 21-APR-15:30 | 448566.544 | 326066.958 | 37286.398 | 0 | 179771.514 | 0 | 46917.531 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1454930000000 | 1217357.564 | 31-MAY-15:00 | 448566.544 | 326066.958 | 48875.212 | 0 | 220763.665 | 0 | 48762.4 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1552660000000 | 1311203.778 | 27-JUN-15:00 | 448566.544 | 326066.958 | 64084.701 | 0 | 296735.184 | 0 | 51427.605 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1578590000000 | 1319255.764 | 25-JUL-15:00 | 448566.544 | 326066.958 | 61321.298 | 0 | 302981.374 | 0 | 55996.804 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1666940000000 | 1337132.801 | 07-AUG-15:00 | 448566.544 | 326066.958 | 56994.526 | 0 | 327150.972 | 0 | 54031.017 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1461700000000 | 1285923.279 | 01-SEP-15:09 | 448566.544 | 326066.958 | 57031.409 | 0 | 271098.656 | 0 | 58836.927 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1383300000000 | 1184919.205 | 03-OCT-15:09 | 448566.544 | 326066.958 | 44175.988 | 0 | 193966.313 | 0 | 47820.617 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1219110000000 | 1086153.518 | 10-NOV-16:10 | 448566.544 | 326066.958 | 31423.711 | 0 | 110612.766 | 0 | 45160.754 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1154430000000 | 1074292.527 | 05-DEC-16:10 | 448566.544 | 326066.958 | 30747.94 | 0 | 99730.027 | 0 | 44858.273 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 16351600000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1106550000000 | 1049958.033 |  | 448566.544 | 326066.958 | 30628.696 | 0 | 76054.72 | 0 | 44318.33 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1666940000000 | 1337132.801 |  | 448566.544 | 326066.958 | 64084.701 | 0 | 327150.972 | 0 | 58836.927 | 38767.401 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 437307.31 | 11944.95 | 0 | 449252.26
Cost per Total Building Area ($/m2) | 9.44 | 0.26 | 0 | 9.7
Cost per Net Conditioned Building Area ($/m2) | 9.44 | 0.26 | 0 | 9.7

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18439.32 | 398.08 | 398.08
Net Site Energy | 18439.32 | 398.08 | 398.08
Total Source Energy | 50033.32 | 1080.16 | 1080.16
Net Source Energy | 50033.32 | 1080.16 | 1080.16
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3252.16 | 0 | 0 | 0 | 0
Cooling | 634.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 508.13 | 0 | 0 | 0 | 0 | 0
Pumps | 519.17 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 414.24 | 0 | 0 | 0 | 0 | 4961.94
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 260.76 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14926.4 | 3512.92 | 0 | 0 | 0 | 6466.07
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.39 | 0.223 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.39 | 0.223 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.39 | 0.223 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 1390.85 | 5.83 | 0.39 | 0.223
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3032327.47 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2720968.25 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2866927.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 337924.92 | 241437.69 | 96487.23 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 3715177.67 | 2658743.15 | 1056434.52 | 0.72 | -
VAV_3_COOLC | Coil:Cooling:Water | 364284.35 | 260707.14 | 103577.21 | 0.72 | -
VAV_5_COOLC | Coil:Cooling:Water | 73615.25 | 52850.27 | 20764.99 | 0.72 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 43089.83 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 99099.23 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1170973.29 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 115660.96 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33000.92 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20150.22 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11803.77 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25521.16 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 343046.93 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 200683.83 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 120780.22 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 254336.61 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33212.28 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19208.85 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11969.63 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24912.35 | -
VAV_1_HEATC | Coil:Heating:Water | 16814.39 | -
VAV_2_HEATC | Coil:Heating:Water | 144708.28 | -
VAV_3_HEATC | Coil:Heating:Water | 14956.29 | -
VAV_5_HEATC | Coil:Heating:Water | 13949.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.46 | 26185.33 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 170.37 | 280759.08 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.71 | 28128.28 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.51 | 6700.57 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27787.08 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15410.89 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 40462.69 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 130239.6922 | 113.0688 | 926.0468 | 0 | 0.0005 | 5586660 | 47901.5088
February | 111092.0202 | 95.9516 | 878.2741 | 0 | 0.0004 | 5298840 | 41128.7145
March | 129526.5844 | 112.002 | 1001.084 | 0 | 0.0005 | 6039690 | 47883.6366
April | 117611.9385 | 101.4337 | 956.5247 | 0 | 0.0005 | 5771050 | 43624.0088
May | 124871.5917 | 107.4634 | 1056.9676 | 0 | 0.0005 | 6377220 | 46443.0343
June | 122772.5972 | 105.5555 | 1057.3581 | 0 | 0.0005 | 6379640 | 45717.7602
July | 120315.8279 | 103.3286 | 1056.7152 | 0 | 0.0005 | 6375840 | 44865.5065
August | 129677.8696 | 111.398 | 1133.717 | 0 | 0.0005 | 6840420 | 48340.6544
September | 119737.5171 | 102.7964 | 1058.0034 | 0 | 0.0005 | 6383630 | 44669.2823
October | 122398.9451 | 105.2225 | 1056.2441 | 0 | 0.0005 | 6372930 | 45585.0396
November | 121631.401 | 104.9511 | 980.1117 | 0 | 0.0005 | 5913330 | 45087.1145
December | 126818.2367 | 110.0806 | 904.9041 | 0 | 0.0005 | 5459120 | 46652.8318
Annual Sum or Average | 1476690 | 1273.2522 | 12065.9509 | 0 | 0.0058 | 72798400 | 547899.0922
Minimum of Months | 111092.0202 | 95.9516 | 878.2741 | 0 | 0.0004 | 5298840 | 41128.7145
Maximum of Months | 130239.6922 | 113.0688 | 1133.717 | 0 | 0.0005 | 6840420 | 48340.6544
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1145480000000 | 1007853.744 | 06-JAN-16:10 | 448566.544 | 326066.958 | 29423.605 | 0 | 37925.514 | 0 | 42687.311 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1086460000000 | 1105839.186 | 15-FEB-16:10 | 448566.544 | 326066.958 | 33443.025 | 0 | 128617.632 | 0 | 45961.215 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1238360000000 | 1059460.368 | 20-MAR-15:09 | 448566.544 | 326066.958 | 30880.876 | 0 | 85127.477 | 0 | 45634.701 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1183280000000 | 1097157.214 | 13-APR-15:09 | 448566.544 | 326066.958 | 33718.164 | 0 | 121335.09 | 0 | 44286.646 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1307570000000 | 1108307.356 | 25-MAY-15:50 | 448566.544 | 326066.958 | 31425.286 | 0 | 133382.656 | 0 | 45682.1 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1308070000000 | 1132580.797 | 16-JUN-15:00 | 448566.544 | 326066.958 | 34390.401 | 0 | 153293.726 | 0 | 47079.356 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1307290000000 | 1160647.319 | 03-JUL-15:09 | 448566.544 | 326066.958 | 35732.547 | 0 | 179920.995 | 0 | 47176.464 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1402540000000 | 1119968.598 | 14-AUG-15:09 | 448566.544 | 326066.958 | 31617.292 | 0 | 144156.915 | 0 | 46377.077 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1308880000000 | 1218856.971 | 28-SEP-15:09 | 448566.544 | 326066.958 | 46565.45 | 0 | 223762.099 | 0 | 50712.108 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1306690000000 | 1134258.395 | 13-OCT-15:09 | 448566.544 | 326066.958 | 36527.772 | 0 | 152887.708 | 0 | 47025.601 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1212450000000 | 1080816.724 | 16-NOV-16:10 | 448566.544 | 326066.958 | 29423.605 | 0 | 108609.622 | 0 | 44966.184 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1119330000000 | 1004885.953 | 12-DEC-08:09 | 448566.544 | 326066.958 | 29423.605 | 0 | 0.157 | 0 | 40978.283 | 37628.427 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14926400000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1086460000000 | 1004885.953 |  | 448566.544 | 326066.958 | 29423.605 | 0 | 0.157 | 0 | 40978.283 | 37628.427 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1402540000000 | 1218856.971 |  | 448566.544 | 326066.958 | 46565.45 | 0 | 223762.099 | 0 | 50712.108 | 37628.427 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 616534.65 | 29982.03 | 0 | 646516.68
Cost per Total Building Area ($/m2) | 13.31 | 0.65 | 0 | 13.96
Cost per Net Conditioned Building Area ($/m2) | 13.31 | 0.65 | 0 | 13.96

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21300.73 | 459.86 | 459.86
Net Site Energy | 21300.73 | 459.86 | 459.86
Total Source Energy | 65090.56 | 1405.23 | 1405.23
Net Source Energy | 65090.56 | 1405.23 | 1405.23
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4196.13 | 0 | 0 | 0 | 0
Cooling | 1965.51 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 536.73 | 0 | 0 | 0 | 0 | 0
Pumps | 913.14 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 574.16 | 0 | 0 | 0 | 0 | 11092.61
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 264.76 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16839.84 | 4460.89 | 0 | 0 | 0 | 12596.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3611471.63 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3094815.27 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3414482.27
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 346527.2 | 240648.27 | 105878.92 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 3787114.87 | 2638211.26 | 1148903.61 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 402979.03 | 281784.51 | 121194.52 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 128085.72 | 88784.35 | 39301.38 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 68788.66 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 109530.98 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1214457.57 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 133211.81 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16021.72 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20751.82 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14039.82 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 23674.44 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 173251.7 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 222363.48 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 156113.61 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 253918.02 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17157.96 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22426.01 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17302.22 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26329.46 | -
VAV_1_HEATC | Coil:Heating:Water | 47376.73 | -
VAV_2_HEATC | Coil:Heating:Water | 455790.38 | -
VAV_3_HEATC | Coil:Heating:Water | 44070.38 | -
VAV_5_HEATC | Coil:Heating:Water | 25345.35 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.08 | 25544.39 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 165.51 | 272744.2 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.73 | 29849.34 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.64 | 10572.86 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33094.14 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17528.26 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 48190.65 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 271597.6431 | 476.1534 | 1269.027 | 0 | 0.0052 | 78907.8684 | 114996.6082
February | 233107.6762 | 420.9431 | 1156.9268 | 0 | 0.0047 | 71942.1429 | 99821.4623
March | 254090.4237 | 480.8 | 1382.3547 | 0 | 0.0056 | 85967.9384 | 110815.2531
April | 234925.1722 | 453.9009 | 1329.8034 | 0 | 0.0054 | 82702.8419 | 103313.2093
May | 253325.9101 | 500.335 | 1494.0464 | 0 | 0.006 | 92920.8071 | 112400.3205
June | 267842.1698 | 533.7489 | 1605.8505 | 0 | 0.0065 | 99875.7759 | 119274.888
July | 270998.2623 | 540.6643 | 1628.229 | 0 | 0.0066 | 101267.792 | 120737.5859
August | 290051.9703 | 578.4168 | 1741.2662 | 0 | 0.007 | 108298.0729 | 129202.6785
September | 247110.9551 | 490.1236 | 1468.7865 | 0 | 0.0059 | 91350.4105 | 109831.4423
October | 246307.5747 | 482.0644 | 1428.3102 | 0 | 0.0058 | 88831.0867 | 108883.1601
November | 239072.3454 | 455.3856 | 1317.2334 | 0 | 0.0053 | 81919.0505 | 104540.1052
December | 254759.5173 | 458.3347 | 1254.9602 | 0 | 0.0052 | 78037.6255 | 108937.1285
Annual Sum or Average | 3063190 | 5870.8706 | 17076.7943 | 0 | 0.0693 | 1062020 | 1342750
Minimum of Months | 233107.6762 | 420.9431 | 1156.9268 | 0 | 0.0047 | 71942.1429 | 99821.4623
Maximum of Months | 290051.9703 | 578.4168 | 1741.2662 | 0 | 0.007 | 108298.0729 | 129202.6785
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1251200000000 | 1092724.335 | 09-JAN-08:00 | 448566.544 | 326066.958 | 29159.953 | 0 | 69184.959 | 0 | 52708.863 | 44815.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1140740000000 | 1069143.534 | 15-FEB-16:10 | 448566.544 | 326066.958 | 29159.953 | 0 | 83971.458 | 0 | 51008.158 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1363140000000 | 1163242.245 | 09-MAR-16:10 | 448566.544 | 326066.958 | 29784.623 | 0 | 174321.637 | 0 | 54132.018 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1311370000000 | 1159657.35 | 04-APR-07:00 | 448566.544 | 326066.958 | 29159.953 | 0 | 135718.765 | 0 | 53108.072 | 44815.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
May | 1473390000000 | 1284046.901 | 31-MAY-15:00 | 448566.544 | 326066.958 | 31690.579 | 0 | 290361.655 | 0 | 56990.699 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1583670000000 | 1397834.61 | 30-JUN-15:00 | 448566.544 | 326066.958 | 42467.939 | 0 | 390768.768 | 0 | 59593.936 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1605740000000 | 1436637.55 | 25-JUL-15:39 | 448566.544 | 326066.958 | 46088.195 | 0 | 424959.796 | 0 | 60585.593 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1717220000000 | 1478965.832 | 09-AUG-15:09 | 448566.544 | 326066.958 | 42855.54 | 0 | 470074.962 | 0 | 61031.364 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1448490000000 | 1249119.059 | 05-SEP-15:09 | 448566.544 | 326066.958 | 40104.468 | 0 | 247346.558 | 0 | 56664.067 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1408540000000 | 1226527.037 | 03-OCT-07:00 | 448566.544 | 326066.958 | 29159.953 | 0 | 200801.678 | 0 | 54894.847 | 44815.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1298940000000 | 1181847.92 | 03-NOV-15:09 | 448566.544 | 326066.958 | 33312.172 | 0 | 188745.067 | 0 | 54786.714 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1237400000000 | 1052607.438 | 08-DEC-08:00 | 448566.544 | 326066.958 | 29159.953 | 0 | 31740.909 | 0 | 50036.017 | 44815.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 16839800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1140740000000 | 1052607.438 |  | 448566.544 | 326066.958 | 29159.953 | 0 | 31740.909 | 0 | 50036.017 | 44815.08 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1717220000000 | 1478965.832 |  | 448566.544 | 326066.958 | 46088.195 | 0 | 470074.962 | 0 | 61031.364 | 44815.08 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 325187.34 | 43276.29 | 0 | 368463.63
Cost per Total Building Area ($/m2) | 7.02 | 0.93 | 0 | 7.95
Cost per Net Conditioned Building Area ($/m2) | 7.02 | 0.93 | 0 | 7.95

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18048.59 | 389.65 | 389.65
Net Site Energy | 18048.59 | 389.65 | 389.65
Total Source Energy | 54109.57 | 1168.16 | 1168.16
Net Source Energy | 54109.57 | 1168.16 | 1168.16
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2334.74 | 0 | 0 | 0 | 0
Cooling | 1104.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 630.06 | 0 | 0 | 0 | 0 | 0
Pumps | 497.85 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 371.61 | 0 | 0 | 0 | 0 | 11038.61
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 259.89 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15453.96 | 2594.63 | 0 | 0 | 0 | 12542.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2886113.87 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2739977.07 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2728689.48
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 261956.41 | 169327.14 | 92629.27 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water | 2914097.56 | 1888314.67 | 1025782.88 | 0.65 | -
VAV_3_COOLC | Coil:Cooling:Water | 296911.21 | 192556.26 | 104354.94 | 0.65 | -
VAV_5_COOLC | Coil:Cooling:Water | 79997.66 | 51536.92 | 28460.74 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 55166.09 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 104297.44 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1189101.38 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 120685.92 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13523.25 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18354.03 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12710.73 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 22082.06 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 144822.72 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 196113.23 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 133822.44 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 238023.01 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15114.47 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19340.59 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14193.45 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24576.88 | -
VAV_1_HEATC | Coil:Heating:Water | 33851.32 | -
VAV_2_HEATC | Coil:Heating:Water | 317667.86 | -
VAV_3_HEATC | Coil:Heating:Water | 31346.62 | -
VAV_5_HEATC | Coil:Heating:Water | 19576.91 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.93 | 28493.61 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 188.3 | 310296.56 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.2 | 32317.45 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.46 | 10246.11 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26447.24 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15518.55 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 38511.65 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 338308.7501 | 565.675 | 1401.0616 | 0 | 0.0055 | 1456710 | 142454.0688
February | 296572.0672 | 503.5853 | 1269.8739 | 0 | 0.005 | 1320370 | 125634.688
March | 344934.0173 | 591.6013 | 1508.8665 | 0 | 0.0059 | 1568900 | 146700.2911
April | 324275.9464 | 563.0693 | 1455.8409 | 0 | 0.0057 | 1513810 | 138591.1315
May | 371779.572 | 650.5699 | 1696.2575 | 0 | 0.0066 | 1763840 | 159385.5399
June | 387087.3336 | 678.096 | 1770.1013 | 0 | 0.0069 | 1840630 | 166020.6456
July | 392149.7907 | 687.2264 | 1794.6696 | 0 | 0.007 | 1866170 | 168217.6229
August | 413015.9569 | 723.6971 | 1889.6415 | 0 | 0.0074 | 1964930 | 177158.9714
September | 361683.5551 | 633.2154 | 1651.8842 | 0 | 0.0064 | 1717700 | 155087.908
October | 341973.4589 | 594.2623 | 1537.8018 | 0 | 0.006 | 1599040 | 146200.2532
November | 321065.0654 | 549.7101 | 1399.2958 | 0 | 0.0055 | 1454970 | 136455.3375
December | 328361.5736 | 551.1095 | 1371.0535 | 0 | 0.0054 | 1425530 | 138468.2776
Annual Sum or Average | 4221210 | 7291.8177 | 18746.348 | 0 | 0.0733 | 19492600 | 1800370
Minimum of Months | 296572.0672 | 503.5853 | 1269.8739 | 0 | 0.005 | 1320370 | 125634.688
Maximum of Months | 413015.9569 | 723.6971 | 1889.6415 | 0 | 0.0074 | 1964930 | 177158.9714
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1154900000000 | 1025223.993 | 26-JAN-16:10 | 448566.544 | 326066.958 | 39452.728 | 0 | 48945.533 | 0 | 40822.797 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1046800000000 | 1082028.984 | 14-FEB-16:10 | 448566.544 | 326066.958 | 40665.385 | 0 | 102616.6 | 0 | 42744.063 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1243840000000 | 1082175.891 | 02-MAR-16:10 | 448566.544 | 326066.958 | 40440.403 | 0 | 103016.883 | 0 | 42715.668 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1200170000000 | 1120127.406 | 21-APR-15:00 | 448566.544 | 326066.958 | 42869.883 | 0 | 137054.2 | 0 | 44200.388 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1398390000000 | 1181129.908 | 31-MAY-15:00 | 448566.544 | 326066.958 | 53489.019 | 0 | 185186.26 | 0 | 46451.692 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1459270000000 | 1247838.764 | 29-JUN-15:00 | 448566.544 | 326066.958 | 70706.061 | 0 | 221597.041 | 0 | 59532.726 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1479530000000 | 1260269.323 | 03-JUL-15:30 | 448566.544 | 326066.958 | 66763.954 | 0 | 243486.71 | 0 | 54015.723 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1557820000000 | 1271985.569 | 04-AUG-08:00 | 448566.544 | 326066.958 | 42628.842 | 0 | 282276.574 | 0 | 51077.217 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1361810000000 | 1215113.865 | 05-SEP-15:09 | 448566.544 | 326066.958 | 46191.801 | 0 | 223996.91 | 0 | 48922.219 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1267740000000 | 1139534.444 | 11-OCT-15:39 | 448566.544 | 326066.958 | 43111.896 | 0 | 149572.312 | 0 | 50847.3 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1153510000000 | 1068668.963 | 08-NOV-16:10 | 448566.544 | 326066.958 | 38161.485 | 0 | 92496.703 | 0 | 42007.838 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1130170000000 | 997519.681 | 05-DEC-16:10 | 448566.544 | 326066.958 | 37567.876 | 0 | 23994.367 | 0 | 39954.502 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 15454000000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1046800000000 | 997519.681 |  | 448566.544 | 326066.958 | 37567.876 | 0 | 23994.367 | 0 | 39954.502 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1557820000000 | 1271985.569 |  | 448566.544 | 326066.958 | 70706.061 | 0 | 282276.574 | 0 | 59532.726 | 35814.049 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 158714.82 | 17892.72 | 0 | 176607.54
Cost per Total Building Area ($/m2) | 3.43 | 0.39 | 0 | 3.81
Cost per Net Conditioned Building Area ($/m2) | 3.43 | 0.39 | 0 | 3.81

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19359.07 | 417.94 | 417.94
Net Site Energy | 19359.07 | 417.94 | 417.94
Total Source Energy | 30604.75 | 660.72 | 660.72
Net Source Energy | 30604.75 | 660.72 | 660.72
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4519.88 | 0 | 0 | 0 | 0
Cooling | 531.53 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 510.03 | 0 | 0 | 0 | 0 | 0
Pumps | 382.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 286.28 | 0 | 0 | 0 | 0 | 4036.61
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 278.2 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14560.99 | 4798.08 | 0 | 0 | 0 | 5540.74
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3067341.55 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2918500.69 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2900032.01
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 326891.38 | 231086.95 | 95804.43 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 3654296.65 | 2588691.91 | 1065604.74 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 363967.47 | 258179.84 | 105787.64 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 88136.75 | 62425.09 | 25711.65 | 0.71 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 51115.49 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 105046.14 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1212125.9 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 120701.75 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25468.6 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19082.41 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12539.08 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 22197.75 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 279501.33 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 202705.85 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 133752.82 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 239514.31 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27801.09 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20020.57 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13648.88 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24530.18 | -
VAV_1_HEATC | Coil:Heating:Water | 33376.92 | -
VAV_2_HEATC | Coil:Heating:Water | 308909.63 | -
VAV_3_HEATC | Coil:Heating:Water | 30891.21 | -
VAV_5_HEATC | Coil:Heating:Water | 20129.97 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.24 | 25816.39 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 170.91 | 281646.92 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.09 | 28762.37 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.23 | 8059.41 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28107.94 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16529.66 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 40929.91 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 99447.1498 | 128.3751 | 243.7107 | 0 | 0.001 | 3218420 | 38499.8792
February | 79190.6239 | 106.4634 | 221.1229 | 0 | 0.0009 | 2920880 | 31111.5971
March | 87355.6796 | 119.7103 | 258.4147 | 0 | 0.0011 | 3413830 | 34562.5049
April | 74092.7323 | 105.0467 | 241.6013 | 0 | 0.001 | 3192230 | 29691.0797
May | 70726.8375 | 106.9887 | 273.4942 | 0 | 0.0011 | 3614520 | 29061.3556
June | 69351.2083 | 107.2308 | 283.0073 | 0 | 0.0011 | 3740510 | 28744.9211
July | 67937.2451 | 106.9084 | 289.1376 | 0 | 0.0011 | 3821730 | 28358.4768
August | 72921.3085 | 114.6689 | 309.822 | 0 | 0.0012 | 4095120 | 30430.0842
September | 69296.801 | 105.4998 | 272.27 | 0 | 0.0011 | 3598420 | 28545.9829
October | 76036.075 | 109.1488 | 256.5382 | 0 | 0.001 | 3389770 | 30614.093
November | 85900.6419 | 115.5451 | 240.2471 | 0 | 0.001 | 3173510 | 33754.2677
December | 97524.7954 | 125.7628 | 238.1647 | 0 | 0.001 | 3145160 | 37741.6556
Annual Sum or Average | 949781.0982 | 1351.3488 | 3127.5307 | 0 | 0.0127 | 41324100 | 381115.8977
Minimum of Months | 67937.2451 | 105.0467 | 221.1229 | 0 | 0.0009 | 2920880 | 28358.4768
Maximum of Months | 99447.1498 | 128.3751 | 309.822 | 0 | 0.0012 | 4095120 | 38499.8792
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1134040000000 | 968108.322 | 30-JAN-08:09 | 448566.544 | 326066.958 | 29639.85 | 0 | 0.099 | 0 | 41612.892 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1029200000000 | 1024493.516 | 21-FEB-16:10 | 448566.544 | 326066.958 | 29639.85 | 0 | 53488.202 | 0 | 43113.657 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1202900000000 | 1074941.229 | 29-MAR-15:30 | 448566.544 | 326066.958 | 30348.464 | 0 | 102285.994 | 0 | 44054.964 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1124820000000 | 1048682.029 | 14-APR-15:09 | 448566.544 | 326066.958 | 29639.85 | 0 | 77244.407 | 0 | 43545.965 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1273620000000 | 1130707.214 | 05-MAY-15:00 | 448566.544 | 326066.958 | 30181.458 | 0 | 155597.987 | 0 | 46675.962 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1318010000000 | 1137376.598 | 28-JUN-15:30 | 448566.544 | 326066.958 | 33276.219 | 0 | 158591.718 | 0 | 47256.854 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1346630000000 | 1187627.25 | 31-JUL-15:00 | 448566.544 | 326066.958 | 35543.72 | 0 | 205532.275 | 0 | 48299.447 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1442960000000 | 1165128.226 | 07-AUG-15:09 | 448566.544 | 326066.958 | 35491.697 | 0 | 183621.052 | 0 | 47763.67 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1267940000000 | 1173129.639 | 01-SEP-15:00 | 448566.544 | 326066.958 | 33586.567 | 0 | 193485.705 | 0 | 47805.56 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1194420000000 | 1095166.498 | 17-OCT-15:09 | 448566.544 | 326066.958 | 32285.951 | 0 | 120096.109 | 0 | 44532.631 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1118220000000 | 1030697.904 | 03-NOV-15:09 | 448566.544 | 326066.958 | 29639.85 | 0 | 59096.244 | 0 | 43710.004 | 38062.92 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1108230000000 | 967951.102 | 14-DEC-08:20 | 448566.544 | 326066.958 | 29639.85 | 0 | 0.323 | 0 | 41455.449 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14561000000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1029200000000 | 967951.102 |  | 448566.544 | 326066.958 | 29639.85 | 0 | 0.099 | 0 | 41455.449 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1442960000000 | 1187627.25 |  | 448566.544 | 326066.958 | 35543.72 | 0 | 205532.275 | 0 | 48299.447 | 38062.92 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 291134.79 | 40365.27 | 0 | 331500.06
Cost per Total Building Area ($/m2) | 6.29 | 0.87 | 0 | 7.16
Cost per Net Conditioned Building Area ($/m2) | 6.29 | 0.87 | 0 | 7.16

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22589.28 | 487.67 | 487.67
Net Site Energy | 22589.28 | 487.67 | 487.67
Total Source Energy | 63381.39 | 1368.33 | 1368.33
Net Source Energy | 63381.39 | 1368.33 | 1368.33
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6526.09 | 0 | 0 | 0 | 0
Cooling | 1319.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 605.19 | 0 | 0 | 0 | 0 | 0
Pumps | 620.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 379.67 | 0 | 0 | 0 | 0 | 7714.07
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 287.35 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15775.84 | 6813.44 | 0 | 0 | 0 | 9218.21
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3885354.31 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3578444.02 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3673425.89
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 370879.48 | 257986.53 | 112892.95 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 4037795.3 | 2820257.86 | 1217537.43 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 424877.27 | 297670.94 | 127206.33 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 138647.15 | 96276.14 | 42371.02 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 76981.79 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 126598.43 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1403046.17 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 148712.53 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16954.5 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20722.11 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15822.03 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 23573.24 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 176980.67 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 222553.2 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 177552.33 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 253027.75 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19186.69 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22425.5 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 19386.12 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26030.86 | -
VAV_1_HEATC | Coil:Heating:Water | 63417.48 | -
VAV_2_HEATC | Coil:Heating:Water | 616927.39 | -
VAV_3_HEATC | Coil:Heating:Water | 60485.33 | -
VAV_5_HEATC | Coil:Heating:Water | 32709.99 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.97 | 28569.93 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 186.09 | 306662.47 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.64 | 33068.75 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.41 | 12034.35 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 35603.89 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20267.42 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 51845.28 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 486568.6954 | 808.8035 | 2202.9446 | 0 | 0.0068 | 507042.6795 | 203504.9762
February | 419376.9543 | 710.0388 | 1976.2176 | 0 | 0.0061 | 454878.1571 | 176638.1655
March | 459641.6256 | 798.0112 | 2284.6581 | 0 | 0.007 | 525903.6566 | 195490.5168
April | 418742.7604 | 741.3003 | 2167.0703 | 0 | 0.0066 | 498856.6504 | 179462.643
May | 483235.0581 | 871.1018 | 2594.5325 | 0 | 0.0078 | 597279.3185 | 208596.8992
June | 534160.764 | 970.3581 | 2912.6494 | 0 | 0.0088 | 670521.9074 | 231292.6764
July | 540751.351 | 983.1032 | 2953.2177 | 0 | 0.0089 | 679862.1416 | 234220.2799
August | 573794.0408 | 1042.5557 | 3129.9571 | 0 | 0.0094 | 720548.6294 | 248473.0552
September | 490314.0166 | 886.9601 | 2651.1083 | 0 | 0.008 | 610307.5702 | 211948.8037
October | 452045.9805 | 806.5606 | 2377.2092 | 0 | 0.0072 | 547238.9936 | 194338.263
November | 426262.5915 | 742.9547 | 2136.1006 | 0 | 0.0065 | 491711.4496 | 181570.8303
December | 460689.7848 | 776.2533 | 2148.5261 | 0 | 0.0066 | 494533.828 | 193682.032
Annual Sum or Average | 5745580 | 10138.0012 | 29534.1915 | 0 | 0.0897 | 6798680 | 2459220
Minimum of Months | 418742.7604 | 710.0388 | 1976.2176 | 0 | 0.0061 | 454878.1571 | 176638.1655
Maximum of Months | 573794.0408 | 1042.5557 | 3129.9571 | 0 | 0.0094 | 720548.6294 | 248473.0552
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1176550000000 | 982955.993 | 09-JAN-08:50 | 448566.544 | 326066.958 | 32743.467 | 0 | 0 | 0 | 53357.046 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1055510000000 | 982384.054 | 27-FEB-08:09 | 448566.544 | 326066.958 | 32743.467 | 0 | 0 | 0 | 52785.107 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1220320000000 | 1125583.795 | 31-MAR-15:50 | 448566.544 | 326066.958 | 32743.467 | 0 | 128920.511 | 0 | 55517.215 | 48213.715 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1157560000000 | 1181428.032 | 10-APR-07:00 | 448566.544 | 326066.958 | 32743.467 | 0 | 145757.175 | 0 | 57858.196 | 48213.715 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
May | 1385940000000 | 1332453.236 | 30-MAY-08:00 | 448566.544 | 326066.958 | 33011.846 | 0 | 328448.182 | 0 | 62590.607 | 48213.715 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1555900000000 | 1362630.348 | 29-JUN-07:00 | 448566.544 | 326066.958 | 32743.467 | 0 | 322019.746 | 0 | 62797.941 | 48213.715 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
July | 1577570000000 | 1363208.679 | 13-JUL-15:09 | 448566.544 | 326066.958 | 40674.297 | 0 | 351781.55 | 0 | 62350.231 | 48213.715 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1671980000000 | 1430682.776 | 04-AUG-15:50 | 448566.544 | 326066.958 | 39846.89 | 0 | 418780.968 | 0 | 63652.317 | 48213.715 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1416170000000 | 1297706.952 | 07-SEP-15:09 | 448566.544 | 326066.958 | 34005.216 | 0 | 293606.973 | 0 | 61692.162 | 48213.715 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1269830000000 | 1226460.501 | 31-OCT-07:00 | 448566.544 | 326066.958 | 32743.467 | 0 | 189745 | 0 | 58902.838 | 48213.715 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1140980000000 | 1235334.426 | 02-NOV-07:00 | 448566.544 | 326066.958 | 32743.467 | 0 | 198112.578 | 0 | 59409.186 | 48213.715 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1147530000000 | 982493.856 | 11-DEC-08:09 | 448566.544 | 326066.958 | 32743.467 | 0 | 0 | 0 | 52894.909 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 15775800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1055510000000 | 982384.054 |  | 448566.544 | 326066.958 | 32743.467 | 0 | 0 | 0 | 52785.107 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1671980000000 | 1430682.776 |  | 448566.544 | 326066.958 | 40674.297 | 0 | 418780.968 | 0 | 63652.317 | 48213.715 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 386311.29 | 56986.66 | 0 | 443297.95
Cost per Total Building Area ($/m2) | 8.34 | 1.23 | 0 | 9.57
Cost per Net Conditioned Building Area ($/m2) | 8.34 | 1.23 | 0 | 9.57

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19083.62 | 411.99 | 411.99
Net Site Energy | 19083.62 | 411.99 | 411.99
Total Source Energy | 54150.26 | 1169.04 | 1169.04
Net Source Energy | 54150.26 | 1169.04 | 1169.04
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3832.95 | 0 | 0 | 0 | 0
Cooling | 794.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.24 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 610.03 | 0 | 0 | 0 | 0 | 0
Pumps | 424.89 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 285.09 | 0 | 0 | 0 | 0 | 7971.2
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 286.18 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14964.49 | 4119.13 | 0 | 0 | 0 | 9475.33
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2810534.56 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 2941529.36 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2657232.68
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 257092.62 | 164255.52 | 92837.11 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water | 2875730.47 | 1841613.72 | 1034116.74 | 0.64 | -
VAV_3_COOLC | Coil:Cooling:Water | 288515.12 | 184869.7 | 103645.42 | 0.64 | -
VAV_5_COOLC | Coil:Cooling:Water | 77147.3 | 49283.61 | 27863.68 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 54102.1 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 102871.25 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1181441.52 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 118276.98 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13648.77 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17932.89 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12237.74 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 21736.19 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 147917.71 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 189276.95 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 128467.77 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 233930.57 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14895.58 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18510.15 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13223.09 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 23927.13 | -
VAV_1_HEATC | Coil:Heating:Water | 50250.09 | -
VAV_2_HEATC | Coil:Heating:Water | 483989.05 | -
VAV_3_HEATC | Coil:Heating:Water | 48316.62 | -
VAV_5_HEATC | Coil:Heating:Water | 26194.76 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.71 | 28121.85 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 186.57 | 307460.02 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.73 | 31529.01 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.37 | 10066.99 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25754.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16660.09 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 37503.13 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 356889.1959 | 583.9514 | 1408.7765 | 0 | 0.0056 | 1464640 | 149023.1676
February | 308883.1548 | 514.1826 | 1266.8004 | 0 | 0.005 | 1317100 | 129838.9227
March | 347759.4785 | 589.8986 | 1485.7813 | 0 | 0.0058 | 1544860 | 147259.6017
April | 319508.5976 | 550.8585 | 1413.1513 | 0 | 0.0055 | 1469400 | 136167.8608
May | 348001.7505 | 605.0891 | 1566.8108 | 0 | 0.0061 | 1629210 | 148811.91
June | 363894.2714 | 635.7603 | 1654.8066 | 0 | 0.0064 | 1720730 | 155905.832
July | 381189.6953 | 667.552 | 1741.9816 | 0 | 0.0068 | 1811380 | 163470.3147
August | 395706.2341 | 692.7853 | 1807.2994 | 0 | 0.007 | 1879300 | 169677.1255
September | 343602.0221 | 599.5755 | 1558.565 | 0 | 0.0061 | 1620650 | 147140.0622
October | 338673.3587 | 585.8574 | 1508.5092 | 0 | 0.0059 | 1568560 | 144527.477
November | 323509.1846 | 547.3751 | 1374.6598 | 0 | 0.0054 | 1429310 | 136854.59
December | 343600.2922 | 563.975 | 1365.8858 | 0 | 0.0054 | 1420070 | 143647.5894
Annual Sum or Average | 4171220 | 7136.8608 | 18153.0278 | 0 | 0.0711 | 18875200 | 1772320
Minimum of Months | 308883.1548 | 514.1826 | 1266.8004 | 0 | 0.005 | 1317100 | 129838.9227
Maximum of Months | 395706.2341 | 692.7853 | 1807.2994 | 0 | 0.007 | 1879300 | 169677.1255
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1161190000000 | 1017670.536 | 27-JAN-16:10 | 448566.544 | 326066.958 | 32795.796 | 0 | 50118.912 | 0 | 39690.762 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1044210000000 | 967156.075 | 08-FEB-08:20 | 448566.544 | 326066.958 | 32471.623 | 0 | 0 | 0 | 37828.972 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1224780000000 | 1073929.784 | 30-MAR-15:09 | 448566.544 | 326066.958 | 35395.135 | 0 | 101954.995 | 0 | 41514.588 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1164960000000 | 1101093.207 | 26-APR-15:00 | 448566.544 | 326066.958 | 39091.986 | 0 | 124580.519 | 0 | 42355.636 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1291650000000 | 1146556.801 | 24-MAY-15:00 | 448566.544 | 326066.958 | 44596.877 | 0 | 160333.763 | 0 | 46561.096 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1364210000000 | 1188898.707 | 27-JUN-15:39 | 448566.544 | 326066.958 | 50548.857 | 0 | 188115.403 | 0 | 55169.381 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1436090000000 | 1236288.471 | 17-JUL-15:09 | 448566.544 | 326066.958 | 83067.94 | 0 | 210278.526 | 0 | 47876.939 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1489930000000 | 1210806.136 | 30-AUG-15:30 | 448566.544 | 326066.958 | 55832.004 | 0 | 207711.351 | 0 | 52197.716 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1284870000000 | 1171151.469 | 01-SEP-15:00 | 448566.544 | 326066.958 | 48087.148 | 0 | 174408.243 | 0 | 53591.013 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1243580000000 | 1129220.836 | 05-OCT-15:39 | 448566.544 | 326066.958 | 44502.107 | 0 | 146114.749 | 0 | 43538.914 | 34876.179 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1133170000000 | 1030368.705 | 10-NOV-13:00 | 448566.544 | 326066.958 | 39457.995 | 0 | 102943.808 | 0 | 41790.628 | 34876.179 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
December | 1125840000000 | 967891.973 | 01-DEC-08:30 | 448566.544 | 326066.958 | 32471.623 | 0 | 0 | 0 | 38564.87 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14964500000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1044210000000 | 967156.075 |  | 448566.544 | 326066.958 | 32471.623 | 0 | 0 | 0 | 37828.972 | 0 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1489930000000 | 1236288.471 |  | 448566.544 | 326066.958 | 83067.94 | 0 | 210278.526 | 0 | 55169.381 | 34876.179 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 153693.97 | 28457.15 | 0 | 182151.12
Cost per Total Building Area ($/m2) | 3.32 | 0.61 | 0 | 3.93
Cost per Net Conditioned Building Area ($/m2) | 3.32 | 0.61 | 0 | 3.93

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 23979.13 | 517.68 | 517.68
Net Site Energy | 23979.13 | 517.68 | 517.68
Total Source Energy | 62327.43 | 1345.57 | 1345.57
Net Source Energy | 62327.43 | 1345.57 | 1345.57
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8259.81 | 0 | 0 | 0 | 0
Cooling | 1097.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.23 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 588.9 | 0 | 0 | 0 | 0 | 0
Pumps | 545.22 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 330.74 | 0 | 0 | 0 | 0 | 6386.8
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 306.86 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15412.46 | 8566.67 | 0 | 0 | 0 | 7890.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3589991.92 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3509991.14 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3394174.18
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 335487.81 | 229298.56 | 106189.25 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 3712563.19 | 2545696.11 | 1166867.08 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 389709.93 | 267798.61 | 121911.32 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 114779.47 | 78115.21 | 36664.26 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 63969.11 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 108362.12 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1222799.06 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 130450.03 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18432.29 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20508.33 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13592.46 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 23183.46 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 200943.61 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 218159.86 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 153515.18 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 248778.86 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20350.26 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21892.67 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16917.25 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25515.08 | -
VAV_1_HEATC | Coil:Heating:Water | 73080.31 | -
VAV_2_HEATC | Coil:Heating:Water | 723339.92 | -
VAV_3_HEATC | Coil:Heating:Water | 71810.28 | -
VAV_5_HEATC | Coil:Heating:Water | 36441.34 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.46 | 26190.79 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 171.66 | 282889.09 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.07 | 30410.65 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.37 | 10077.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32897.31 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19879.72 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 47904.03 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 381015.5866 | 580.7638 | 766.6741 | 0 | 0.0058 | 503547.3539 | 154324.7829
February | 312133.6029 | 495.3995 | 691.9866 | 0 | 0.0052 | 454600.5995 | 128301.4337
March | 311788.9842 | 526.4519 | 794.1154 | 0 | 0.0059 | 521851.2908 | 131180.261
April | 269750.8852 | 475.2032 | 751.2969 | 0 | 0.0055 | 493798.6752 | 115379.5294
May | 308024.2286 | 555.97 | 901.341 | 0 | 0.0066 | 592469.7549 | 133025.4583
June | 331401.0651 | 602.7858 | 984.795 | 0 | 0.0072 | 647343.1992 | 143562.9031
July | 338024.6743 | 615.6116 | 1007.0118 | 0 | 0.0073 | 661949.9731 | 146506.6345
August | 360035.6247 | 655.1839 | 1070.9107 | 0 | 0.0078 | 703951.4243 | 155997.4755
September | 294259.8563 | 531.8286 | 863.3518 | 0 | 0.0063 | 567501.3315 | 127148.2515
October | 279725.5685 | 492.9886 | 779.7733 | 0 | 0.0057 | 512515.9633 | 119666.3769
November | 295022.3863 | 496.4298 | 745.8371 | 0 | 0.0055 | 490117.9124 | 123962.343
December | 343552.1703 | 541.5706 | 749.6103 | 0 | 0.0057 | 492438.0949 | 140862.7809
Annual Sum or Average | 3824730 | 6570.1872 | 10106.7041 | 0 | 0.0746 | 6642090 | 1619920
Minimum of Months | 269750.8852 | 475.2032 | 691.9866 | 0 | 0.0052 | 454600.5995 | 115379.5294
Maximum of Months | 381015.5866 | 655.1839 | 1070.9107 | 0 | 0.0078 | 703951.4243 | 155997.4755
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1168440000000 | 978365.528 | 02-JAN-08:50 | 448566.544 | 326066.958 | 30094.674 | 0 | 0 | 0 | 51415.374 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1054870000000 | 977168.631 | 08-FEB-08:30 | 448566.544 | 326066.958 | 30094.674 | 0 | 0 | 0 | 50218.477 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1210920000000 | 1000142.418 | 23-MAR-15:00 | 448566.544 | 326066.958 | 30642.878 | 0 | 58836.035 | 0 | 50474.619 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1145820000000 | 1111053.714 | 14-APR-15:00 | 448566.544 | 326066.958 | 30615.888 | 0 | 124276.228 | 0 | 51424.175 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1374780000000 | 1232082.374 | 31-MAY-15:09 | 448566.544 | 326066.958 | 34328.11 | 0 | 236657.661 | 0 | 56359.18 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1502110000000 | 1351767.15 | 29-JUN-15:00 | 448566.544 | 326066.958 | 42635.807 | 0 | 345599.331 | 0 | 58794.589 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1536010000000 | 1379276.188 | 13-JUL-15:00 | 448566.544 | 326066.958 | 38954.692 | 0 | 376503.977 | 0 | 59080.096 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1633470000000 | 1350873.522 | 25-AUG-15:00 | 448566.544 | 326066.958 | 37582.891 | 0 | 350111.33 | 0 | 58441.879 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1316840000000 | 1269270.551 | 22-SEP-15:00 | 448566.544 | 326066.958 | 30094.674 | 0 | 277327.499 | 0 | 57110.956 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1189250000000 | 1133629.543 | 06-OCT-15:09 | 448566.544 | 326066.958 | 33924.687 | 0 | 139154.297 | 0 | 55813.136 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1137280000000 | 1092036.821 | 02-NOV-15:09 | 448566.544 | 326066.958 | 34332.408 | 0 | 101842.854 | 0 | 51124.137 | 44548.536 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1142670000000 | 976791.557 | 20-DEC-08:39 | 448566.544 | 326066.958 | 30094.674 | 0 | 0 | 0 | 49841.404 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 15412500000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1054870000000 | 976791.557 |  | 448566.544 | 326066.958 | 30094.674 | 0 | 0 | 0 | 49841.404 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1633470000000 | 1379276.188 |  | 448566.544 | 326066.958 | 42635.807 | 0 | 376503.977 | 0 | 59080.096 | 44548.536 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 261976.25 | 67689.17 | 0 | 329665.42
Cost per Total Building Area ($/m2) | 5.66 | 1.46 | 0 | 7.12
Cost per Net Conditioned Building Area ($/m2) | 5.66 | 1.46 | 0 | 7.12

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21136.62 | 456.31 | 456.31
Net Site Energy | 21136.62 | 456.31 | 456.31
Total Source Energy | 57886.77 | 1249.7 | 1249.7
Net Source Energy | 57886.77 | 1249.7 | 1249.7
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6226.54 | 0 | 0 | 0 | 0
Cooling | 553.78 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 598.63 | 0 | 0 | 0 | 0 | 0
Pumps | 368.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 228.9 | 0 | 0 | 0 | 0 | 5544.58
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 310.42 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14599.66 | 6536.97 | 0 | 0 | 0 | 7048.71
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.385 | 0.305 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.385 | 0.305 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 1390.85 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2788866.1 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3275553.06 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2636746.14
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 272827.48 | 181079.81 | 91747.67 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water | 3054118.07 | 2030476.26 | 1023641.81 | 0.66 | -
VAV_3_COOLC | Coil:Cooling:Water | 308702.62 | 205315.87 | 103386.76 | 0.67 | -
VAV_5_COOLC | Coil:Cooling:Water | 77413.76 | 51626.8 | 25786.97 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 52669.29 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 103113.34 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1183547.4 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 120163.47 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17588.26 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18375.13 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12501.49 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 21855.82 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 192407.07 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 196599.07 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 132375.72 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 236011.13 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19029.67 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19337.58 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13578.12 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24180.88 | -
VAV_1_HEATC | Coil:Heating:Water | 66985.24 | -
VAV_2_HEATC | Coil:Heating:Water | 661390.4 | -
VAV_3_HEATC | Coil:Heating:Water | 66018.77 | -
VAV_5_HEATC | Coil:Heating:Water | 33108.42 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.29 | 27424.35 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 182.32 | 300450.94 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.44 | 31038.42 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 4.95 | 9281.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25556.1 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18551.92 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 37213.99 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 359532.491 | 564.1607 | 861.6799 | 0 | 0.0061 | 20431500 | 147422.454
February | 304393.9826 | 490.2244 | 775.0425 | 0 | 0.0055 | 18379500 | 126029.947
March | 321640.3567 | 541.6825 | 904.6039 | 0 | 0.0063 | 21456100 | 135459.8333
April | 279670.4631 | 480.5608 | 821.1419 | 0 | 0.0057 | 19478000 | 118708.2757
May | 303645.3928 | 531.2974 | 926.0369 | 0 | 0.0064 | 21967600 | 129806.8096
June | 320101.2566 | 563.9692 | 990.2494 | 0 | 0.0069 | 23491400 | 137216.5153
July | 327597.184 | 580.2441 | 1024.5345 | 0 | 0.0071 | 24305200 | 140726.3436
August | 338936.8047 | 599.5784 | 1057.2839 | 0 | 0.0073 | 25082000 | 145524.9692
September | 298692.7423 | 524.9271 | 919.2342 | 0 | 0.0064 | 21806600 | 127911.4653
October | 296388.9645 | 511.6363 | 878.7201 | 0 | 0.0061 | 20844100 | 126031.5238
November | 297409.237 | 499.4375 | 831.2586 | 0 | 0.0058 | 19716200 | 125115.9409
December | 339545.6639 | 540.1957 | 840.5305 | 0 | 0.006 | 19931400 | 139942.1207
Annual Sum or Average | 3787550 | 6427.914 | 10830.3162 | 0 | 0.0758 | 256890000 | 1599900
Minimum of Months | 279670.4631 | 480.5608 | 775.0425 | 0 | 0.0055 | 18379500 | 118708.2757
Maximum of Months | 359532.491 | 599.5784 | 1057.2839 | 0 | 0.0073 | 25082000 | 147422.454
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1161170000000 | 968856.04 | 10-JAN-08:09 | 448566.544 | 326066.958 | 31698.286 | 0 | 0.143 | 2499 | 37803.13 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1044550000000 | 985842.812 | 03-FEB-16:10 | 448566.544 | 326066.958 | 33944.372 | 0 | 18697.038 | 0 | 38405.222 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1219400000000 | 1072038.08 | 30-MAR-15:09 | 448566.544 | 326066.958 | 35554.305 | 0 | 100767.65 | 0 | 40919.945 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1106980000000 | 1055049.411 | 06-APR-15:30 | 448566.544 | 326066.958 | 32638.118 | 0 | 87260.233 | 0 | 40354.88 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1248470000000 | 1092438.51 | 16-MAY-15:00 | 448566.544 | 326066.958 | 34193.636 | 0 | 122119.338 | 0 | 41329.356 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1335070000000 | 1195821.822 | 26-JUN-15:39 | 448566.544 | 326066.958 | 47863.743 | 0 | 204488.304 | 0 | 48673.596 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1381320000000 | 1207091.926 | 21-JUL-15:00 | 448566.544 | 326066.958 | 51297.273 | 0 | 208595.635 | 0 | 52402.839 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1425470000000 | 1185393.662 | 09-AUG-15:00 | 448566.544 | 326066.958 | 46609.404 | 0 | 192425.755 | 0 | 51562.323 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1239320000000 | 1138022.295 | 01-SEP-15:00 | 448566.544 | 326066.958 | 39570.391 | 0 | 161069.826 | 0 | 42585.898 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1184620000000 | 1102445.068 | 06-OCT-15:20 | 448566.544 | 326066.958 | 39092.941 | 0 | 126783.069 | 0 | 41772.879 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1120520000000 | 974552.973 | 21-NOV-16:10 | 448566.544 | 326066.958 | 31698.286 | 0 | 10045.216 | 0 | 38013.291 | 34607.293 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1132750000000 | 966136.708 | 01-DEC-08:50 | 448566.544 | 326066.958 | 31698.286 | 0 | 0.369 | 0 | 37582.573 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14599700000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1044550000000 | 966136.708 |  | 448566.544 | 326066.958 | 31698.286 | 0 | 0.143 | 0 | 37582.573 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1425470000000 | 1207091.926 |  | 448566.544 | 326066.958 | 51297.273 | 0 | 208595.635 | 2499 | 52402.839 | 34607.293 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 313337.45 | 52725.3 | 0 | 366062.75
Cost per Total Building Area ($/m2) | 6.76 | 1.14 | 0 | 7.9
Cost per Net Conditioned Building Area ($/m2) | 6.76 | 1.14 | 0 | 7.9

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 24935.52 | 538.33 | 538.33
Net Site Energy | 24935.52 | 538.33 | 538.33
Total Source Energy | 61729.84 | 1332.67 | 1332.67
Net Source Energy | 61729.84 | 1332.67 | 1332.67
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9884.19 | 0 | 0 | 0 | 0
Cooling | 576.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 642.67 | 0 | 0 | 0 | 0 | 0
Pumps | 425.33 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 217.18 | 0 | 0 | 0 | 0 | 3673.4
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 339.07 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14712.26 | 10223.25 | 0 | 0 | 0 | 5177.54
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.487 | 0.409 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 3.241 | 0.487 | 0.409 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 3.241 | 0.487 | 0.409 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 1390.85 | 3.24 | 0.487 | 0.409
Non-North Total or Average |  |  | 3245.31 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3405411.51 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 3652872.47 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3219661.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 332251.88 | 229725.42 | 102526.46 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 3689692.2 | 2558457.59 | 1131234.62 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 366897.09 | 254965.27 | 111931.82 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 98866.51 | 68497.14 | 30369.37 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 59424.98 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 106608.38 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1216426.07 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 121103.38 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23058.62 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22730.61 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13807.53 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26198.74 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 250480.84 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 244548.17 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 146202.37 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 284739.59 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24990.88 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24309.46 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14567.71 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29105.14 | -
VAV_1_HEATC | Coil:Heating:Water | 76098.83 | -
VAV_2_HEATC | Coil:Heating:Water | 752825.53 | -
VAV_3_HEATC | Coil:Heating:Water | 75276.4 | -
VAV_5_HEATC | Coil:Heating:Water | 37524.08 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.5 | 27778.1 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 183.74 | 302794.55 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.36 | 30907.07 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.1 | 9561.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 31205.88 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20688.96 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 45441.03 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 379854.2146 | 580.9221 | 770.6168 | 0 | 0.0059 | 506147.4786 | 154038.7281
February | 323401.9756 | 506.5404 | 695.0101 | 0 | 0.0053 | 456553.358 | 132288.6694
March | 327965.604 | 542.3001 | 797.982 | 0 | 0.0059 | 524342.6139 | 136890.3361
April | 268295.0526 | 465.3565 | 723.5305 | 0 | 0.0053 | 475520.0276 | 114060.7593
May | 286660.2473 | 509.0579 | 811.6332 | 0 | 0.0059 | 533471.4726 | 123000.8082
June | 303156.7878 | 548.6992 | 892.0301 | 0 | 0.0065 | 586355.2327 | 131068.1607
July | 324381.8156 | 588.9666 | 960.5117 | 0 | 0.007 | 631376.9454 | 140421.6266
August | 324792.2413 | 588.0782 | 956.4076 | 0 | 0.007 | 628673.0587 | 140443.14
September | 274917.4172 | 489.4901 | 782.5707 | 0 | 0.0057 | 514374.2449 | 118085.0363
October | 278028.4825 | 484.6029 | 757.4764 | 0 | 0.0056 | 497839.7121 | 118424.7034
November | 310241.6124 | 509.9218 | 744.8572 | 0 | 0.0056 | 489421.0834 | 129198.9163
December | 355864.1703 | 554.5295 | 755.4735 | 0 | 0.0057 | 496257.1882 | 145294.4373
Annual Sum or Average | 3757560 | 6368.4653 | 9648.0999 | 0 | 0.0714 | 6340330 | 1583220
Minimum of Months | 268295.0526 | 465.3565 | 695.0101 | 0 | 0.0053 | 456553.358 | 114060.7593
Maximum of Months | 379854.2146 | 588.9666 | 960.5117 | 0 | 0.007 | 631376.9454 | 154038.7281
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1174480000000 | 976533.878 | 27-JAN-08:39 | 448566.544 | 326066.958 | 31943.285 | 0 | 0 | 0 | 47735.113 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1059400000000 | 976864.525 | 06-FEB-08:30 | 448566.544 | 326066.958 | 31943.285 | 0 | 0 | 0 | 48065.76 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1216700000000 | 975808.623 | 09-MAR-08:30 | 448566.544 | 326066.958 | 31943.285 | 0 | 0 | 0 | 47009.858 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1103410000000 | 1002027.803 | 04-APR-15:09 | 448566.544 | 326066.958 | 34167.272 | 0 | 59460.994 | 0 | 48210.65 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1237880000000 | 1131500.99 | 31-MAY-15:00 | 448566.544 | 326066.958 | 36292.061 | 0 | 142895.02 | 0 | 49866.961 | 42258.061 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1360590000000 | 1261673.834 | 14-JUN-15:09 | 448566.544 | 326066.958 | 37282.367 | 0 | 267426.516 | 0 | 54518.004 | 42258.061 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1465060000000 | 1380263.489 | 07-JUL-07:00 | 448566.544 | 326066.958 | 38651.237 | 0 | 344749.378 | 0 | 57749.333 | 42258.061 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
August | 1458790000000 | 1280649.571 | 11-AUG-15:39 | 448566.544 | 326066.958 | 40198.157 | 0 | 282922.491 | 0 | 55081.975 | 42258.061 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1193570000000 | 1271456.837 | 07-SEP-15:20 | 448566.544 | 326066.958 | 38212.504 | 0 | 275248.111 | 0 | 55549.274 | 42258.061 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1155200000000 | 1075680.297 | 06-OCT-15:09 | 448566.544 | 326066.958 | 36218.627 | 0 | 88500.683 | 0 | 48514.039 | 42258.061 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1135660000000 | 974837.854 | 30-NOV-08:20 | 448566.544 | 326066.958 | 31943.285 | 0 | 0.046 | 0 | 46039.042 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1151530000000 | 976516.763 | 18-DEC-08:30 | 448566.544 | 326066.958 | 31943.285 | 0 | 0 | 0 | 47717.998 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14712300000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1059400000000 | 974837.854 |  | 448566.544 | 326066.958 | 31943.285 | 0 | 0 | 0 | 46039.042 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1465060000000 | 1380263.489 |  | 448566.544 | 326066.958 | 40198.157 | 0 | 344749.378 | 0 | 57749.333 | 42258.061 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 250493.87 | 80592.23 | 0 | 331086.1
Cost per Total Building Area ($/m2) | 5.41 | 1.74 | 0 | 7.15
Cost per Net Conditioned Building Area ($/m2) | 5.41 | 1.74 | 0 | 7.15

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 32681.13 | 705.55 | 705.55
Net Site Energy | 32681.13 | 705.55 | 705.55
Total Source Energy | 72549.87 | 1566.26 | 1566.26
Net Source Energy | 72549.87 | 1566.26 | 1566.26
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 17439.39 | 0 | 0 | 0 | 0
Cooling | 422.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 5137.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 898.3 | 0 | 0 | 0 | 0 | 0
Pumps | 476.53 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 216.45 | 0 | 0 | 0 | 0 | 3693.09
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 377.99 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14863.74 | 17817.38 | 0 | 0 | 0 | 5197.22
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 10.76 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 10.76 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 10.76 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 10.76 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 10.76 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 5.5952 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 0.613 | 0.675 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 2.615 | 0.702 | 0.633 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 1159.04 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 772.69 | 2.615 | 0.702 | 0.633 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 115.9 | 115.9 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-90.1-2004-NONRES-FIXED | 77.27 | 77.27 | 2.615 | 0.702 | 0.633 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 1390.85 | 2.61 | 0.702 | 0.633
Non-North Total or Average |  |  | 3245.31 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4069847.12 | 5.5
HEATSYS1 BOILER | Boiler:HotWater | 4905094.99 | 0.78
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3847855.46
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 442843.94 | 315853.32 | 126990.63 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 5052261.9 | 3608286.09 | 1443975.81 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 523554.38 | 373960.8 | 149593.58 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 98252.93 | 70595.13 | 27657.8 | 0.72 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 59333.93 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 126385.54 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1457060.84 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 154252.56 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47421.35 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31045.76 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18092.24 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 33264.97 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 539461.61 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 341535.99 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 214455.31 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 374074.35 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53589 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34307.19 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 23512.99 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 37545.82 | -
VAV_1_HEATC | Coil:Heating:Water | 99995.21 | -
VAV_2_HEATC | Coil:Heating:Water | 985007.3 | -
VAV_3_HEATC | Coil:Heating:Water | 97924.2 | -
VAV_5_HEATC | Coil:Heating:Water | 47126.28 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.22 | 35718.94 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 242.37 | 399414.32 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 25.11 | 42271.02 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.91 | 9372.97 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37294.52 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27781.24 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 54307.11 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 443680.4771 | 483.9096 | 1699.101 | 0 | 0.0062 | 340806.5121 | 166046.5795
February | 358970.4208 | 399.479 | 1541.236 | 0 | 0.0055 | 309186.7966 | 135568.9758
March | 337811.6872 | 391.2474 | 1770.7939 | 0 | 0.0062 | 355315.437 | 129934.8985
April | 258481.1526 | 310.6727 | 1591.4495 | 0 | 0.0055 | 319376.0271 | 101161.0444
May | 263389.7854 | 324.35 | 1784.3853 | 0 | 0.0061 | 358122.1494 | 104278.9724
June | 286099.3371 | 355.5957 | 2006.8602 | 0 | 0.0068 | 402782.8334 | 113774.7115
July | 287391.2756 | 357.5692 | 2023.6148 | 0 | 0.0069 | 406146.6654 | 114345.0646
August | 289281.4525 | 357.2077 | 1980.1611 | 0 | 0.0067 | 397417.0392 | 114679.5903
September | 254342.6125 | 308.156 | 1617.3811 | 0 | 0.0055 | 324588.6667 | 99919.5217
October | 297093.8949 | 349.0732 | 1661.6312 | 0 | 0.0058 | 333432.1418 | 115040.3504
November | 361947.9705 | 408.2227 | 1667.624 | 0 | 0.0059 | 334568.7945 | 137529.0999
December | 400116.25 | 443.3548 | 1677.8673 | 0 | 0.006 | 336586.7345 | 150813.706
Annual Sum or Average | 3838610 | 4488.8381 | 21022.1053 | 0 | 0.073 | 4218330 | 1483090
Minimum of Months | 254342.6125 | 308.156 | 1541.236 | 0 | 0.0055 | 309186.7966 | 99919.5217
Maximum of Months | 443680.4771 | 483.9096 | 2023.6148 | 0 | 0.0069 | 406146.6654 | 166046.5795
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1200870000000 | 1000312.601 | 03-JAN-08:30 | 448566.544 | 326066.958 | 41907.145 | 0 | 0 | 2499 | 59050.976 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1089450000000 | 998571.473 | 02-FEB-08:50 | 448566.544 | 326066.958 | 41907.145 | 0 | 0 | 2499 | 57309.848 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1251990000000 | 994308.038 | 03-MAR-08:00 | 448566.544 | 326066.958 | 41907.145 | 0 | 0 | 0 | 55545.413 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1125360000000 | 993652.266 | 07-APR-07:49 | 448566.544 | 326066.958 | 41907.145 | 0 | 0.046 | 0 | 54889.595 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
May | 1261880000000 | 1154134.044 | 24-MAY-15:09 | 448566.544 | 326066.958 | 48894.592 | 0 | 135424.797 | 0 | 59122.666 | 50503.103 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1419250000000 | 1253452.831 | 21-JUN-15:50 | 448566.544 | 326066.958 | 50437.732 | 0 | 228990.719 | 0 | 63332.391 | 50503.103 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1431100000000 | 1254285.086 | 03-JUL-15:00 | 448566.544 | 326066.958 | 43896.822 | 0 | 234898.044 | 0 | 64798.23 | 50503.103 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1400340000000 | 1238852.452 | 15-AUG-15:09 | 448566.544 | 326066.958 | 48906.873 | 0 | 215072.184 | 0 | 64181.406 | 50503.103 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1143720000000 | 1095550.41 | 07-SEP-15:00 | 448566.544 | 326066.958 | 44966.794 | 0 | 82261.326 | 0 | 57630.302 | 50503.103 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1174880000000 | 996409.531 | 10-OCT-07:10 | 448566.544 | 326066.958 | 41907.145 | 0 | 0.088 | 2499 | 55147.818 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1178890000000 | 997083.379 | 22-NOV-08:00 | 448566.544 | 326066.958 | 41907.145 | 0 | 0 | 2499 | 55821.754 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1186000000000 | 998603.718 | 28-DEC-08:20 | 448566.544 | 326066.958 | 41907.145 | 0 | 0 | 2499 | 57342.093 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 14863700000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1089450000000 | 993652.266 |  | 448566.544 | 326066.958 | 41907.145 | 0 | 0 | 0 | 54889.595 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1431100000000 | 1254285.086 |  | 448566.544 | 326066.958 | 50437.732 | 0 | 234898.044 | 2499 | 64798.23 | 50503.103 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 409402.4 | 73445.63 | 0 | 482848.03
Cost per Total Building Area ($/m2) | 8.84 | 1.59 | 0 | 10.42
Cost per Net Conditioned Building Area ($/m2) | 8.84 | 1.59 | 0 | 10.42

## Picture
DOE Commercial Building Benchmark - Large Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720