## BuildingSummary
Building Summary Outpatient Health Care new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Outpatient Health Care
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, outpatient
Form
| Total Floor Area (m2) | 929.5 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.15
| East | 0.15
| North | 0.15
| West | 0.15
| Total | 0.15
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | single zone per floor
| Floor to Ceiling Height (m) | 3.05
| Floor to Floor Height (m) | 3.05
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 536.66
| Net Dimensions - Total Area (m2) | 456.22
| Wall to Skin Ratio | 0.51348
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 508.48
| Net Dimensions - Total Area (m2) | 508.48
| Roof to Skin Ratio | 0.48652
Window Dimensions (m2)
| South | 24.14
| East | 16.08
| North | 24.14
| West | 16.08
| Total Area (m2) | 80.44
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab w/carpet
| Dimensions - Total Area (m2) | 464.75
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1859.01
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.3 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | CAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 10.03

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First_floor | Yes | 1 | 464.75 | 1416.93 | 3.0488 | 268.33 | 40.22 | 18.5806 | 25.0126 | 10.76 | 8.0699 | 0 | 21.0406 | 2.5 | 0.3 | 201.9565 | 0 | 0.3
Second_floor | Yes | 1 | 464.75 | 1416.93 | 3.0488 | 268.33 | 40.22 | 18.5806 | 25.0126 | 10.76 | 8.0699 | 0 | 21.0406 | 2.5 | 0.3 | 201.9565 | 0 | 0.3
Attic | No | 1 | 464.75 | 631.22 | 1.3582
Total Conditioned Zones |  |  | 929.5 | 2833.86 |  | 536.66 | 80.44 |  | 50.0252
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783 | 0.24783
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.61 | 0.61 | 0.61 | 0.501 | 0.501 | 0.501 | 0.61 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.651 | 0.654
| Visible transmittance | 0.61 | 0.61 | 0.61 | 0.622 | 0.622 | 0.622 | 0.61 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.64 | 0.64
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | 65.8507 | 67.0358 | 70.1834 | 66.524 | 61.97 | 70.4424 | 59.4663 | 65.7955 | 77.0631 | 62.4273 | 64.4383 | 74.1472 | 64.8533 | 70.5957 | 62.7551 | 59.4639
| PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | 37.1783 | 38.3187 | 41.0889 | 35.5183 | 28.8082 | 38.8991 | 29.2051 | 37.647 | 39.2334 | 31.047 | 35.7911 | 35.5798 | 34.6919 | 34.4734 | 30.3925 | 29.8894
Heating (kW)
| PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 7.8181 | 11.4596 | 8.7077 | 13.3282 | 8.1311 | 9.8245 | 8.9876 | 16.6604 | 13.2714 | 11.7025 | 21.5087 | 17.5312 | 25.1597 | 23.8501 | 25.6718 | 35.1136
| PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 10.4813 | 20.5515 | 15.6613 | 22.2303 | 11.0092 | 17.447 | 15.5988 | 25.7552 | 21.8488 | 20.2152 | 31.2473 | 26.9105 | 35.3168 | 34.0657 | 35.8749 | 46.1341
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | 4.31 | 4.28 | 4.32 | 4.32 | 4.36 | 4.18 | 4.37 | 4.31 | 4.18 | 4.37 | 4.37 | 4.18 | 4.37 | 4.18 | 4.37 | 4.37
| PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | 3.59 | 3.61 | 3.44 | 3.66 | 3.74 | 3.74 | 3.74 | 3.63 | 3.74 | 3.75 | 3.62 | 3.74 | 3.66 | 3.74 | 3.75 | 3.75
Heating Efficiency (%)
| PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_2:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_1:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC_2:1_UNITARY_PACKAGE_FAN | 3.9 | 3.99 | 4.24 | 4.02 | 3.74 | 4.26 | 3.59 | 3.95 | 4.66 | 3.77 | 3.89 | 4.48 | 3.92 | 4.26 | 3.79 | 3.59
| PSZ-AC_1:2_UNITARY_PACKAGE_FAN | 1.91 | 2.02 | 2.42 | 1.98 | 1.74 | 2.35 | 1.76 | 2.01 | 2.37 | 1.88 | 1.91 | 2.15 | 1.93 | 2.08 | 1.84 | 1.81
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.083353 | 0.11518 | 0.10303 | 0.10365 | 0.12958 | 0.098736 | 0.1511 | 0.075708 | 0.03763 | 0.075408 | 0.05287 | 0.037656 | 0.060329 | 0.076594 | 0.060718 | 0.10036
| Total Cost ($/m2) | 27.52 | 35.74 | 33.18 | 30.59 | 39.24 | 30.42 | 40.86 | 21.66 | 11.1 | 20.12 | 14.91 | 10.72 | 16.9 | 20.85 | 0 | 0
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011462 | 0.0081733 | 0.0085739 | 0.010495 | 0.0083925 | 0.0081221 | 0.0084624 | 0.009915 | 0.0071161 | 0.0083342 | 0.0085703 | 0.0070678 | 0.0079886 | 0.0082638 | 0.0079617 | 0.0040995
| Total Cost ($/m2) | 0.2 | 0.2 | 0.17 | 0.3 | 0.18 | 0.17 | 0.21 | 0.42 | 0.22 | 0.28 | 0.43 | 0.28 | 0.62 | 0.52 | 0.68 | 0.77
Total Utility Costs
| Cost Intensity ($/m2) | 25762.85 | 33410.77 | 31001.11 | 28712.04 | 36636.63 | 28431.37 | 38174.04 | 20524.16 | 10527.32 | 18964.31 | 14257.38 | 10219.54 | 16280.9 | 19864.18 | 15762.98 | 24899.5
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 70144.4444 | 56872.2222 | 51616.6667 | 45763.8889 | 20950 | 39850 | 8302.7778 | 40072.2222 | 25791.6667 | 8161.1111 | 25130.5556 | 19186.1111 | 23872.2222 | 14000 | 15766.6667 | 12261.1111
| Interior Lighting | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889 | 30513.8889
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556 | 175630.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 30588.8889 | 25394.4444 | 41616.6667 | 22391.6667 | 54380.5556 | 40341.6667 | 36872.2222 | 19750 | 42363.8889 | 33733.3333 | 30819.4444 | 39191.6667 | 30347.2222 | 32866.6667 | 27222.2222 | 22550
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 306877.7778 | 288411.1111 | 299377.7778 | 274300 | 281475 | 286336.1111 | 251319.4444 | 265966.6667 | 274302.7778 | 248038.8889 | 262094.4444 | 264525 | 260363.8889 | 253013.8889 | 249133.3333 | 240955.5556
Gas (MJ)
| Heating | 0 | 5300 | 1470 | 6750 | 10 | 1410 | 2290 | 17690 | 7670 | 8930 | 23900 | 13850 | 47830 | 34490 | 54030 | 147060
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 16010 | 18010 | 16860 | 19950 | 19580 | 18250 | 21240 | 21480 | 21190 | 22280 | 22810 | 22750 | 23960 | 24180 | 25870 | 28180
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 16010 | 23310 | 18330 | 26700 | 19590 | 19660 | 23530 | 39170 | 28860 | 31210 | 46710 | 36600 | 71790 | 58670 | 79900 | 175240
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1120780 | 1061590 | 1096090 | 1014180 | 1032900 | 1050470 | 928280 | 996650 | 1016350 | 924150 | 990250 | 988880 | 1009100 | 969510 | 976770 | 1042680
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 271.6729 | 220.269 | 199.9139 | 177.2458 | 81.1404 | 154.341 | 32.1571 | 155.2017 | 99.8924 | 31.6084 | 97.3319 | 74.3088 | 92.4583 | 54.2227 | 61.0651 | 47.4879
| Interior Lighting (elec) | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818 | 118.1818
| Exterior Lighting (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (elec) | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259 | 680.2259
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 118.4723 | 98.354 | 161.1834 | 86.724 | 210.6186 | 156.2453 | 142.808 | 76.4927 | 164.0775 | 130.6509 | 119.3653 | 151.7913 | 117.5363 | 127.2942 | 105.433 | 87.3373
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1188.553 | 1117.0307 | 1159.5051 | 1062.3776 | 1090.1668 | 1108.9941 | 973.3728 | 1030.1022 | 1062.3884 | 960.667 | 1015.1049 | 1024.5186 | 1008.4024 | 979.9354 | 964.9059 | 933.2329
Gas (MJ/m2)
| Heating (gas) | 0 | 5.702 | 1.5815 | 7.262 | 0.010758 | 1.5169 | 2.4637 | 19.0317 | 8.2517 | 9.6073 | 25.7127 | 14.9005 | 51.4578 | 37.106 | 58.128 | 158.2141
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 17.2243 | 19.376 | 18.1388 | 21.4632 | 21.0651 | 19.6342 | 22.851 | 23.1092 | 22.7972 | 23.9699 | 24.5401 | 24.4755 | 25.7773 | 26.014 | 27.8322 | 30.3174
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 17.2243 | 25.078 | 19.7203 | 28.7251 | 21.0758 | 21.1512 | 25.3147 | 42.1409 | 31.049 | 33.5772 | 50.2528 | 39.376 | 77.2351 | 63.12 | 85.9602 | 188.5315
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1205.7881 | 1142.1087 | 1179.2254 | 1091.1027 | 1111.2426 | 1130.1452 | 998.6875 | 1072.2431 | 1093.4373 | 994.2442 | 1065.3577 | 1063.8838 | 1085.6374 | 1043.0446 | 1050.8553 | 1121.7644
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 69.9934 | 68.0425 | 65.7473 | 63.4503 | 66.4319 | 60.8298 | 55.7371 | 60.232 | 58.2942 | 54.8508 | 56.7946 | 59.3405 | 56.0338 | 58.2909 | 56.5151 | 55.1419
| Feb | 71.0668 | 68.9532 | 67.7224 | 63.2108 | 64.8587 | 63.3131 | 63.9008 | 60.8203 | 63.9363 | 56.5184 | 57.8685 | 57.8421 | 57.5738 | 58.2036 | 57.2288 | 55.5636
| Mar | 71.5805 | 68.2045 | 72.2584 | 66.3638 | 65.7988 | 66.8089 | 58.9234 | 66.1005 | 64.7106 | 61.4146 | 63.7517 | 65.3519 | 59.2898 | 62.7149 | 58.2875 | 56.7005
| Apr | 72.5351 | 70.8357 | 72.9661 | 68.9914 | 67.8333 | 72.4629 | 64.2245 | 67.0932 | 69.3891 | 59.5006 | 64.2711 | 67.3341 | 63.1232 | 61.0239 | 59.9073 | 58.2811
| May | 75.1029 | 75.5375 | 76.6375 | 71.7395 | 70.3065 | 74.9486 | 66.256 | 69.8983 | 71.9401 | 67.0099 | 70.6191 | 69.0773 | 70.3778 | 66.9015 | 65.1734 | 62.8317
| Jun | 76.506 | 76.1165 | 85.2285 | 74.1281 | 69.9799 | 83.071 | 66.5587 | 76.6526 | 75.559 | 68.3354 | 74.7159 | 72.661 | 74.5663 | 73.7751 | 70.8646 | 67.3323
| Jul | 75.4657 | 76.9221 | 84.0101 | 77.226 | 72.1498 | 80.9824 | 68.6554 | 77.8095 | 76.6456 | 70.5206 | 75.8407 | 74.915 | 74.2484 | 73.2519 | 73.6938 | 67.2775
| Aug | 76.628 | 77.4197 | 84.1773 | 75.0692 | 76.0651 | 80.2992 | 67.7225 | 78.2583 | 76.8988 | 69.5886 | 74.931 | 75.3824 | 74.3961 | 71.5417 | 71.1987 | 67.2124
| Sep | 75.2375 | 76.1037 | 80.1137 | 72.5889 | 72.5221 | 79.3175 | 71.9522 | 73.7654 | 75.0491 | 69.9298 | 73.8077 | 71.3936 | 71.1347 | 68.983 | 71.4316 | 58.7688
| Oct | 74.5979 | 72.5089 | 74.727 | 68.3008 | 69.0882 | 72.6836 | 65.8625 | 69.6394 | 69.521 | 62.983 | 68.8783 | 69.6612 | 65.0946 | 65.6927 | 60.85 | 58.0627
| Nov | 72.0792 | 69.3995 | 69.8853 | 65.3997 | 66.0604 | 64.1685 | 58.5719 | 67.1049 | 62.329 | 55.3911 | 69.6966 | 62.9502 | 60.9412 | 57.936 | 56.7406 | 55.6831
| Dec | 70.0804 | 68.3799 | 64.6202 | 62.8727 | 66.3125 | 63.5108 | 57.2537 | 59.5029 | 57.5984 | 55.7088 | 56.9965 | 59.1003 | 56.0389 | 57.1597 | 56.6381 | 54.8766
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-14:30 | 26-JAN-15:00 | 23-JAN-15:00 | 26-JAN-13:00 | 18-JAN-14:00 | 27-JAN-15:39 | 05-JAN-15:09 | 26-JAN-15:00 | 31-JAN-09:50 | 19-JAN-15:00 | 24-JAN-13:00 | 19-JAN-14:50 | 10-JAN-15:00 | 20-JAN-15:30 | 18-JAN-15:20
| Feb | 22-FEB-15:00 | 23-FEB-15:30 | 28-FEB-15:00 | 22-FEB-14:00 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-15:00 | 15-FEB-15:00 | 14-FEB-15:00 | 21-FEB-13:00 | 22-FEB-15:00 | 16-FEB-15:09 | 16-FEB-15:00 | 02-FEB-14:00 | 17-FEB-15:00 | 28-FEB-11:00
| Mar | 13-MAR-14:00 | 28-MAR-14:00 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-14:50 | 31-MAR-14:00 | 01-MAR-13:09 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 24-MAR-10:00 | 10-MAR-15:00
| Apr | 03-APR-14:39 | 21-APR-14:00 | 26-APR-14:00 | 14-APR-14:00 | 11-APR-13:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-14:00 | 21-APR-14:00 | 14-APR-13:00 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 27-APR-09:39
| May | 24-MAY-14:00 | 18-MAY-14:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-14:00 | 17-MAY-13:00 | 31-MAY-14:00 | 31-MAY-14:00 | 04-MAY-14:00 | 30-MAY-09:00 | 23-MAY-14:00 | 31-MAY-14:00 | 16-MAY-14:00 | 31-MAY-14:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-14:00 | 19-JUN-14:00 | 28-JUN-13:00 | 27-JUN-14:00 | 16-JUN-14:00 | 30-JUN-14:00 | 29-JUN-14:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:39 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-10:00 | 21-JUN-14:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 19-JUL-14:00 | 03-JUL-14:00 | 20-JUL-14:00 | 24-JUL-14:00 | 03-JUL-12:00 | 25-JUL-13:50 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 26-JUL-12:39 | 14-JUL-12:00 | 21-JUL-14:00 | 12-JUL-12:00 | 11-JUL-14:00
| Aug | 21-AUG-14:00 | 31-AUG-14:30 | 01-AUG-14:00 | 17-AUG-13:00 | 09-AUG-14:50 | 04-AUG-14:00 | 15-AUG-12:20 | 17-AUG-14:00 | 01-AUG-14:30 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 23-AUG-13:00 | 09-AUG-14:00 | 11-AUG-14:00 | 15-AUG-14:39
| Sep | 01-SEP-14:00 | 15-SEP-14:00 | 08-SEP-14:30 | 11-SEP-13:00 | 07-SEP-09:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 05-SEP-13:09 | 01-SEP-14:00 | 07-SEP-12:00 | 06-SEP-14:50 | 22-SEP-14:00 | 01-SEP-14:00 | 07-SEP-13:50 | 07-SEP-14:00
| Oct | 06-OCT-14:00 | 12-OCT-14:00 | 03-OCT-12:30 | 12-OCT-14:00 | 05-OCT-10:20 | 03-OCT-14:00 | 13-OCT-14:00 | 12-OCT-14:00 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 12-OCT-14:00
| Nov | 07-NOV-14:00 | 03-NOV-14:39 | 13-NOV-15:39 | 22-NOV-14:00 | 20-NOV-13:00 | 10-NOV-14:39 | 08-NOV-14:30 | 03-NOV-14:20 | 08-NOV-15:20 | 29-NOV-09:50 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-14:00 | 28-NOV-15:30 | 10-NOV-15:00 | 14-NOV-15:00
| Dec | 19-DEC-14:30 | 19-DEC-15:30 | 11-DEC-15:00 | 05-DEC-14:00 | 19-DEC-13:09 | 05-DEC-14:00 | 07-DEC-14:00 | 06-DEC-15:09 | 08-DEC-15:20 | 01-DEC-11:30 | 05-DEC-15:09 | 27-DEC-15:39 | 06-DEC-15:09 | 06-DEC-15:39 | 01-DEC-14:50 | 18-DEC-15:00
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
| Total Building | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
Emissions
| Carbon Equivalent (kg) | 84450.149 | 96623.3643 | 90704.9614 | 84975.9824 | 33248.0509 | 96928.3109 | 29794.8858 | 72479.1075 | 112572.163 | 18628.4814 | 140577.6188 | 108717.3442 | 90415.3409 | 93518.2176 | 86717.1189 | 70961.6104
| CO2 (kg) | 195714.5051 | 242615.4035 | 213488.3829 | 193159.7582 | 88844.193 | 229760.4875 | 79640.4029 | 162993.6226 | 262595.0328 | 44540.7092 | 324840.825 | 253690.9569 | 209198.6972 | 218107.1824 | 200758.2007 | 178974.0566
| NOX (kg) | 344.4492 | 318.4021 | 360.0829 | 371.5683 | 76.0838 | 376.0408 | 68.2181 | 323.6627 | 459.4601 | 70.429 | 589.2795 | 443.4962 | 378.3199 | 384.5102 | 362.5302 | 221.071
| SO2 (kg) | 1313.5677 | 1375.7321 | 1203.8574 | 962.8016 | 819.0622 | 1575.079 | 731.3135 | 970.8981 | 1197.829 | 191.7226 | 1766.3185 | 1155.1316 | 614.5202 | 675.5895 | 588.0144 | 1226.6025
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.006 | 0.0039 | 0.0033 | 0.0035 | 0.0004 | 0.003 | 0.0003 | 0.0039 | 0.0047 | 0.0007 | 0.0053 | 0.0045 | 0.0045 | 0.0047 | 0.0043 | 0.0042
| Water for Electricity (m3) | 162.5714 | 469.2804 | 8892.8 | 1712.62 | 4942.06 | 7855.32 | 4412.59 | 60.3846 | 1245.55 | 2534.16 | 406.6236 | 1201.15 | 403.9393 | 16026.9 | 386.5144 | 246.1786

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1120.78 | 1205.78 | 1205.78
Net Site Energy | 1120.78 | 1205.78 | 1205.78
Total Source Energy | 3681.99 | 3961.24 | 3961.24
Net Source Energy | 3681.99 | 3961.24 | 3961.24
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 252.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.12 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 16.01 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1104.76 | 16.01 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 6.49 | 0.358 | 0.358
North Total or Average |  |  | 24.14 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 56.3 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65850.67 | 52102.52 | 13748.15 | 0.79 | 4.31
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37178.28 | 27625.19 | 9553.1 | 0.74 | 3.59
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 7818.09 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10481.32 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.9 | 7434.43 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.91 | 2084.71 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15153.0816 | 26.6592 | 101.6267 | 0 | 0.0005 | 12577.6479 | 6537.5426
February | 13969.9462 | 24.5789 | 93.7015 | 0 | 0.0004 | 11596.7975 | 6027.2218
March | 16304.4615 | 28.6893 | 109.3838 | 0 | 0.0005 | 13537.6906 | 7034.7335
April | 15828.7142 | 27.8573 | 106.2328 | 0 | 0.0005 | 13147.7119 | 6829.985
May | 17253.8002 | 30.3696 | 115.8304 | 0 | 0.0005 | 14335.5534 | 7445.3247
June | 17392.9018 | 30.6183 | 116.7943 | 0 | 0.0005 | 14454.8512 | 7505.7322
July | 17465.6563 | 30.7479 | 117.2951 | 0 | 0.0005 | 14516.8342 | 7537.2848
August | 18307.2658 | 32.2294 | 122.9458 | 0 | 0.0006 | 15216.1864 | 7900.4636
September | 16744.1111 | 29.4741 | 112.4212 | 0 | 0.0005 | 13913.6217 | 7225.544
October | 16688.2704 | 29.3718 | 112.0149 | 0 | 0.0005 | 13863.3258 | 7201.0469
November | 15568.5182 | 27.3957 | 104.4569 | 0 | 0.0005 | 12927.9239 | 6717.3357
December | 15037.7778 | 26.4577 | 100.8642 | 0 | 0.0005 | 12483.2793 | 6487.9342
Annual Sum or Average | 195714.5051 | 344.4492 | 1313.5677 | 0 | 0.006 | 162571.4238 | 84450.149
Minimum of Months | 13969.9462 | 24.5789 | 93.7015 | 0 | 0.0004 | 11596.7975 | 6027.2218
Maximum of Months | 18307.2658 | 32.2294 | 122.9458 | 0 | 0.0006 | 15216.1864 | 7900.4636
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 85472100000 | 69993.379 | 06-JAN-13:00 | 9001.312 | 39217.651 | 6612.66 | 0 | 15161.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 78806700000 | 71066.778 | 22-FEB-15:00 | 9001.312 | 39217.651 | 6882.043 | 0 | 15965.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 91996100000 | 71580.525 | 13-MAR-14:00 | 9001.312 | 39217.651 | 6926.402 | 0 | 16435.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 89346000000 | 72535.063 | 03-APR-14:39 | 9001.312 | 39217.651 | 7141.347 | 0 | 17174.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 97418100000 | 75102.926 | 24-MAY-14:00 | 9001.312 | 39217.651 | 7579.103 | 0 | 19304.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 98228700000 | 76505.992 | 28-JUN-14:00 | 9001.312 | 39217.651 | 7868.662 | 0 | 20418.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 98650000000 | 75465.73 | 13-JUL-14:00 | 9001.312 | 39217.651 | 7745.525 | 0 | 19501.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 103402000000 | 76627.982 | 21-AUG-14:00 | 9001.312 | 39217.651 | 7940.696 | 0 | 20468.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 94550800000 | 75237.492 | 01-SEP-14:00 | 9001.312 | 39217.651 | 7694.221 | 0 | 19324.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 94209000000 | 74597.947 | 06-OCT-14:00 | 9001.312 | 39217.651 | 7630.947 | 0 | 18748.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 87852400000 | 72079.233 | 07-NOV-14:00 | 9001.312 | 39217.651 | 7094.809 | 0 | 16765.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 84830800000 | 70080.424 | 19-DEC-14:30 | 9001.312 | 39217.651 | 6652.476 | 0 | 15208.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1104760000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 78806700000 | 69993.379 |  | 9001.312 | 39217.651 | 6612.66 | 0 | 15161.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 103402000000 | 76627.982 |  | 9001.312 | 39217.651 | 7940.696 | 0 | 20468.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25579.33 | 183.51 | 0 | 25762.85
Cost per Total Building Area ($/m2) | 27.52 | 0.2 | 0 | 27.72
Cost per Net Conditioned Building Area ($/m2) | 27.52 | 0.2 | 0 | 27.72

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1061.59 | 1142.11 | 1142.11
Net Site Energy | 1061.59 | 1142.11 | 1142.11
Total Source Energy | 25.45 | 27.38 | 27.38
Net Source Energy | 25.45 | 27.38 | 27.38
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5.3 | 0 | 0 | 0 | 0
Cooling | 204.74 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 91.42 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.01 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1038.28 | 23.31 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 6.49 | 0.358 | 0.358
North Total or Average |  |  | 24.14 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 56.3 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67035.78 | 53176.5 | 13859.28 | 0.79 | 4.28
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38318.67 | 28809.48 | 9509.19 | 0.75 | 3.61
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11459.58 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20551.47 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 3.99 | 7485.49 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.02 | 2209.2 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17924.8372 | 23.4701 | 100.885 | 0 | 0.0003 | 34412.9697 | 7131.7363
February | 15880.0911 | 20.8213 | 89.7759 | 0 | 0.0003 | 30623.6705 | 6321.8695
March | 19479.252 | 25.5652 | 110.4717 | 0 | 0.0003 | 37683.3604 | 7757.9032
April | 19534.3303 | 25.6442 | 110.878 | 0 | 0.0003 | 37821.9968 | 7780.7038
May | 21961.1465 | 28.8344 | 124.714 | 0 | 0.0004 | 42541.6502 | 8747.8904
June | 22779.1885 | 29.9124 | 129.4137 | 0 | 0.0004 | 44144.8073 | 9074.2438
July | 23118.087 | 30.3591 | 131.3632 | 0 | 0.0004 | 44809.809 | 9209.4683
August | 23956.1895 | 31.4594 | 136.1209 | 0 | 0.0004 | 46432.7094 | 9543.2972
September | 21399.5224 | 28.0994 | 121.5573 | 0 | 0.0003 | 41464.8737 | 8524.4769
October | 20560.4442 | 26.9936 | 116.7346 | 0 | 0.0003 | 39819.76 | 8189.7115
November | 18586.0691 | 24.3966 | 105.4571 | 0 | 0.0003 | 35972.8289 | 7402.6478
December | 17436.2455 | 22.8464 | 98.3605 | 0 | 0.0003 | 33551.9158 | 6939.4156
Annual Sum or Average | 242615.4035 | 318.4021 | 1375.7321 | 0 | 0.0039 | 469280.3518 | 96623.3643
Minimum of Months | 15880.0911 | 20.8213 | 89.7759 | 0 | 0.0003 | 30623.6705 | 6321.8695
Maximum of Months | 23956.1895 | 31.4594 | 136.1209 | 0 | 0.0004 | 46432.7094 | 9543.2972
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 76138800000 | 68042.494 | 03-JAN-14:30 | 9001.312 | 39217.651 | 6030.679 | 0 | 13792.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67754900000 | 68953.21 | 23-FEB-15:30 | 9001.312 | 39217.651 | 6183.953 | 0 | 14550.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 83374500000 | 68204.515 | 28-MAR-14:00 | 9001.312 | 39217.651 | 6131.13 | 0 | 13854.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 83681200000 | 70835.69 | 21-APR-14:00 | 9001.312 | 39217.651 | 6698.041 | 0 | 15918.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 94123500000 | 75537.542 | 18-MAY-14:00 | 9001.312 | 39217.651 | 7673.252 | 0 | 19645.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 97670500000 | 76116.453 | 13-JUN-14:00 | 9001.312 | 39217.651 | 7695.255 | 0 | 20202.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 99141800000 | 76922.065 | 18-JUL-12:00 | 9001.312 | 39217.651 | 7928.108 | 0 | 20774.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 102732000000 | 77419.677 | 31-AUG-14:30 | 9001.312 | 39217.651 | 8009.763 | 0 | 21190.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 91741100000 | 76103.73 | 15-SEP-14:00 | 9001.312 | 39217.651 | 7819.673 | 0 | 20065.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 88101300000 | 72508.918 | 12-OCT-14:00 | 9001.312 | 39217.651 | 7094.397 | 0 | 17195.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 79590000000 | 69399.513 | 03-NOV-14:39 | 9001.312 | 39217.651 | 6393.29 | 0 | 14787.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74233700000 | 68379.864 | 19-DEC-15:30 | 9001.312 | 39217.651 | 6125.586 | 0 | 14035.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1038280000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67754900000 | 68042.494 |  | 9001.312 | 39217.651 | 6030.679 | 0 | 13792.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 102732000000 | 77419.677 |  | 9001.312 | 39217.651 | 8009.763 | 0 | 21190.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33220.25 | 190.52 | 0 | 33410.77
Cost per Total Building Area ($/m2) | 35.74 | 0.2 | 0 | 35.94
Cost per Net Conditioned Building Area ($/m2) | 35.74 | 0.2 | 0 | 35.94

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1096.09 | 1179.22 | 1179.22
Net Site Energy | 1096.09 | 1179.22 | 1179.22
Total Source Energy | 3428.96 | 3689.02 | 3689.02
Net Source Energy | 3428.96 | 3689.02 | 3689.02
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1.47 | 0 | 0 | 0 | 0
Cooling | 185.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 149.82 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 16.86 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1077.76 | 18.33 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.25 | 0.25 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 6.49 | 0.358 | 0.358
North Total or Average |  |  | 24.14 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 56.3 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70183.4 | 56052.34 | 14131.06 | 0.8 | 4.32
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41088.95 | 32408.86 | 8680.09 | 0.79 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 8707.73 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15661.3 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.24 | 7953.78 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.42 | 2641.44 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14582.7079 | 24.5638 | 81.998 | 0 | 0.0002 | 605711.085 | 6192.4996
February | 13383.8655 | 22.5551 | 75.3343 | 0 | 0.0002 | 556487.1492 | 5684.4956
March | 17684.5833 | 29.8217 | 99.6778 | 0 | 0.0003 | 736311.3103 | 7513.0283
April | 17578.1687 | 29.6529 | 99.155 | 0 | 0.0003 | 732450.0138 | 7468.8961
May | 19355.4961 | 32.6593 | 109.2403 | 0 | 0.0003 | 806950.033 | 8224.9114
June | 20563.2044 | 34.707 | 116.1279 | 0 | 0.0003 | 857828.7504 | 8739.1127
July | 20744.4405 | 35.0154 | 117.1694 | 0 | 0.0003 | 865522.3559 | 8816.3874
August | 21315.1993 | 35.9775 | 120.3839 | 0 | 0.0003 | 889267.1429 | 9058.8294
September | 19038.8824 | 32.1294 | 107.4845 | 0 | 0.0003 | 793979.768 | 8090.8041
October | 18441.0291 | 31.112 | 104.0482 | 0 | 0.0003 | 768595.6801 | 7835.8849
November | 16412.4037 | 27.6783 | 92.5209 | 0 | 0.0003 | 683443.9596 | 6972.7527
December | 14388.402 | 24.2105 | 80.7174 | 0 | 0.0002 | 596249.7692 | 6107.3592
Annual Sum or Average | 213488.3829 | 360.0829 | 1203.8574 | 0 | 0.0033 | 8892800 | 90704.9614
Minimum of Months | 13383.8655 | 22.5551 | 75.3343 | 0 | 0.0002 | 556487.1492 | 5684.4956
Maximum of Months | 21315.1993 | 35.9775 | 120.3839 | 0 | 0.0003 | 889267.1429 | 9058.8294
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73408700000 | 65747.321 | 26-JAN-15:00 | 9001.312 | 39217.651 | 5766.716 | 0 | 11761.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67443000000 | 67722.369 | 28-FEB-15:00 | 9001.312 | 39217.651 | 6126.953 | 0 | 13376.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 89236600000 | 72258.434 | 17-MAR-14:00 | 9001.312 | 39217.651 | 7087.179 | 0 | 16952.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 88768700000 | 72966.135 | 26-APR-14:00 | 9001.312 | 39217.651 | 7258.04 | 0 | 17489.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 97797600000 | 76637.481 | 30-MAY-14:00 | 9001.312 | 39217.651 | 7885.077 | 0 | 20533.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 103964000000 | 85228.488 | 08-JUN-14:00 | 9001.312 | 39217.651 | 9673.64 | 0 | 27335.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 104896000000 | 84010.072 | 19-JUL-14:00 | 9001.312 | 39217.651 | 9182.939 | 0 | 26608.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 107774000000 | 84177.339 | 01-AUG-14:00 | 9001.312 | 39217.651 | 9223.942 | 0 | 26734.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 96225700000 | 80113.686 | 08-SEP-14:30 | 9001.312 | 39217.651 | 8538.217 | 0 | 23356.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 93149300000 | 74726.967 | 03-OCT-12:30 | 9001.312 | 39217.651 | 8270.804 | 0 | 18237.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 82829400000 | 69885.26 | 13-NOV-15:39 | 9001.312 | 39217.651 | 6565.77 | 0 | 15100.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 72262000000 | 64620.212 | 11-DEC-15:00 | 9001.312 | 39217.651 | 5434.904 | 0 | 10966.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1077760000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67443000000 | 64620.212 |  | 9001.312 | 39217.651 | 5434.904 | 0 | 10966.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 107774000000 | 85228.488 |  | 9001.312 | 39217.651 | 9673.64 | 0 | 27335.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 30843.95 | 157.16 | 0 | 31001.11
Cost per Total Building Area ($/m2) | 33.18 | 0.17 | 0 | 33.35
Cost per Net Conditioned Building Area ($/m2) | 33.18 | 0.17 | 0 | 33.35

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1014.18 | 1091.1 | 1091.1
Net Site Energy | 1014.18 | 1091.1 | 1091.1
Total Source Energy | 3351.04 | 3605.19 | 3605.19
Net Source Energy | 3351.04 | 3605.19 | 3605.19
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6.75 | 0 | 0 | 0 | 0
Cooling | 164.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 80.61 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.95 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 987.48 | 26.7 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.334 | 0.41
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 66524.04 | 53129.78 | 13394.27 | 0.8 | 4.32
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35518.35 | 27337.16 | 8181.19 | 0.77 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13328.19 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22230.25 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.02 | 7539.07 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.98 | 2161.51 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14272.0862 | 27.2743 | 70.2569 | 0 | 0.0003 | 124970.6623 | 6262.0428
February | 13050.1244 | 25.0337 | 64.7054 | 0 | 0.0002 | 115096.7685 | 5734.6319
March | 15711.4327 | 30.2263 | 78.3297 | 0 | 0.0003 | 139332.1614 | 6912.1744
April | 15423.6695 | 29.6921 | 76.9901 | 0 | 0.0003 | 136949.4335 | 6787.3646
May | 17447.4424 | 33.6017 | 87.1589 | 0 | 0.0003 | 155037.8036 | 7679.2078
June | 18096.8536 | 34.8631 | 90.4554 | 0 | 0.0003 | 160901.6025 | 7966.0209
July | 18302.8212 | 35.2657 | 91.5136 | 0 | 0.0003 | 162784.0731 | 8057.227
August | 19115.4017 | 36.8304 | 95.5714 | 0 | 0.0003 | 170002.0032 | 8414.843
September | 17222.3439 | 33.1783 | 86.084 | 0 | 0.0003 | 153125.7456 | 7581.0671
October | 15995.221 | 30.8014 | 79.8871 | 0 | 0.0003 | 142102.6156 | 7039.7107
November | 14445.473 | 27.7998 | 72.0622 | 0 | 0.0003 | 128183.6954 | 6356.0497
December | 14076.8886 | 27.0014 | 69.7867 | 0 | 0.0003 | 124135.2308 | 6185.6424
Annual Sum or Average | 193159.7582 | 371.5683 | 962.8016 | 0 | 0.0035 | 1712620 | 84975.9824
Minimum of Months | 13050.1244 | 25.0337 | 64.7054 | 0 | 0.0002 | 115096.7685 | 5734.6319
Maximum of Months | 19115.4017 | 36.8304 | 95.5714 | 0 | 0.0003 | 170002.0032 | 8414.843
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 72056900000 | 63450.267 | 23-JAN-15:00 | 9001.312 | 39217.651 | 5155.022 | 0 | 10076.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66363700000 | 63210.846 | 22-FEB-14:00 | 9001.312 | 39217.651 | 5060.92 | 0 | 9930.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 80337600000 | 66363.766 | 28-MAR-14:00 | 9001.312 | 39217.651 | 5828.483 | 0 | 12316.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 78963700000 | 68991.421 | 14-APR-14:00 | 9001.312 | 39217.651 | 6413.648 | 0 | 14358.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 89393300000 | 71739.501 | 15-MAY-14:00 | 9001.312 | 39217.651 | 7046.899 | 0 | 16473.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 92774300000 | 74128.148 | 19-JUN-14:00 | 9001.312 | 39217.651 | 7457.772 | 0 | 18451.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 93859800000 | 77226.038 | 03-JUL-14:00 | 9001.312 | 39217.651 | 8094.686 | 0 | 20912.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 98021500000 | 75069.157 | 17-AUG-13:00 | 9001.312 | 39217.651 | 7764.079 | 0 | 19086.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 88290900000 | 72588.911 | 11-SEP-13:00 | 9001.312 | 39217.651 | 7279.334 | 0 | 17090.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 81935000000 | 68300.804 | 12-OCT-14:00 | 9001.312 | 39217.651 | 6315.347 | 0 | 13766.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 73909500000 | 65399.725 | 22-NOV-14:00 | 9001.312 | 39217.651 | 5654.138 | 0 | 11526.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 71575200000 | 62872.728 | 05-DEC-14:00 | 9001.312 | 39217.651 | 4978.041 | 0 | 9675.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 987482000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66363700000 | 62872.728 |  | 9001.312 | 39217.651 | 4978.041 | 0 | 9675.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 98021500000 | 77226.038 |  | 9001.312 | 39217.651 | 8094.686 | 0 | 20912.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28431.83 | 280.21 | 0 | 28712.04
Cost per Total Building Area ($/m2) | 30.59 | 0.3 | 0 | 30.89
Cost per Net Conditioned Building Area ($/m2) | 30.59 | 0.3 | 0 | 30.89

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1032.9 | 1111.24 | 1111.24
Net Site Energy | 1032.9 | 1111.24 | 1111.24
Total Source Energy | 3157.58 | 3397.06 | 3397.06
Net Source Energy | 3157.58 | 3397.06 | 3397.06
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 0.01 | 0 | 0 | 0 | 0
Cooling | 75.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 195.77 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.58 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1013.31 | 19.59 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.334 | 0.41
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61969.98 | 49492.65 | 12477.33 | 0.8 | 4.36
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28808.18 | 23007.81 | 5800.38 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 8131.15 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11009.2 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.74 | 7140.67 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.74 | 1903.24 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6745.0683 | 5.7769 | 62.068 | 0 | 0 | 374505.7108 | 2523.8465
February | 6205.3079 | 5.3146 | 57.1168 | 0 | 0 | 344631.5267 | 2321.9287
March | 7359.8487 | 6.3032 | 67.7751 | 0 | 0 | 408941.4356 | 2754.0352
April | 7077.6277 | 6.0613 | 65.2201 | 0 | 0 | 393525.4595 | 2648.5629
May | 7701.113 | 6.5949 | 71.0137 | 0 | 0 | 428482.9613 | 2882.0282
June | 7728.5614 | 6.6183 | 71.301 | 0 | 0 | 430216.6805 | 2892.4047
July | 7978.0123 | 6.8316 | 73.6521 | 0 | 0 | 444402.4497 | 2985.913
August | 8548.9322 | 7.3204 | 78.9308 | 0 | 0 | 476253.5346 | 3199.6146
September | 7780.598 | 6.6626 | 71.8168 | 0 | 0 | 433329.0486 | 2911.9884
October | 7691.6416 | 6.5867 | 70.9457 | 0 | 0 | 428072.7237 | 2878.5427
November | 7113.4095 | 6.0919 | 65.5488 | 0 | 0 | 395508.2533 | 2661.9497
December | 6914.0725 | 5.9214 | 63.6731 | 0 | 0 | 384190.9823 | 2587.2363
Annual Sum or Average | 88844.193 | 76.0838 | 819.0622 | 0 | 0.0004 | 4942060 | 33248.0509
Minimum of Months | 6205.3079 | 5.3146 | 57.1168 | 0 | 0 | 344631.5267 | 2321.9287
Maximum of Months | 8548.9322 | 7.3204 | 78.9308 | 0 | 0 | 476253.5346 | 3199.6146
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 76787700000 | 66431.877 | 26-JAN-13:00 | 9001.312 | 39217.651 | 5978.114 | 0 | 12234.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 70662400000 | 64858.726 | 13-FEB-11:00 | 9001.312 | 39217.651 | 5512.4 | 0 | 11127.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 83848400000 | 65798.763 | 31-MAR-14:50 | 9001.312 | 39217.651 | 6022.859 | 0 | 11556.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 80687500000 | 67833.253 | 11-APR-13:00 | 9001.312 | 39217.651 | 6499.234 | 0 | 13115.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 87855100000 | 70306.542 | 30-MAY-12:00 | 9001.312 | 39217.651 | 7223.611 | 0 | 14863.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 88210600000 | 69979.889 | 28-JUN-13:00 | 9001.312 | 39217.651 | 7111.863 | 0 | 14649.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 91119200000 | 72149.763 | 20-JUL-14:00 | 9001.312 | 39217.651 | 7824.699 | 0 | 16106.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 97649900000 | 76065.093 | 09-AUG-14:50 | 9001.312 | 39217.651 | 8918.003 | 0 | 18928.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 88848700000 | 72522.084 | 07-SEP-09:00 | 9001.312 | 39217.651 | 7923.785 | 0 | 16379.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 87771000000 | 69088.176 | 05-OCT-10:20 | 9001.312 | 39217.651 | 6866.143 | 0 | 14003.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 81094100000 | 66060.442 | 20-NOV-13:00 | 9001.312 | 39217.651 | 5816.407 | 0 | 12025.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 78773600000 | 66312.516 | 19-DEC-13:09 | 9001.312 | 39217.651 | 5922.04 | 0 | 12171.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1013310000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 70662400000 | 64858.726 |  | 9001.312 | 39217.651 | 5512.4 | 0 | 11127.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 97649900000 | 76065.093 |  | 9001.312 | 39217.651 | 8918.003 | 0 | 18928.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 36472.22 | 164.41 | 0 | 36636.63
Cost per Total Building Area ($/m2) | 39.24 | 0.18 | 0 | 39.42
Cost per Net Conditioned Building Area ($/m2) | 39.24 | 0.18 | 0 | 39.42

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1050.47 | 1130.14 | 1130.14
Net Site Energy | 1050.47 | 1130.14 | 1130.14
Total Source Energy | 3708.67 | 3989.94 | 3989.94
Net Source Energy | 3708.67 | 3989.94 | 3989.94
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1.41 | 0 | 0 | 0 | 0
Cooling | 143.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 145.23 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.25 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1030.81 | 19.66 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.262 | 0.318 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.334 | 0.41
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.262 | 0.318
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70442.43 | 56259.22 | 14183.21 | 0.8 | 4.18
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38899.09 | 31066.96 | 7832.13 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 9824.46 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17446.97 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.26 | 7983.14 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.35 | 2569.91 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15543.7577 | 25.3859 | 106.05 | 0 | 0.0002 | 528896.825 | 6551.7855
February | 15139.4197 | 24.7641 | 103.653 | 0 | 0.0002 | 516943.6784 | 6385.3538
March | 17852.0111 | 29.204 | 122.2518 | 0 | 0.0002 | 609700.6838 | 7529.7407
April | 19159.238 | 31.3607 | 131.3755 | 0 | 0.0002 | 655203.365 | 8083.0101
May | 20897.8228 | 34.2146 | 143.373 | 0 | 0.0003 | 715038.5523 | 8817.335
June | 22230.0272 | 36.4058 | 152.6072 | 0 | 0.0003 | 761092.2095 | 9380.4704
July | 22449.4692 | 36.7692 | 154.1514 | 0 | 0.0003 | 768793.7969 | 9473.4867
August | 23243.2022 | 38.0681 | 159.5908 | 0 | 0.0003 | 795921.391 | 9808.3152
September | 20794.7918 | 34.0525 | 142.7279 | 0 | 0.0003 | 711821.6214 | 8774.5468
October | 20000.605 | 32.7437 | 137.1985 | 0 | 0.0003 | 684244.6808 | 8438.5656
November | 16849.9827 | 27.5717 | 115.4546 | 0 | 0.0002 | 575801.5464 | 7107.8145
December | 15600.16 | 25.5005 | 106.6453 | 0 | 0.0002 | 531866.3371 | 6577.8865
Annual Sum or Average | 229760.4875 | 376.0408 | 1575.079 | 0 | 0.003 | 7855320 | 96928.3109
Minimum of Months | 15139.4197 | 24.7641 | 103.653 | 0 | 0.0002 | 516943.6784 | 6385.3538
Maximum of Months | 23243.2022 | 38.0681 | 159.5908 | 0 | 0.0003 | 795921.391 | 9808.3152
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69404000000 | 60829.845 | 18-JAN-14:00 | 9001.312 | 39217.651 | 4466.653 | 0 | 8144.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67835400000 | 63313.083 | 08-FEB-15:00 | 9001.312 | 39217.651 | 5227.573 | 0 | 9866.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 80007400000 | 66808.932 | 31-MAR-14:00 | 9001.312 | 39217.651 | 6070.746 | 0 | 12519.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 85978400000 | 72462.894 | 21-APR-14:00 | 9001.312 | 39217.651 | 7175.246 | 0 | 17068.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 93830200000 | 74948.605 | 31-MAY-14:00 | 9001.312 | 39217.651 | 7723.97 | 0 | 19005.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 99873600000 | 83071.001 | 27-JUN-14:00 | 9001.312 | 39217.651 | 9360.414 | 0 | 25491.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 100884000000 | 80982.417 | 24-JUL-14:00 | 9001.312 | 39217.651 | 8858.994 | 0 | 23904.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 104444000000 | 80299.224 | 04-AUG-14:00 | 9001.312 | 39217.651 | 8589.909 | 0 | 23490.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 93408100000 | 79317.517 | 01-SEP-14:00 | 9001.312 | 39217.651 | 8504.741 | 0 | 22593.812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 89789400000 | 72683.633 | 03-OCT-14:00 | 9001.312 | 39217.651 | 7285.37 | 0 | 17179.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 75559000000 | 64168.464 | 10-NOV-14:39 | 9001.312 | 39217.651 | 5464.976 | 0 | 10484.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 69793600000 | 63510.775 | 05-DEC-14:00 | 9001.312 | 39217.651 | 5289.718 | 0 | 10002.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1030810000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67835400000 | 60829.845 |  | 9001.312 | 39217.651 | 4466.653 | 0 | 8144.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 104444000000 | 83071.001 |  | 9001.312 | 39217.651 | 9360.414 | 0 | 25491.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28271.7 | 159.68 | 0 | 28431.37
Cost per Total Building Area ($/m2) | 30.42 | 0.17 | 0 | 30.59
Cost per Net Conditioned Building Area ($/m2) | 30.42 | 0.17 | 0 | 30.59

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 928.28 | 998.68 | 998.68
Net Site Energy | 928.28 | 998.68 | 998.68
Total Source Energy | 2825.89 | 3040.21 | 3040.21
Net Source Energy | 2825.89 | 3040.21 | 3040.21
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2.29 | 0 | 0 | 0 | 0
Cooling | 29.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 132.74 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.24 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 904.75 | 23.53 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.391 | 0.39 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.391 | 0.39 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.391 | 0.39 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 6.49 | 0.61 | 0.61 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 6.49 | 0.391 | 0.39 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 6.49 | 0.391 | 0.39 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 6.49 | 0.391 | 0.39 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 6.49 | 0.456 | 0.456
North Total or Average |  |  | 24.14 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 56.3 | 6.49 | 0.391 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 59466.35 | 47493.11 | 11973.24 | 0.8 | 4.37
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29205.12 | 23324.83 | 5880.3 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 8987.6 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15598.75 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.59 | 6852.18 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.76 | 1929.46 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6027.8457 | 5.1669 | 54.7036 | 0 | 0 | 330067.6538 | 2253.1459
February | 5702.9249 | 4.8851 | 52.3569 | 0 | 0 | 315910.4743 | 2133.5307
March | 6533.5302 | 5.5967 | 59.9563 | 0 | 0 | 361763.4834 | 2444.19
April | 6312.0181 | 5.4066 | 57.9906 | 0 | 0 | 349903.2647 | 2361.5271
May | 6935.3494 | 5.94 | 63.7958 | 0 | 0 | 384930.776 | 2594.9745
June | 7041.7085 | 6.0309 | 64.8241 | 0 | 0 | 391135.6973 | 2634.923
July | 7174.131 | 6.144 | 66.0888 | 0 | 0 | 398766.7186 | 2684.6131
August | 7565.7391 | 6.4794 | 69.6953 | 0 | 0 | 420527.3717 | 2831.1525
September | 7134.5804 | 6.1101 | 65.7259 | 0 | 0 | 396576.76 | 2669.8172
October | 6980.8136 | 5.9787 | 64.2554 | 0 | 0 | 387703.9868 | 2612.1119
November | 6286.1505 | 5.3844 | 57.7603 | 0 | 0 | 348513.8792 | 2351.8718
December | 5945.6115 | 5.0953 | 54.1606 | 0 | 0 | 326792.3092 | 2223.028
Annual Sum or Average | 79640.4029 | 68.2181 | 731.3135 | 0 | 0.0003 | 4412590 | 29794.8858
Minimum of Months | 5702.9249 | 4.8851 | 52.3569 | 0 | 0 | 315910.4743 | 2133.5307
Maximum of Months | 7565.7391 | 6.4794 | 69.6953 | 0 | 0 | 420527.3717 | 2831.1525
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67676300000 | 55737.112 | 27-JAN-15:39 | 9001.312 | 39217.651 | 7518.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 64773500000 | 63900.756 | 15-FEB-15:00 | 9001.312 | 39217.651 | 5347.439 | 0 | 10334.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74175100000 | 58923.381 | 01-MAR-13:09 | 9001.312 | 39217.651 | 5091.532 | 0 | 5612.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 71743300000 | 64224.508 | 13-APR-14:00 | 9001.312 | 39217.651 | 5539.031 | 0 | 10466.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 78925300000 | 66255.972 | 17-MAY-13:00 | 9001.312 | 39217.651 | 5870.33 | 0 | 12166.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 80197500000 | 66558.743 | 16-JUN-14:00 | 9001.312 | 39217.651 | 5990.873 | 0 | 12348.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 81762200000 | 68655.415 | 03-JUL-12:00 | 9001.312 | 39217.651 | 6340.54 | 0 | 14095.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 86223900000 | 67722.474 | 15-AUG-12:20 | 9001.312 | 39217.651 | 6164.029 | 0 | 13339.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 81313100000 | 71952.209 | 28-SEP-14:00 | 9001.312 | 39217.651 | 7089.314 | 0 | 16643.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 79493900000 | 65862.532 | 13-OCT-14:00 | 9001.312 | 39217.651 | 5878.887 | 0 | 11764.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71458400000 | 58571.941 | 08-NOV-14:30 | 9001.312 | 39217.651 | 5006.062 | 0 | 5346.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67004700000 | 57253.727 | 07-DEC-14:00 | 9001.312 | 39217.651 | 4203.127 | 0 | 4831.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 904747000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 64773500000 | 55737.112 |  | 9001.312 | 39217.651 | 4203.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 86223900000 | 71952.209 |  | 9001.312 | 39217.651 | 7518.149 | 0 | 16643.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37974.92 | 199.12 | 0 | 38174.04
Cost per Total Building Area ($/m2) | 40.86 | 0.21 | 0 | 41.07
Cost per Net Conditioned Building Area ($/m2) | 40.86 | 0.21 | 0 | 41.07

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 996.65 | 1072.24 | 1072.24
Net Site Energy | 996.65 | 1072.24 | 1072.24
Total Source Energy | 3466.73 | 3729.66 | 3729.66
Net Source Energy | 3466.73 | 3729.66 | 3729.66
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 17.69 | 0 | 0 | 0 | 0
Cooling | 144.26 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 71.1 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.48 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 957.48 | 39.17 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65795.48 | 52421.48 | 13374.01 | 0.8 | 4.31
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37647.04 | 28437.64 | 9209.4 | 0.76 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16660.37 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25755.21 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 3.95 | 7417.53 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.01 | 2194.4 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 12295.3054 | 24.0226 | 71.071 | 0 | 0.0003 | 4420.1142 | 5431.5065
February | 11064.4308 | 21.7928 | 64.923 | 0 | 0.0003 | 4037.8059 | 4903.7736
March | 13062.8058 | 25.9722 | 77.992 | 0 | 0.0003 | 4850.6922 | 5811.6989
April | 12536.9806 | 24.9589 | 75.0307 | 0 | 0.0003 | 4666.5243 | 5580.7072
May | 14232.5174 | 28.353 | 85.2804 | 0 | 0.0003 | 5304.0047 | 6337.1516
June | 15477.1964 | 30.85 | 92.835 | 0 | 0.0004 | 5773.8696 | 6892.9553
July | 15784.8937 | 31.4717 | 94.7267 | 0 | 0.0004 | 5891.5263 | 7030.755
August | 16577.5834 | 33.0524 | 99.4853 | 0 | 0.0004 | 6187.4876 | 7383.8536
September | 14201.102 | 28.3058 | 85.1769 | 0 | 0.0003 | 5297.5729 | 6324.5671
October | 13480.7641 | 26.853 | 80.7627 | 0 | 0.0003 | 5023.0266 | 6002.2078
November | 12350.81 | 24.5453 | 73.6788 | 0 | 0.0003 | 4582.4303 | 5493.8987
December | 11929.233 | 23.485 | 69.9356 | 0 | 0.0003 | 4349.5573 | 5286.0322
Annual Sum or Average | 162993.6226 | 323.6627 | 970.8981 | 0 | 0.0039 | 60384.6118 | 72479.1075
Minimum of Months | 11064.4308 | 21.7928 | 64.923 | 0 | 0.0003 | 4037.8059 | 4903.7736
Maximum of Months | 16577.5834 | 33.0524 | 99.4853 | 0 | 0.0004 | 6187.4876 | 7383.8536
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 70087100000 | 60231.962 | 05-JAN-15:09 | 9001.312 | 39217.651 | 4268.638 | 0 | 7744.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 64025100000 | 60820.292 | 15-FEB-15:00 | 9001.312 | 39217.651 | 4369.226 | 0 | 8232.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 76914500000 | 66100.455 | 09-MAR-15:00 | 9001.312 | 39217.651 | 5643.794 | 0 | 12237.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 73994300000 | 67093.246 | 04-APR-14:00 | 9001.312 | 39217.651 | 5931.386 | 0 | 12942.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 84102400000 | 69898.301 | 31-MAY-14:00 | 9001.312 | 39217.651 | 6611.282 | 0 | 15068.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 91552800000 | 76652.575 | 30-JUN-14:00 | 9001.312 | 39217.651 | 7915.364 | 0 | 20518.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 93418400000 | 77809.484 | 25-JUL-13:50 | 9001.312 | 39217.651 | 8152.878 | 0 | 21437.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 98111300000 | 78258.303 | 17-AUG-14:00 | 9001.312 | 39217.651 | 8326.929 | 0 | 21712.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 84000500000 | 73765.415 | 08-SEP-14:00 | 9001.312 | 39217.651 | 7300.634 | 0 | 18245.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 79647100000 | 69639.435 | 12-OCT-14:00 | 9001.312 | 39217.651 | 6536.743 | 0 | 14883.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 72660900000 | 67104.873 | 03-NOV-14:20 | 9001.312 | 39217.651 | 5954.836 | 0 | 12931.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 68968300000 | 59502.893 | 06-DEC-15:09 | 9001.312 | 39217.651 | 4051.336 | 0 | 7232.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 957483000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 64025100000 | 59502.893 |  | 9001.312 | 39217.651 | 4051.336 | 0 | 7232.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 98111300000 | 78258.303 |  | 9001.312 | 39217.651 | 8326.929 | 0 | 21712.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20135.79 | 388.37 | 0 | 20524.16
Cost per Total Building Area ($/m2) | 21.66 | 0.42 | 0 | 22.08
Cost per Net Conditioned Building Area ($/m2) | 21.66 | 0.42 | 0 | 22.08

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1016.35 | 1093.43 | 1093.43
Net Site Energy | 1016.35 | 1093.43 | 1093.43
Total Source Energy | 3308 | 3558.88 | 3558.88
Net Source Energy | 3308 | 3558.88 | 3558.88
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7.67 | 0 | 0 | 0 | 0
Cooling | 92.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 152.51 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.19 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 987.49 | 28.86 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 77063.11 | 61546.86 | 15516.25 | 0.8 | 4.18
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39233.4 | 31333.96 | 7899.44 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13271.4 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21848.84 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.66 | 8733.45 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.37 | 2591.99 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18424.2939 | 32.1122 | 83.3679 | 0 | 0.0003 | 86688.3637 | 7886.1043
February | 16857.1613 | 29.4615 | 76.7139 | 0 | 0.0003 | 79769.8757 | 7223.2503
March | 20362.7816 | 35.6224 | 92.8518 | 0 | 0.0004 | 96550.8714 | 8728.7426
April | 20850.8482 | 36.5038 | 95.2264 | 0 | 0.0004 | 99020.2755 | 8940.6601
May | 24588.7207 | 43.0624 | 112.3769 | 0 | 0.0004 | 116854.1811 | 10544.8688
June | 25550.7232 | 44.7569 | 116.8258 | 0 | 0.0005 | 121480.3268 | 10958.3699
July | 25627.5003 | 44.897 | 117.2076 | 0 | 0.0005 | 121877.3942 | 10991.8563
August | 26937.222 | 47.1913 | 123.1963 | 0 | 0.0005 | 128104.6861 | 11553.5831
September | 24391.6815 | 42.7279 | 111.5334 | 0 | 0.0004 | 115977.0772 | 10461.4008
October | 22066.5479 | 38.6415 | 100.829 | 0 | 0.0004 | 104846.1337 | 9462.8558
November | 18843.9909 | 32.9427 | 85.8028 | 0 | 0.0003 | 89220.9589 | 8075.4581
December | 18093.5611 | 31.5405 | 81.8973 | 0 | 0.0003 | 85159.2978 | 7745.0129
Annual Sum or Average | 262595.0328 | 459.4601 | 1197.829 | 0 | 0.0047 | 1245550 | 112572.163
Minimum of Months | 16857.1613 | 29.4615 | 76.7139 | 0 | 0.0003 | 79769.8757 | 7223.2503
Maximum of Months | 26937.222 | 47.1913 | 123.1963 | 0 | 0.0005 | 128104.6861 | 11553.5831
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68727600000 | 58294.222 | 26-JAN-15:00 | 9001.312 | 39217.651 | 4885.352 | 0 | 5189.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 63242500000 | 63936.349 | 14-FEB-15:00 | 9001.312 | 39217.651 | 5456.285 | 0 | 10261.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 76546700000 | 64710.613 | 02-MAR-14:00 | 9001.312 | 39217.651 | 5682.434 | 0 | 10809.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 78504500000 | 69389.068 | 21-APR-14:00 | 9001.312 | 39217.651 | 6846.767 | 0 | 14323.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 92643400000 | 71940.108 | 31-MAY-14:00 | 9001.312 | 39217.651 | 7204.666 | 0 | 16516.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 96311100000 | 75558.961 | 29-JUN-14:00 | 9001.312 | 39217.651 | 7944.028 | 0 | 19395.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 96625900000 | 76645.561 | 31-JUL-14:00 | 9001.312 | 39217.651 | 8179.645 | 0 | 20246.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 101563000000 | 76898.798 | 01-AUG-14:30 | 9001.312 | 39217.651 | 8250.15 | 0 | 20429.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 91948000000 | 75049.085 | 05-SEP-13:09 | 9001.312 | 39217.651 | 8507.14 | 0 | 18322.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 83123300000 | 69521.029 | 13-OCT-14:00 | 9001.312 | 39217.651 | 6910.568 | 0 | 14391.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 70735500000 | 62329.04 | 08-NOV-15:20 | 9001.312 | 39217.651 | 4943.516 | 0 | 9166.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67515300000 | 57598.376 | 08-DEC-15:20 | 9001.312 | 39217.651 | 9379.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 987487000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 63242500000 | 57598.376 |  | 9001.312 | 39217.651 | 4885.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 101563000000 | 76898.798 |  | 9001.312 | 39217.651 | 9379.413 | 0 | 20429.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10321.95 | 205.37 | 0 | 10527.32
Cost per Total Building Area ($/m2) | 11.1 | 0.22 | 0 | 11.33
Cost per Net Conditioned Building Area ($/m2) | 11.1 | 0.22 | 0 | 11.33

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 924.15 | 994.24 | 994.24
Net Site Energy | 924.15 | 994.24 | 994.24
Total Source Energy | 1589.58 | 1710.14 | 1710.14
Net Source Energy | 1589.58 | 1710.14 | 1710.14
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8.93 | 0 | 0 | 0 | 0
Cooling | 29.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 121.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.28 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 892.94 | 31.21 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.704 | 0.79 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.704 | 0.79 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 62427.33 | 49857.92 | 12569.42 | 0.8 | 4.37
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31047.01 | 24795.85 | 6251.15 | 0.8 | 3.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11702.5 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20215.15 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.77 | 7193.37 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.88 | 2051.15 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3426.6413 | 5.3229 | 14.1409 | 0 | 0.0001 | 186902.6088 | 1422.9276
February | 3083.4826 | 4.8532 | 13.1292 | 0 | 0.0001 | 173538.238 | 1287.2145
March | 3602.4083 | 5.6838 | 15.4268 | 0 | 0.0001 | 203908.0131 | 1505.3187
April | 3449.2529 | 5.4653 | 14.9189 | 0 | 0.0001 | 197196.8712 | 1443.8023
May | 3912.31 | 6.2162 | 17.0313 | 0 | 0.0001 | 225120.6008 | 1639.469
June | 4070.6993 | 6.4743 | 17.7621 | 0 | 0.0001 | 234780.9792 | 1706.5353
July | 4228.2535 | 6.7308 | 18.4875 | 0 | 0.0001 | 244369.5196 | 1773.2214
August | 4471.9728 | 7.1186 | 19.5519 | 0 | 0.0001 | 258439.3962 | 1875.4111
September | 3930.5276 | 6.2529 | 17.1603 | 0 | 0.0001 | 226825.8506 | 1647.9359
October | 3677.0953 | 5.8385 | 15.9819 | 0 | 0.0001 | 211248.6697 | 1540.4738
November | 3326.417 | 5.2391 | 14.1858 | 0 | 0.0001 | 187503.9403 | 1389.0004
December | 3361.6486 | 5.2335 | 13.9461 | 0 | 0.0001 | 184329.7812 | 1397.1713
Annual Sum or Average | 44540.7092 | 70.429 | 191.7226 | 0 | 0.0007 | 2534160 | 18628.4814
Minimum of Months | 3083.4826 | 4.8532 | 13.1292 | 0 | 0.0001 | 173538.238 | 1287.2145
Maximum of Months | 4471.9728 | 7.1186 | 19.5519 | 0 | 0.0001 | 258439.3962 | 1875.4111
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 65857200000 | 54850.809 | 31-JAN-09:50 | 9001.312 | 39217.651 | 2606.11 | 0 | 4025.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61148100000 | 56518.408 | 21-FEB-13:00 | 9001.312 | 39217.651 | 3892.93 | 0 | 4406.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 71849200000 | 61414.564 | 29-MAR-14:00 | 9001.312 | 39217.651 | 4741.183 | 0 | 8454.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 69484500000 | 59500.587 | 14-APR-13:00 | 9001.312 | 39217.651 | 4094.563 | 0 | 7187.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 79323700000 | 67009.861 | 04-MAY-14:00 | 9001.312 | 39217.651 | 6192.289 | 0 | 12598.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 82727600000 | 68335.445 | 28-JUN-14:00 | 9001.312 | 39217.651 | 6457.698 | 0 | 13658.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 86106200000 | 70520.569 | 24-JUL-14:00 | 9001.312 | 39217.651 | 6875.044 | 0 | 15426.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 91063900000 | 69588.619 | 07-AUG-14:00 | 9001.312 | 39217.651 | 6748.177 | 0 | 14621.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 79924500000 | 69929.775 | 01-SEP-14:00 | 9001.312 | 39217.651 | 6784.989 | 0 | 14925.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 74435800000 | 62983.043 | 17-OCT-12:00 | 9001.312 | 39217.651 | 5148.588 | 0 | 9615.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66069000000 | 55391.087 | 29-NOV-09:50 | 9001.312 | 39217.651 | 2829.414 | 0 | 4342.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 64950600000 | 55708.823 | 01-DEC-11:30 | 9001.312 | 39217.651 | 2913.413 | 0 | 4576.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 892940000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61148100000 | 54850.809 |  | 9001.312 | 39217.651 | 2606.11 | 0 | 4025.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 91063900000 | 70520.569 |  | 9001.312 | 39217.651 | 6875.044 | 0 | 15426.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18704.2 | 260.11 | 0 | 18964.31
Cost per Total Building Area ($/m2) | 20.12 | 0.28 | 0 | 20.4
Cost per Net Conditioned Building Area ($/m2) | 20.12 | 0.28 | 0 | 20.4

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 990.25 | 1065.35 | 1065.35
Net Site Energy | 990.25 | 1065.35 | 1065.35
Total Source Energy | 3396.79 | 3654.42 | 3654.42
Net Source Energy | 3396.79 | 3654.42 | 3654.42
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 23.9 | 0 | 0 | 0 | 0
Cooling | 90.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.95 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.81 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 943.54 | 46.71 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 64438.32 | 51464 | 12974.32 | 0.8 | 4.37
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35791.07 | 27043.13 | 8747.93 | 0.76 | 3.62
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21508.65 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31247.34 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.89 | 7425.09 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.91 | 2087.55 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23817.5322 | 42.8102 | 127.1331 | 0 | 0.0004 | 29266.7507 | 10269.3678
February | 21511.539 | 38.8645 | 116.0178 | 0 | 0.0004 | 26708.2193 | 9294.134
March | 24675.2933 | 44.7715 | 134.2263 | 0 | 0.0004 | 30900.2004 | 10679.3135
April | 24550.6129 | 44.6028 | 133.893 | 0 | 0.0004 | 30823.5597 | 10630.8547
May | 29405.0332 | 53.4499 | 160.5339 | 0 | 0.0005 | 36956.6108 | 12735.5547
June | 31896.6177 | 57.9943 | 174.2294 | 0 | 0.0005 | 40109.4598 | 13816.1607
July | 32379.3987 | 58.8803 | 176.9156 | 0 | 0.0005 | 40727.8701 | 14026.063
August | 33725.1206 | 61.3268 | 184.2642 | 0 | 0.0006 | 42419.6083 | 14608.9349
September | 29701.956 | 54.0056 | 162.2507 | 0 | 0.0005 | 37351.8503 | 12865.6814
October | 26871.1758 | 48.8436 | 146.698 | 0 | 0.0004 | 33771.422 | 11638.0789
November | 22979.1145 | 41.7039 | 125.0596 | 0 | 0.0004 | 28789.9644 | 9946.1759
December | 23327.4311 | 42.026 | 125.0968 | 0 | 0.0004 | 28798.1252 | 10067.2992
Annual Sum or Average | 324840.825 | 589.2795 | 1766.3185 | 0 | 0.0053 | 406623.6411 | 140577.6188
Minimum of Months | 21511.539 | 38.8645 | 116.0178 | 0 | 0.0004 | 26708.2193 | 9294.134
Maximum of Months | 33725.1206 | 61.3268 | 184.2642 | 0 | 0.0006 | 42419.6083 | 14608.9349
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67911300000 | 56794.606 | 19-JAN-15:00 | 9001.312 | 39217.651 | 3319.539 | 0 | 5256.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61974400000 | 57868.467 | 22-FEB-15:00 | 9001.312 | 39217.651 | 3616.819 | 0 | 6032.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 71701600000 | 63751.716 | 31-MAR-14:00 | 9001.312 | 39217.651 | 5237.483 | 0 | 10295.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 71523700000 | 64271.091 | 07-APR-14:00 | 9001.312 | 39217.651 | 5334.789 | 0 | 10717.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 85755000000 | 70619.094 | 30-MAY-09:00 | 9001.312 | 39217.651 | 7436.803 | 0 | 14963.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 93071000000 | 74715.903 | 08-JUN-12:00 | 9001.312 | 39217.651 | 7626.8 | 0 | 18870.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 94506000000 | 75840.72 | 13-JUL-14:00 | 9001.312 | 39217.651 | 7872.159 | 0 | 19749.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 98431500000 | 74931.01 | 04-AUG-14:00 | 9001.312 | 39217.651 | 7832.691 | 0 | 18879.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 86672200000 | 73807.74 | 07-SEP-12:00 | 9001.312 | 39217.651 | 8394.383 | 0 | 17194.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 78364000000 | 68878.336 | 31-OCT-11:00 | 9001.312 | 39217.651 | 6754.999 | 0 | 13904.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66804900000 | 69696.634 | 02-NOV-14:39 | 9001.312 | 39217.651 | 7010.559 | 0 | 14467.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 66823900000 | 56996.475 | 05-DEC-15:09 | 9001.312 | 39217.651 | 3392.672 | 0 | 5384.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 943540000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61974400000 | 56794.606 |  | 9001.312 | 39217.651 | 3319.539 | 0 | 5256.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 98431500000 | 75840.72 |  | 9001.312 | 39217.651 | 8394.383 | 0 | 19749.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13857.06 | 400.32 | 0 | 14257.38
Cost per Total Building Area ($/m2) | 14.91 | 0.43 | 0 | 15.34
Cost per Net Conditioned Building Area ($/m2) | 14.91 | 0.43 | 0 | 15.34

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 988.88 | 1063.88 | 1063.88
Net Site Energy | 988.88 | 1063.88 | 1063.88
Total Source Energy | 3199.65 | 3442.32 | 3442.32
Net Source Energy | 3199.65 | 3442.32 | 3442.32
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13.85 | 0 | 0 | 0 | 0
Cooling | 69.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 141.09 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.75 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 952.29 | 36.6 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 74147.23 | 59218.08 | 14929.16 | 0.8 | 4.18
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35579.82 | 28416.01 | 7163.81 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17531.2 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26910.51 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.48 | 8403 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.15 | 2350.62 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18759.6747 | 32.5972 | 84.3469 | 0 | 0.0003 | 87705.783 | 8019.8975
February | 16820.8123 | 29.3366 | 76.216 | 0 | 0.0003 | 79251.7539 | 7201.6494
March | 20030.083 | 35.0144 | 91.194 | 0 | 0.0004 | 94826.9018 | 8583.5776
April | 19704.502 | 34.4854 | 89.9289 | 0 | 0.0004 | 93511.6774 | 8447.992
May | 22495.4384 | 39.3828 | 102.736 | 0 | 0.0004 | 106829.0225 | 9645.8219
June | 24050.7989 | 42.1178 | 109.9045 | 0 | 0.0004 | 114283.2075 | 10313.9273
July | 25139.4294 | 44.0338 | 114.9309 | 0 | 0.0004 | 119509.9865 | 10781.7129
August | 26217.4387 | 45.921 | 119.8541 | 0 | 0.0005 | 124629.2758 | 11243.951
September | 22797.3544 | 39.9255 | 104.1915 | 0 | 0.0004 | 108342.6293 | 9776.6703
October | 21125.7207 | 36.9799 | 96.4539 | 0 | 0.0004 | 100296.6825 | 9058.0189
November | 18371.7265 | 32.1037 | 83.5803 | 0 | 0.0003 | 86909.7605 | 7871.7641
December | 18177.9777 | 31.5981 | 81.7946 | 0 | 0.0003 | 85051.9036 | 7772.3613
Annual Sum or Average | 253690.9569 | 443.4962 | 1155.1316 | 0 | 0.0045 | 1201150 | 108717.3442
Minimum of Months | 16820.8123 | 29.3366 | 76.216 | 0 | 0.0003 | 79251.7539 | 7201.6494
Maximum of Months | 26217.4387 | 45.921 | 119.8541 | 0 | 0.0005 | 124629.2758 | 11243.951
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 69534200000 | 59340.527 | 24-JAN-13:00 | 9001.312 | 39217.651 | 3970.647 | 0 | 7150.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62831700000 | 57842.072 | 16-FEB-15:09 | 9001.312 | 39217.651 | 3659.488 | 0 | 5963.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 75179900000 | 65351.937 | 30-MAR-14:00 | 9001.312 | 39217.651 | 5867.084 | 0 | 11265.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 74137200000 | 67334.109 | 25-APR-14:00 | 9001.312 | 39217.651 | 6209.059 | 0 | 12906.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 84695300000 | 69077.27 | 23-MAY-14:00 | 9001.312 | 39217.651 | 6549.896 | 0 | 14308.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 90605100000 | 72660.994 | 28-JUN-13:39 | 9001.312 | 39217.651 | 7247.895 | 0 | 17194.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 94749000000 | 74915.011 | 26-JUL-12:39 | 9001.312 | 39217.651 | 8497.619 | 0 | 18198.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 98807600000 | 75382.416 | 30-AUG-13:00 | 9001.312 | 39217.651 | 7827.077 | 0 | 19336.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 85895300000 | 71393.562 | 06-SEP-14:50 | 9001.312 | 39217.651 | 7109.001 | 0 | 16065.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 79516400000 | 69661.234 | 05-OCT-14:00 | 9001.312 | 39217.651 | 6794.122 | 0 | 14648.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 68903100000 | 62950.158 | 10-NOV-13:00 | 9001.312 | 39217.651 | 5147.959 | 0 | 9583.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67430200000 | 59100.344 | 27-DEC-15:39 | 9001.312 | 39217.651 | 4037.237 | 0 | 6844.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 952285000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62831700000 | 57842.072 |  | 9001.312 | 39217.651 | 3659.488 | 0 | 5963.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 98807600000 | 75382.416 |  | 9001.312 | 39217.651 | 8497.619 | 0 | 19336.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9960.86 | 258.68 | 0 | 10219.54
Cost per Total Building Area ($/m2) | 10.72 | 0.28 | 0 | 10.99
Cost per Net Conditioned Building Area ($/m2) | 10.72 | 0.28 | 0 | 10.99

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1009.1 | 1085.63 | 1085.63
Net Site Energy | 1009.1 | 1085.63 | 1085.63
Total Source Energy | 3299.93 | 3550.21 | 3550.21
Net Source Energy | 3299.93 | 3550.21 | 3550.21
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 47.83 | 0 | 0 | 0 | 0
Cooling | 85.94 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 109.25 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.96 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 937.31 | 71.79 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 64853.34 | 51795.46 | 13057.88 | 0.8 | 4.37
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34691.92 | 26669.48 | 8022.44 | 0.77 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25159.66 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35316.79 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.92 | 7472.91 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.93 | 2105.54 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16079.5311 | 28.3334 | 44.8071 | 0 | 0.0003 | 29450.0207 | 6878.3178
February | 14172.0726 | 25.3234 | 40.6348 | 0 | 0.0003 | 26709.1182 | 6095.921
March | 16182.8601 | 29.2902 | 47.6177 | 0 | 0.0003 | 31300.3954 | 6996.5734
April | 15840.8269 | 28.8028 | 47.04 | 0 | 0.0003 | 30921.1138 | 6861.281
May | 18951.7116 | 34.4839 | 56.3581 | 0 | 0.0004 | 37046.3866 | 8211.0833
June | 20339.6271 | 37.0242 | 60.5339 | 0 | 0.0004 | 39791.3582 | 8813.8387
July | 20694.8917 | 37.6804 | 61.6223 | 0 | 0.0004 | 40506.8122 | 8968.6976
August | 21670.1421 | 39.4565 | 64.5277 | 0 | 0.0005 | 42416.6915 | 9391.3931
September | 18382.9221 | 33.4635 | 54.7142 | 0 | 0.0004 | 35965.8544 | 7966.0441
October | 16343.2963 | 29.723 | 48.5535 | 0 | 0.0004 | 31916.051 | 7079.5497
November | 14953.8502 | 27.0347 | 43.9003 | 0 | 0.0003 | 28856.7045 | 6462.2494
December | 15586.9653 | 27.7038 | 44.2105 | 0 | 0.0003 | 29058.8117 | 6690.3917
Annual Sum or Average | 209198.6972 | 378.3199 | 614.5202 | 0 | 0.0045 | 403939.3182 | 90415.3409
Minimum of Months | 14172.0726 | 25.3234 | 40.6348 | 0 | 0.0003 | 26709.1182 | 6095.921
Maximum of Months | 21670.1421 | 39.4565 | 64.5277 | 0 | 0.0005 | 42416.6915 | 9391.3931
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68336600000 | 56033.818 | 19-JAN-14:50 | 9001.312 | 39217.651 | 3069.48 | 0 | 4745.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61976500000 | 57573.815 | 16-FEB-15:00 | 9001.312 | 39217.651 | 3575.861 | 0 | 5778.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 72630200000 | 59289.832 | 23-MAR-14:00 | 9001.312 | 39217.651 | 3851.064 | 0 | 7219.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 71750100000 | 63123.183 | 14-APR-14:00 | 9001.312 | 39217.651 | 5115.393 | 0 | 9788.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 85963300000 | 70377.823 | 31-MAY-14:00 | 9001.312 | 39217.651 | 7216.09 | 0 | 14942.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 92332800000 | 74566.295 | 29-JUN-14:00 | 9001.312 | 39217.651 | 7699.325 | 0 | 18648.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 93993000000 | 74248.368 | 14-JUL-12:00 | 9001.312 | 39217.651 | 8593.814 | 0 | 17435.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 98424700000 | 74396.126 | 23-AUG-13:00 | 9001.312 | 39217.651 | 8611.666 | 0 | 17565.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 83456100000 | 71134.719 | 22-SEP-14:00 | 9001.312 | 39217.651 | 7622.733 | 0 | 15293.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 74058800000 | 65094.583 | 06-OCT-14:00 | 9001.312 | 39217.651 | 5640.968 | 0 | 11234.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66959800000 | 60941.163 | 02-NOV-14:00 | 9001.312 | 39217.651 | 4409.878 | 0 | 8312.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67428800000 | 56038.921 | 06-DEC-15:09 | 9001.312 | 39217.651 | 3078.287 | 0 | 4741.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 937311000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61976500000 | 56033.818 |  | 9001.312 | 39217.651 | 3069.48 | 0 | 4741.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 98424700000 | 74566.295 |  | 9001.312 | 39217.651 | 8611.666 | 0 | 18648.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15707.4 | 573.5 | 0 | 16280.9
Cost per Total Building Area ($/m2) | 16.9 | 0.62 | 0 | 17.52
Cost per Net Conditioned Building Area ($/m2) | 16.9 | 0.62 | 0 | 17.52

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 969.51 | 1043.05 | 1043.05
Net Site Energy | 969.51 | 1043.05 | 1043.05
Total Source Energy | 3230.16 | 3475.15 | 3475.15
Net Source Energy | 3230.16 | 3475.15 | 3475.15
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 34.49 | 0 | 0 | 0 | 0
Cooling | 50.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 118.32 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 24.18 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 910.85 | 58.67 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.477 | 0.51 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.477 | 0.51 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.622 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.402 | 0.495 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.432 | 0.533
North Total or Average |  |  | 24.14 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70595.74 | 56381.66 | 14214.08 | 0.8 | 4.18
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34473.42 | 27532.38 | 6941.04 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23850.14 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34065.66 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.26 | 8000.51 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.08 | 2277.52 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16864.3922 | 29.2526 | 50.5079 | 0 | 0.0004 | 1198120 | 7184.743
February | 15164.0985 | 26.4896 | 46.0892 | 0 | 0.0003 | 1093330 | 6478.3699
March | 17668.0231 | 31.1673 | 54.7978 | 0 | 0.0004 | 1299960 | 7577.4464
April | 16218.9972 | 28.6953 | 50.6081 | 0 | 0.0004 | 1200580 | 6964.1266
May | 18791.7229 | 33.262 | 58.6897 | 0 | 0.0004 | 1392300 | 8070.2477
June | 20472.8261 | 36.2528 | 63.9951 | 0 | 0.0004 | 1518160 | 8793.6805
July | 21719.4936 | 38.4719 | 67.9334 | 0 | 0.0005 | 1611600 | 9330.2685
August | 22245.9061 | 39.4025 | 69.5734 | 0 | 0.0005 | 1650500 | 9556.2321
September | 19151.8682 | 33.9161 | 59.8744 | 0 | 0.0004 | 1420410 | 8226.5168
October | 17399.174 | 30.7895 | 54.313 | 0 | 0.0004 | 1288470 | 7471.47
November | 15878.1748 | 28.0111 | 49.2508 | 0 | 0.0003 | 1168370 | 6809.9303
December | 16532.5056 | 28.7994 | 49.9568 | 0 | 0.0003 | 1185060 | 7055.1859
Annual Sum or Average | 218107.1824 | 384.5102 | 675.5895 | 0 | 0.0047 | 16026900 | 93518.2176
Minimum of Months | 15164.0985 | 26.4896 | 46.0892 | 0 | 0.0003 | 1093330 | 6478.3699
Maximum of Months | 22245.9061 | 39.4025 | 69.5734 | 0 | 0.0005 | 1650500 | 9556.2321
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68092000000 | 58290.943 | 10-JAN-15:00 | 9001.312 | 39217.651 | 3776.496 | 0 | 6295.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 62136500000 | 58203.569 | 02-FEB-14:00 | 9001.312 | 39217.651 | 4816.972 | 0 | 5167.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 73879800000 | 62714.884 | 30-MAR-14:00 | 9001.312 | 39217.651 | 5060.767 | 0 | 9435.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 68231800000 | 61023.883 | 06-APR-14:00 | 9001.312 | 39217.651 | 4530.44 | 0 | 8274.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 79127900000 | 66901.503 | 16-MAY-14:00 | 9001.312 | 39217.651 | 6126.963 | 0 | 12555.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 86280900000 | 73775.056 | 30-JUN-14:00 | 9001.312 | 39217.651 | 7370.573 | 0 | 18185.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 91590800000 | 73251.872 | 21-JUL-14:00 | 9001.312 | 39217.651 | 7351.066 | 0 | 17681.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 93802000000 | 71541.724 | 09-AUG-14:00 | 9001.312 | 39217.651 | 6976.137 | 0 | 16346.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 80725300000 | 68983.028 | 01-SEP-14:00 | 9001.312 | 39217.651 | 6500.705 | 0 | 14263.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 73226900000 | 65692.692 | 06-OCT-14:00 | 9001.312 | 39217.651 | 5894.348 | 0 | 11579.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66401200000 | 57935.951 | 28-NOV-15:30 | 9001.312 | 39217.651 | 3635.197 | 0 | 6081.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67350000000 | 57159.731 | 06-DEC-15:39 | 9001.312 | 39217.651 | 3387.444 | 0 | 5553.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 910845000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62136500000 | 57159.731 |  | 9001.312 | 39217.651 | 3387.444 | 0 | 5167.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 93802000000 | 73775.056 |  | 9001.312 | 39217.651 | 7370.573 | 0 | 18185.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 19379.34 | 484.84 | 0 | 19864.18
Cost per Total Building Area ($/m2) | 20.85 | 0.52 | 0 | 21.37
Cost per Net Conditioned Building Area ($/m2) | 20.85 | 0.52 | 0 | 21.37

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 976.77 | 1050.86 | 1050.86
Net Site Energy | 976.77 | 1050.86 | 1050.86
Total Source Energy | 3169.82 | 3410.22 | 3410.22
Net Source Energy | 3169.82 | 3410.22 | 3410.22
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 54.03 | 0 | 0 | 0 | 0
Cooling | 56.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 98 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 25.87 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 896.88 | 79.9 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.651 | 0.64 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.501 | 0.49 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.49 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.501 | 0.49 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 3.18 | 0.651 | 0.64 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 3.18 | 0.501 | 0.49 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 3.18 | 0.501 | 0.49 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 3.18 | 0.501 | 0.49 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 3.18 | 0.546 | 0.535
North Total or Average |  |  | 24.14 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 56.3 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 62755.07 | 50119.67 | 12635.4 | 0.8 | 4.37
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30392.48 | 24273.12 | 6119.37 | 0.8 | 3.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25671.84 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35874.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.79 | 7231.14 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.84 | 2007.91 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16005.7262 | 28.2866 | 44.8724 | 0 | 0.0003 | 29493.2575 | 6854.7002
February | 14309.6272 | 25.4341 | 40.5894 | 0 | 0.0003 | 26678.7195 | 6142.1758
March | 16106.6609 | 29.0656 | 47.1111 | 0 | 0.0003 | 30967.0728 | 6955.3396
April | 14966.7965 | 27.1827 | 44.3438 | 0 | 0.0003 | 29148.7099 | 6479.7483
May | 17139.5681 | 31.1643 | 50.8966 | 0 | 0.0004 | 33456.2455 | 7423.8167
June | 18977.9939 | 34.5294 | 56.4288 | 0 | 0.0004 | 37092.8637 | 8222.252
July | 19919.5682 | 36.2551 | 59.2692 | 0 | 0.0004 | 38959.9612 | 8631.3845
August | 19929.8089 | 36.2692 | 59.2851 | 0 | 0.0004 | 38970.4464 | 8635.3964
September | 16935.9353 | 30.8135 | 50.3555 | 0 | 0.0004 | 33100.6316 | 7337.4822
October | 15800.1919 | 28.7176 | 46.8823 | 0 | 0.0003 | 30817.4207 | 6842.5938
November | 15012.5698 | 27.0246 | 43.6939 | 0 | 0.0003 | 28720.605 | 6476.5058
December | 15653.7539 | 27.7876 | 44.2863 | 0 | 0.0003 | 29108.5004 | 6715.7236
Annual Sum or Average | 200758.2007 | 362.5302 | 588.0144 | 0 | 0.0043 | 386514.4342 | 86717.1189
Minimum of Months | 14309.6272 | 25.4341 | 40.5894 | 0 | 0.0003 | 26678.7195 | 6142.1758
Maximum of Months | 19929.8089 | 36.2692 | 59.2851 | 0 | 0.0004 | 38970.4464 | 8635.3964
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 68436900000 | 56515.126 | 20-JAN-15:30 | 9001.312 | 39217.651 | 3275.043 | 0 | 5021.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61906000000 | 57228.76 | 17-FEB-15:00 | 9001.312 | 39217.651 | 3497.155 | 0 | 5512.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 71856800000 | 58287.47 | 24-MAR-10:00 | 9001.312 | 39217.651 | 3808.75 | 0 | 6259.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 67637400000 | 59907.262 | 04-APR-14:00 | 9001.312 | 39217.651 | 4121.907 | 0 | 7566.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 77632700000 | 65173.447 | 31-MAY-14:00 | 9001.312 | 39217.651 | 5789.255 | 0 | 11165.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 86071200000 | 70864.641 | 14-JUN-10:00 | 9001.312 | 39217.651 | 7502.07 | 0 | 15143.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 90403700000 | 73693.785 | 12-JUL-12:00 | 9001.312 | 39217.651 | 8479.182 | 0 | 16995.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 90428000000 | 71198.67 | 11-AUG-14:00 | 9001.312 | 39217.651 | 7128.944 | 0 | 15850.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 76807500000 | 71431.635 | 07-SEP-13:50 | 9001.312 | 39217.651 | 7670.79 | 0 | 15541.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 71509500000 | 60850.047 | 06-OCT-14:00 | 9001.312 | 39217.651 | 4420.609 | 0 | 8210.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66644000000 | 56740.575 | 10-NOV-15:00 | 9001.312 | 39217.651 | 3293.156 | 0 | 5228.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 67544100000 | 56638.113 | 01-DEC-14:50 | 9001.312 | 39217.651 | 3283.529 | 0 | 5135.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 896878000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61906000000 | 56515.126 |  | 9001.312 | 39217.651 | 3275.043 | 0 | 5021.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 90428000000 | 73693.785 |  | 9001.312 | 39217.651 | 8479.182 | 0 | 16995.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15126.84 | 636.14 | 0 | 15762.98
Cost per Total Building Area ($/m2) | 16.27 | 0.68 | 0 | 16.96
Cost per Net Conditioned Building Area ($/m2) | 16.27 | 0.68 | 0 | 16.96

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1042.68 | 1121.76 | 1121.76
Net Site Energy | 1042.68 | 1121.76 | 1121.76
Total Source Energy | 3289.84 | 3539.36 | 3539.36
Net Source Energy | 3289.84 | 3539.36 | 3539.36
Area [m2]
Total Building Area | 929.5
Net Conditioned Building Area | 929.5
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 147.06 | 0 | 0 | 0 | 0
Cooling | 44.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 109.85 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 632.27 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 81.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 28.18 | 0 | 0 | 0 | 89
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 867.44 | 175.24 | 0 | 0 | 0 | 89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FIRST_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 77.9281
SECOND_FLOOR | 464.75 | Yes | 1416.94 | 1 | 268.33 | 40.22 | 10.76 | 18.59 | 8.07
ATTIC | 464.75 | No | 631.22 | 1 | 0 | 0 | 0 |  | 0
Total | 1394.26 |  | 3465.09 |  | 536.65 | 80.44 | 7.1733 | 27.88 | 28.666
Conditioned Total | 929.5 |  | 2833.87 |  | 536.65 | 80.44 | 10.76 | 18.59 | 42.999
Unconditioned Total | 464.75 |  | 631.22 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
FIRST_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
FIRST_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
FIRST_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
FIRST_FLOOR_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 464.75 | 0 | 180
SECOND_FLOOR_WALL_NORTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 0 | 90 | N
SECOND_FLOOR_WALL_EAST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 90 | 90 | E
SECOND_FLOOR_WALL_SOUTH | EXT-WALLS | 0.3 | 0.364 | 0.38 | 80.5 | 180 | 90 | S
SECOND_FLOOR_WALL_WEST | EXT-WALLS | 0.3 | 0.364 | 0.38 | 53.67 | 270 | 90 | W
WEST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 270 | 45
EAST-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 36.51 | 90 | 45
SOUTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 180 | 18.43
NORTH-ROOF | ATTIC-ROOF | 0.3 | 4.035 | 16.83 | 217.73 | 0 | 18.44
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FIRST_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 2.58 | 0.654 | 0.64 | No | FIRST_FLOOR_WALL_NORTH | 0 | N
FIRST_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 2.58 | 0.504 | 0.49 | No | FIRST_FLOOR_WALL_EAST | 90 | E
FIRST_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 2.58 | 0.504 | 0.49 | No | FIRST_FLOOR_WALL_SOUTH | 180 | S
FIRST_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 2.58 | 0.504 | 0.49 | No | FIRST_FLOOR_WALL_WEST | 270 | W
SECOND_FLOOR_WALL_NORTH_WINDOW | WINDOW_NORTH | 12.07 | 12.07 | 2.58 | 0.654 | 0.64 | No | SECOND_FLOOR_WALL_NORTH | 0 | N
SECOND_FLOOR_WALL_EAST_WINDOW | WINDOW_EAST | 8.04 | 8.04 | 2.58 | 0.504 | 0.49 | No | SECOND_FLOOR_WALL_EAST | 90 | E
SECOND_FLOOR_WALL_SOUTH_WINDOW | WINDOW_SOUTH | 12.07 | 12.07 | 2.58 | 0.504 | 0.49 | No | SECOND_FLOOR_WALL_SOUTH | 180 | S
SECOND_FLOOR_WALL_WEST_WINDOW | WINDOW_WEST | 8.04 | 8.04 | 2.58 | 0.504 | 0.49 | No | SECOND_FLOOR_WALL_WEST | 270 | W
Total or Average |  |  | 80.44 | 2.58 | 0.549 | 0.535
North Total or Average |  |  | 24.14 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 56.3 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 59463.89 | 47491.15 | 11972.74 | 0.8 | 4.37
PSZ-AC_1:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29889.36 | 23871.29 | 6018.07 | 0.8 | 3.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_2:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35113.55 | 0.8
PSZ-AC_1:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46134.12 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_2:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.59 | 6851.9 | 1 | Unitary Fans
PSZ-AC_1:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.81 | 1974.67 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15513.0355 | 18.6425 | 95.4529 | 0 | 0.0003 | 19155.7057 | 6070.8536
February | 13686.0617 | 16.5632 | 86.6431 | 0 | 0.0003 | 17388.1587 | 5373.7749
March | 14707.49 | 18.158 | 100.6118 | 0 | 0.0003 | 20192.7186 | 5830.0179
April | 13401.421 | 16.7097 | 95.1131 | 0 | 0.0003 | 19089.6427 | 5337.5678
May | 15149.2822 | 18.9344 | 108.4659 | 0 | 0.0004 | 21769.7459 | 6040.684
June | 16616.4172 | 20.7736 | 119.0853 | 0 | 0.0004 | 23901.1402 | 6626.5411
July | 16799.7063 | 21.0062 | 120.4713 | 0 | 0.0004 | 24179.3422 | 6700.169
August | 16587.8549 | 20.7385 | 118.8942 | 0 | 0.0004 | 23862.7919 | 6615.2507
September | 13659.4464 | 17.0732 | 97.8179 | 0 | 0.0003 | 19632.6425 | 5446.7606
October | 13792.4824 | 17.1424 | 96.7398 | 0 | 0.0003 | 19415.9606 | 5484.8714
November | 14238.7869 | 17.3959 | 93.5679 | 0 | 0.0003 | 18778.4219 | 5615.9971
December | 14822.0721 | 17.9335 | 93.7395 | 0 | 0.0003 | 18812.2821 | 5819.1223
Annual Sum or Average | 178974.0566 | 221.071 | 1226.6025 | 0 | 0.0042 | 246178.5529 | 70961.6104
Minimum of Months | 13401.421 | 16.5632 | 86.6431 | 0 | 0.0003 | 17388.1587 | 5337.5678
Maximum of Months | 16799.7063 | 21.0062 | 120.4713 | 0 | 0.0004 | 24179.3422 | 6700.169
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY [Invalid/Undefined] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67497200000 | 55141.914 | 18-JAN-15:20 | 9001.312 | 39217.651 | 2701.773 | 0 | 4221.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 61269100000 | 55563.566 | 28-FEB-11:00 | 9001.312 | 39217.651 | 2903.912 | 0 | 4440.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 71151200000 | 56700.548 | 10-MAR-15:00 | 9001.312 | 39217.651 | 3275.172 | 0 | 5206.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 67264400000 | 58281.05 | 27-APR-09:39 | 9001.312 | 39217.651 | 3766.837 | 0 | 6295.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 76708100000 | 62831.737 | 24-MAY-14:00 | 9001.312 | 39217.651 | 5083.957 | 0 | 9528.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 84218300000 | 67332.293 | 21-JUN-14:00 | 9001.312 | 39217.651 | 6215.858 | 0 | 12897.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 85198500000 | 67277.462 | 11-JUL-14:00 | 9001.312 | 39217.651 | 6220.077 | 0 | 12838.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 84083100000 | 67212.438 | 15-AUG-14:39 | 9001.312 | 39217.651 | 6121.539 | 0 | 12871.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 69177700000 | 58768.846 | 07-SEP-14:00 | 9001.312 | 39217.651 | 3674.103 | 0 | 6875.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 68414200000 | 58062.725 | 12-OCT-14:00 | 9001.312 | 39217.651 | 3708.131 | 0 | 6135.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 66167800000 | 55683.091 | 14-NOV-15:00 | 9001.312 | 39217.651 | 2902.919 | 0 | 4561.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 66287100000 | 54876.57 | 18-DEC-15:00 | 9001.312 | 39217.651 | 2605.981 | 0 | 4051.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 867437000000 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61269100000 | 54876.57 |  | 9001.312 | 39217.651 | 2605.981 | 0 | 4051.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 85198500000 | 67332.293 |  | 9001.312 | 39217.651 | 6220.077 | 0 | 12897.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24181.11 | 718.39 | 0 | 24899.5
Cost per Total Building Area ($/m2) | 26.02 | 0.77 | 0 | 26.79
Cost per Net Conditioned Building Area ($/m2) | 26.02 | 0.77 | 0 | 26.79

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 60.1 | 3133.79
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
BLDG_LIGHT_EXTD_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.2 | 104.6 | 5454.14
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 13.6
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 | 8.5 | 46.7 | 2435.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 3.8
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4
BLDG_OCC_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 13.5 | 90.4 | 4713.71
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.7
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 96.7 | 5042.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8
BLDG_EQUIP_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 15.3 | 99.9 | 5209.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12.2
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 11.2
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
INFIL_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 77 | 4015
|  |  | Sat, WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
First_floor Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
First_floor Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
First_floor Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
First_floor Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Second_floor Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Second_floor Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Second_floor Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Second_floor Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720