## BuildingSummary
Building Summary Outpatient Health Care new construction
|  | Value | Data Source
Program
| Building Name | Outpatient Health Care
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, outpatient
Form
| Total Floor Area (m2) | 3804.01 | Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health Care Facilities – 30% Energy Savings. Golden, CO: National Renewable Energy Laboratory, NREL/TP-550-46314. Available at www.nrel.gov/docs/fy10osti/46314.pdf
| Building Shape | Irregular
| Aspect Ratio | 1.43
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.2408
| East | 0.1914
| North | 0.2052
| West | 0.1288
| Total | 0.1985
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Zoned By Use
| Floor to Ceiling Height (m) | 3.05
| Floor to Floor Height (m) | 3.05
| Roof type | Flat
Fabric
Exterior walls
| Construction Type | Steel frame
| Gross Dimensions - Total Area (m2) | 1553.34
| Net Dimensions - Total Area (m2) | 1245.05
| Wall to Skin Ratio | 0.53076
Roof
| Construction Type | Flat, IEAD
| Gross Dimensions - Total Area (m2) | 1373.29
| Net Dimensions - Total Area (m2) | 1373.29
| Roof to Skin Ratio | 0.46924
Window Dimensions (m2)
| South | 114.08
| East | 57.97
| North | 97.22
| West | 39.02
| Total Area (m2) | 308.29
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 8in slab w/carpet
| Dimensions - Total Area (m2) | 1373.29
Interior Partitions
| Construction | Gypsum Board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 2746.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ft3/min per ft2 of exterior wall) | 0.2
HVAC
| System Type | Packaged VAV With Reheat
| Heating Type | Hot Water Boiler
| Cooling Type | DX Cooling Coil
| Fan Control | VAV
Service Water Heating
| SWH Type | Gas Water Heater
| Fuel | Gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 10.03

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
FLOOR 1 ANESTHESIA | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 | 0 | 0 | 32.29 | 21.53 | 0 | 3.8 | 0 | 6.3513 | 61.1582 | 67.9604 | 0.29752
FLOOR 1 BIO HAZ | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 3.964 | 0 | 0
FLOOR 1 CAFE | Yes | 1 | 39.0193 | 118.9308 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 9.69 | 10.76 | 0 | 0 | 9.438 | 0 | 368.2639 | 0 | 0.17003
FLOOR 1 CLEAN | Yes | 1 | 11.7058 | 35.6792 | 3.048 | 0 | 0 | 5 | 2.3412 | 12.92 | 21.53 | 0 | 0 | 0 | 1.5878 | 17.8378 | 0 | 0
FLOOR 1 CLEAN WORK | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 12.92 | 21.53 | 0 | 0 | 0 | 1.5878 | 23.359 | 0 | 0
FLOOR 1 DICTATION | Yes | 1 | 11.7058 | 35.6792 | 3.048 | 0 | 0 | 20 | 0.58529 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 5.524 | 0 | 0
FLOOR 1 DRESSING ROOM | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 1.9728 | 0 | 0.71404
FLOOR 1 ELECTRICAL ROOM | Yes | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 | 0 | 0 | 16.15 | 53.82 | 0 | 0 | 0 | 0.26464 | 2.3123 | 0 | 0.25493
FLOOR 1 ELEVATOR PUMP ROOM | Yes | 1 | 8.4542 | 25.7683 | 3.048 | 18.58 | 0 | 0 | 0 | 16.15 | 53.82 | 0 | 0 | 0 | 0.26464 | 2.1471 | 0 | 0.78475
FLOOR 1 HUMID | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 2.3674 | 0 | 0
FLOOR 1 IT HALL | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 3.3033 | 0 | 0
FLOOR 1 IT ROOM | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 4.9102 | 0 | 0
FLOOR 1 LOBBY | Yes | 1 | 57.7857 | 176.1308 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 13.99 | 11.84 | 0 | 0 | 7.0785 | 0 | 122.7108 | 0 | 0.1263
FLOOR 1 LOBBY HALL | Yes | 1 | 22.2967 | 67.9604 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 5.6628 | 0 | 0
FLOOR 1 LOBBY TOILET | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 50.9652 | 42.4753 | 0.39645
FLOOR 1 LOCKER ROOM | Yes | 1 | 61.316 | 186.8912 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 8.61 | 32.29 | 0 | 0 | 7.0785 | 0 | 65.1038 | 0 | 0.11903
FLOOR 1 LOCKER ROOM HALL | Yes | 1 | 46.0799 | 140.4516 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 11.7031 | 0 | 0
FLOOR 1 LOUNGE | Yes | 1 | 33.4451 | 101.9406 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 8.61 | 32.29 | 0 | 0 | 7.0785 | 0 | 35.5112 | 0 | 0
FLOOR 1 MRI CONTROL ROOM | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 3.964 | 0 | 1.3138
FLOOR 1 MRI HALL | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 4.31 | 11.84 | 0 | 3.8 | 0 | 1.5878 | 23.7837 | 79.2872 | 0.10638
FLOOR 1 MRI ROOM | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 3.4685 | 0 | 0
FLOOR 1 MRI TOILET | Yes | 1 | 40.8773 | 124.5941 | 3.048 | 0 | 0 | 5 | 8.1755 | 4.31 | 571.116 | 0 | 3.8 | 0 | 1.5878 | 62.2907 | 207.6569 | 0
FLOOR 1 MED GAS | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 50.9652 | 42.4753 | 0.39645
FLOOR 1 NOURISHMENT | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 10.76 | 21.53 | 0 | 0 | 9.438 | 0 | 31.9162 | 0 | 0
FLOOR 1 NURSE HALL | Yes | 1 | 46.0799 | 140.4516 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 11.7031 | 0 | 0
FLOOR 1 NURSE JANITOR | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 3.8224 | 0 | 0
FLOOR 1 NURSE STATION | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 10.76 | 21.53 | 0 | 0 | 9.438 | 0 | 45.7699 | 0 | 0
FLOOR 1 NURSE TOILET | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 50.9652 | 42.4753 | 0
FLOOR 1 OFFICE | Yes | 1 | 44.8722 | 136.7704 | 3.048 | 0 | 0 | 20 | 2.2436 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 21.1752 | 0 | 0
FLOOR 1 OPERATING ROOM 1 | Yes | 1 | 42.7354 | 130.2575 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 23.68 | 43.07 | 75.29 | 22.7 | 0 | 0 | 108.5371 | 0 | 0.3338
FLOOR 1 OPERATING ROOM 2 | Yes | 1 | 44.5935 | 135.9209 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 23.68 | 43.07 | 75.29 | 22.7 | 0 | 0 | 113.2561 | 0 | 0.17856
FLOOR 1 OPERATING ROOM 3 | Yes | 1 | 44.2218 | 134.7882 | 3.048 | 0 | 0 | 5 | 8.8444 | 23.68 | 43.07 | 75.29 | 22.7 | 0 | 0 | 112.3123 | 0 | 0
FLOOR 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 8.61 | 32.29 | 0 | 3.8 | 0 | 0 | 16.9884 | 0 | 0
FLOOR 1 PRE-OP HALL | Yes | 1 | 49.0528 | 149.513 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 12.4581 | 0 | 0
FLOOR 1 PRE-OP ROOM 1 | Yes | 1 | 17.5587 | 53.5188 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 7.53 | 21.53 | 0 | 3.8 | 0 | 0 | 29.7297 | 0 | 0.07565
FLOOR 1 PRE-OP ROOM 2 | Yes | 1 | 31.4012 | 95.7109 | 3.048 | 0 | 0 | 10 | 3.1401 | 7.53 | 21.53 | 0 | 3.8 | 0 | 0 | 53.1675 | 0 | 0
FLOOR 1 PRE-OP TOILET | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 50.9652 | 42.4753 | 0.39645
FLOOR 1 PROCEDURE ROOM | Yes | 1 | 26.4774 | 80.703 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 29.06 | 32.29 | 0 | 3.8 | 0 | 0 | 67.2458 | 0 | 0.23803
FLOOR 1 RECEPTION | Yes | 1 | 47.2876 | 144.1327 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 13.99 | 11.84 | 0 | 0 | 7.0785 | 0 | 100.4177 | 0 | 0.091218
FLOOR 1 RECEPTION HALL | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 3.0202 | 0 | 0
FLOOR 1 RECOVERY ROOM | Yes | 1 | 50.1676 | 152.911 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 8.61 | 32.29 | 0 | 3.8 | 0 | 0 | 84.9421 | 0 | 0.29759
FLOOR 1 SCHEDULING | Yes | 1 | 11.0555 | 33.697 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 5.2171 | 0 | 0.20994
FLOOR 1 SCRUB | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 1.982 | 0 | 0
FLOOR 1 SOIL | Yes | 1 | 11.7058 | 35.6792 | 3.048 | 0 | 0 | 5 | 2.3412 | 12.92 | 21.53 | 0 | 0 | 0 | 7.9392 | 89.189 | 99.109 | 0
FLOOR 1 SOIL HOLD | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 12.92 | 21.53 | 0 | 0 | 0 | 7.9392 | 39.6396 | 44.0484 | 0
FLOOR 1 SOIL WORK | Yes | 1 | 16.7225 | 50.9703 | 3.048 | 0 | 0 | 5 | 3.3445 | 12.92 | 21.53 | 0 | 0 | 0 | 7.9392 | 127.4129 | 141.5842 | 0
FLOOR 1 STEP DOWN | Yes | 1 | 27.8709 | 84.9505 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 8.61 | 32.29 | 0 | 3.8 | 0 | 0 | 47.19 | 0 | 0.44034
FLOOR 1 STERILE HALL | Yes | 1 | 57.2283 | 174.4318 | 3.048 | 7.43 | 2.23 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 14.5345 | 0 | 0.046359
FLOOR 1 STERILE STORAGE | Yes | 1 | 36.7896 | 112.1347 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 28.0308 | 0 | 0
FLOOR 1 STORAGE | Yes | 1 | 85.4708 | 260.515 | 3.048 | 58.53 | 8.36 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 65.1221 | 0 | 0.6016
FLOOR 1 SUB-STERILE | Yes | 1 | 18.209 | 55.501 | 3.048 | 13.01 | 2.97 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.6246 | 0 | 0.25512
FLOOR 1 UTILITY HALL | Yes | 1 | 23.7832 | 72.4911 | 3.048 | 14.86 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 6.0403 | 0 | 0.58018
FLOOR 1 UTILITY JANITOR | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 2.973 | 0 | 0
FLOOR 1 UTILITY ROOM | Yes | 1 | 33.4451 | 101.9406 | 3.048 | 16.72 | 2.23 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 25.4826 | 0 | 0.17851
FLOOR 1 VESTIBULE | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 1.6988 | 0 | 0.39663
FLOOR 2 CONFERENCE | Yes | 1 | 31.2154 | 95.1446 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 13.99 | 10.76 | 0 | 0 | 9.438 | 0 | 147.3056 | 0 | 0.42508
FLOOR 2 CONFERENCE TOILET | Yes | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 60.4031 | 50.3411 | 0
FLOOR 2 DICTATION | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 3.0689 | 0 | 0
FLOOR 2 EXAM 1 | Yes | 1 | 33.4451 | 101.9406 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 50.9652 | 0 | 0.4166
FLOOR 2 EXAM 2 | Yes | 1 | 50.1676 | 152.911 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 76.4477 | 0 | 0.11901
FLOOR 2 EXAM 3 | Yes | 1 | 66.8902 | 203.8813 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 101.9303 | 0 | 0.11904
FLOOR 2 EXAM 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 11.8919 | 0 | 0.29742
FLOOR 2 EXAM 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 49.5495 | 0 | 0.2551
FLOOR 2 EXAM 6 | Yes | 1 | 20.9032 | 63.7129 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 31.8532 | 0 | 0.23813
FLOOR 2 EXAM 7 | Yes | 1 | 73.5792 | 224.2694 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 112.1233 | 0 | 0.10822
FLOOR 2 EXAM 8 | Yes | 1 | 25.0838 | 76.4555 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 38.2239 | 0 | 0.23801
FLOOR 2 EXAM 9 | Yes | 1 | 36.7896 | 112.1347 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 56.0617 | 0 | 0.10822
FLOOR 2 EXAM HALL 1 | Yes | 1 | 16.7225 | 50.9703 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.2471 | 0 | 0.11894
FLOOR 2 EXAM HALL 2 | Yes | 1 | 16.7225 | 50.9703 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.2471 | 0 | 0.11894
FLOOR 2 EXAM HALL 3 | Yes | 1 | 16.7225 | 50.9703 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.2471 | 0 | 0.11894
FLOOR 2 EXAM HALL 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.6718 | 0 | 0.10812
FLOOR 2 EXAM HALL 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.6718 | 0 | 0.10812
FLOOR 2 EXAM HALL 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.6718 | 0 | 0.10812
FLOOR 2 JANITOR | Yes | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 4.4595 | 0 | 0.90658
FLOOR 2 LOUNGE | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 8.61 | 32.29 | 0 | 0 | 7.0785 | 0 | 7.8914 | 0 | 0
FLOOR 2 NURSE STATION 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 10.76 | 21.53 | 0 | 0 | 9.438 | 0 | 26.3046 | 0 | 0
FLOOR 2 NURSE STATION 2 | Yes | 1 | 16.7225 | 50.9703 | 3.048 | 0 | 0 | 5 | 3.3445 | 10.76 | 21.53 | 0 | 0 | 9.438 | 0 | 31.5655 | 0 | 0
FLOOR 2 OFFICE | Yes | 1 | 52.0257 | 158.5743 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 24.5509 | 0 | 0.25505
FLOOR 2 OFFICE HALL | Yes | 1 | 41.2489 | 125.7268 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 10.4762 | 0 | 0
FLOOR 2 RECEPTION | Yes | 1 | 91.4166 | 278.6378 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 13.99 | 11.84 | 0 | 0 | 7.0785 | 0 | 194.1277 | 0 | 0.1778
FLOOR 2 RECEPTION HALL | Yes | 1 | 52.3973 | 159.707 | 3.048 | 87.33 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 13.3076 | 0 | 0.59513
FLOOR 2 RECEPTION TOILET | Yes | 1 | 11.7058 | 35.6792 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 118.9187 | 99.109 | 0
FLOOR 2 SCHEDULING 1 | Yes | 1 | 30.1006 | 91.7466 | 3.048 | 0 | 0 | 20 | 1.505 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 14.2045 | 0 | 0
FLOOR 2 SCHEDULING 2 | Yes | 1 | 31.7728 | 96.8436 | 3.048 | 0 | 0 | 20 | 1.5886 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 14.9936 | 0 | 0
FLOOR 2 STORAGE 1 | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 3.964 | 0 | 0
FLOOR 2 STORAGE 2 | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 8.4942 | 0 | 0
FLOOR 2 STORAGE 3 | Yes | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 10.193 | 0 | 0
FLOOR 2 UTILITY | Yes | 1 | 11.7058 | 35.6792 | 3.048 | 8.36 | 2.23 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 8.9189 | 0 | 0.25501
FLOOR 2 WORK | Yes | 1 | 157.0061 | 478.5547 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 74.0912 | 0 | 0.054924
FLOOR 2 WORK HALL | Yes | 1 | 77.4811 | 236.1625 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 19.6782 | 0 | 0.02567
FLOOR 2 WORK TOILET | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 50.9652 | 42.4753 | 0.39645
FLOOR 2 X-RAY | Yes | 1 | 83.6127 | 254.8516 | 3.048 | 0 | 0 | 5 | 16.7225 | 4.31 | 14.0206 | 0 | 3.8 | 0 | 1.5878 | 127.4129 | 0 | 0
FLOOR 3 DRESSING ROOM | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 1.8413 | 0 | 0.35708
FLOOR 3 ELEVATOR HALL | Yes | 1 | 34.3741 | 104.7723 | 3.048 | 3.72 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 8.7301 | 0 | 0.39572
FLOOR 3 HUMID | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 4.7348 | 0 | 0.35708
FLOOR 3 JANITOR | Yes | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 4.4595 | 0 | 1.2637
FLOOR 3 LOCKER | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 8.61 | 32.29 | 0 | 0 | 7.0785 | 0 | 11.8371 | 0 | 0.35708
FLOOR 3 LOUNGE | Yes | 1 | 70.5134 | 214.9249 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 8.61 | 32.29 | 0 | 0 | 7.0785 | 0 | 74.8694 | 0 | 0.46529
FLOOR 3 LOUNGE TOILET | Yes | 1 | 17.8374 | 54.3683 | 3.048 | 11.15 | 4.18 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 181.2094 | 151.0232 | 0.58028
FLOOR 3 MECHANICAL | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 0 | 0 | 16.15 | 53.82 | 0 | 0 | 0 | 0.26464 | 8.2582 | 0 | 0.61218
FLOOR 3 MECHANICAL HALL | Yes | 1 | 27.8709 | 84.9505 | 3.048 | 0 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 7.0785 | 0 | 0.35708
FLOOR 3 OFFICE | Yes | 1 | 282.0536 | 859.6995 | 3.048 | 68.75 | 19.51 | 20 | 14.1027 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 133.1011 | 0 | 0.44411
FLOOR 3 OFFICE HALL | Yes | 1 | 77.4811 | 236.1625 | 3.048 | 5.57 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 19.6782 | 0 | 0.38274
FLOOR 3 OFFICE TOILET | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 50.9652 | 42.4753 | 0.75353
FLOOR 3 PHYSICAL THERAPY 1 | Yes | 1 | 120.774 | 368.119 | 3.048 | 78.97 | 28.99 | 5 | 24.1548 | 9.69 | 16.15 | 0 | 3.8 | 7.0785 | 0 | 170.9797 | 0 | 0.59055
FLOOR 3 PHYSICAL THERAPY 2 | Yes | 1 | 54.9986 | 167.6357 | 3.048 | 0 | 0 | 5 | 10.9997 | 9.69 | 16.15 | 0 | 3.8 | 7.0785 | 0 | 77.8615 | 0 | 0.35708
FLOOR 3 PHYSICAL THERAPY TOILET | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 4.31 | 0 | 0 | 0 | 10.5856 | 79.2791 | 66.0726 | 0.35708
FLOOR 3 STORAGE 1 | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 7.6448 | 0 | 0.35708
FLOOR 3 STORAGE 2 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 5.9459 | 0 | 0.35708
FLOOR 3 TREATMENT | Yes | 1 | 44.2218 | 134.7882 | 3.048 | 0 | 0 | 5 | 8.8444 | 16.15 | 11.84 | 0 | 0 | 0 | 1.5878 | 67.3873 | 0 | 0.35708
FLOOR 3 UNDEVELOPED 1 | Yes | 1 | 210.7041 | 642.2261 | 3.048 | 66.89 | 25.64 | 20 | 10.5352 | 11.84 | 11.84 | 0 | 0 | 0 | 0.79392 | 160.5402 | 0 | 0.47043
FLOOR 3 UNDEVELOPED 2 | Yes | 1 | 107.0243 | 326.2101 | 3.048 | 52.03 | 13.38 | 20 | 5.3512 | 11.84 | 11.84 | 0 | 0 | 0 | 0.79392 | 81.5442 | 0 | 0.53067
FLOOR 3 UTILITY | Yes | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 | 0 | 0 | 9.69 | 1.08 | 0 | 0 | 0 | 0.79392 | 15.2895 | 0 | 0.35708
FLOOR 3 WORK | Yes | 1 | 53.3263 | 162.5387 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 11.84 | 11.84 | 0 | 0 | 9.438 | 0 | 25.1647 | 0 | 0.61213
NE STAIR | Yes | 1 | 15.6077 | 142.7169 | 9.144 | 97.55 | 12.02 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 3.964 | 0 | 1
NW ELEVATOR | Yes | 1 | 13.0064 | 118.9308 | 9.144 | 75.25 | 0 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 3.3033 | 0 | 1
NW STAIR | Yes | 1 | 17.8374 | 163.105 | 9.144 | 111.48 | 11.15 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 4.5302 | 0 | 1
SW STAIR | Yes | 1 | 8.9187 | 81.5525 | 9.144 | 55.74 | 1.11 | 0 | 0 | 10.76 | 4.31 | 0 | 0 | 0 | 0.26464 | 2.2651 | 0 | 1
Total Conditioned Zones |  |  | 3804.0079 | 11932.1528 |  | 1634.12 | 308.28 |  | 414.8028
Data Source | [7 empty] | 1 |  | 2 | 5 | 5 | 5 | 3, 4 | 3, 4 | 3, 4 | 5 | 6
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health
[6] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 12.0363 | 183.3674 | 43.3615 | 187.8142 |  | 88.8067 | 19.7797 | 264.2744 | 7.5099 | 58.4502 | 342.01 | 70.3698 | 110.6579 | 10.7551 | 12.5902 | 0.66527
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD | Flat, IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| AHU-1_COOLC DXCOIL | 399.514 | 397.4793 | 376.9913 | 376.9085 | 329.3293 | 338.9755 | 304.7929 | 380.2478 | 309.2278 | 312.3925 | 373.5013 | 304.1087 | 366.4194 | 295.021 | 332.997 | 297.5159
| AHU-2_COOLC DXCOIL | 329.6487 | 337.0449 | 333.6741 | 312.4943 | 249.0609 | 288.7199 | 251.8557 | 322.8354 | 286.8199 | 250.554 | 314.35 | 272.4452 | 302.8033 | 264.319 | 269.1594 | 268.4462
Heating (kW)
| HEATSYS1 BOILER | 168.7242 | 169.609 | 154.4823 | 168.4509 | 156.3797 | 152.711 | 156.5897 | 175.5903 | 159.7157 | 165.5015 | 184.4815 | 169.2999 | 191.1115 | 181.4148 | 191.8348 | 218.7941
HVAC Efficiency
Air Conditioning (COP)
| AHU-1_COOLC DXCOIL | 3.27 | 3.28 | 3.34 | 3.34 | 3.43 | 3.45 | 3.52 | 3.31 | 3.73 | 3.5 | 3.32 | 3.73 | 3.34 | 3.71 | 3.44 | 3.58
| AHU-2_COOLC DXCOIL | 3.39 | 3.39 | 3.5 | 3.47 | 3.63 | 3.66 | 3.74 | 3.43 | 3.73 | 3.74 | 3.43 | 3.73 | 3.47 | 3.74 | 3.62 | 3.73
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
HVAC Control - Economizer
| AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| AHU-1_FAN | 16.51 | 16.58 | 16.84 | 16.72 | 15.92 | 16.83 | 15.82 | 16.36 | 18.68 | 16.01 | 16.29 | 18.37 | 16.38 | 17.59 | 16.28 | 16.26
| AHU-2_FAN | 15.28 | 15.69 | 17.21 | 15.56 | 13.98 | 16.64 | 15.21 | 15.58 | 17.33 | 15.14 | 15.15 | 16.46 | 15.1 | 15.97 | 15.02 | 16.22
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.07873 | 0.10509 | 0.07583 | 0.099001 | 0.12257 | 0.088861 | 0.14529 | 0.067269 | 0.037029 | 0.072612 | 0.097163 | 0.037032 | 0.053259 | 0.069996 | 0.053476 | 0.089268
| Total Cost ($/m2) | 41.76 | 53.29 | 38.45 | 47.19 | 51.77 | 45.81 | 52.97 | 31.96 | 18.55 | 27.65 | 43.76 | 17.97 | 24.32 | 33.04 | 23.71 | 42.78
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.0081931 | 0.0086254 | 0.010918 | 0.0083899 | 0.0082128 | 0.0083908 | 0.010149 | 0.0072523 | 0.0082673 | 0.0090225 | 0.0072488 | 0.008003 | 0.0088765 | 0.0080039 | 0.0041946
| Total Cost ($/m2) | 14.52 | 11 | 11.51 | 15.18 | 11.49 | 10.6 | 11.91 | 14.66 | 9.48 | 11.89 | 13.16 | 9.62 | 12.33 | 12.69 | 12.56 | 8.2
Total Utility Costs
| Cost Intensity ($/m2) | 56.28 | 64.28 | 49.96 | 62.38 | 63.26 | 56.41 | 64.88 | 46.62 | 28.02 | 39.54 | 56.91 | 27.58 | 36.66 | 45.72 | 36.27 | 50.98
Energy - End Uses
Electricity (kWh)
| Heating | 18966.6667 | 58494.4444 | 53941.6667 | 76097.2222 | 41825 | 56916.6667 | 88569.4444 | 112597.2222 | 78605.5556 | 121325 | 122761.1111 | 92166.6667 | 144911.1111 | 131366.6667 | 162127.7778 | 235177.7778
| Cooling | 990041.6667 | 829136.1111 | 637291.6667 | 623805.5556 | 494494.4444 | 457761.1111 | 253677.7778 | 536036.1111 | 303577.7778 | 197050 | 320291.6667 | 225980.5556 | 292063.8889 | 160733.3333 | 156475 | 99111.1111
| Interior Lighting | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444 | 170494.4444
| Exterior Lighting | 7088.8889 | 7086.1111 | 7086.1111 | 7083.3333 | 7080.5556 | 7077.7778 | 7080.5556 | 7077.7778 | 7080.5556 | 7066.6667 | 7077.7778 | 7075 | 7072.2222 | 7072.2222 | 7066.6667 | 7025
| Interior Equipment | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 269311.1111 | 269419.4444 | 277230.5556 | 270477.7778 | 258611.1111 | 275738.8889 | 257900 | 265000 | 303419.4444 | 260486.1111 | 263250 | 296663.8889 | 264669.4444 | 283930.5556 | 263422.2222 | 265352.7778
| Pumps | 8208.3333 | 8252.7778 | 7522.2222 | 8197.2222 | 7613.8889 | 7436.1111 | 7625 | 8541.6667 | 7775 | 8052.7778 | 8969.4444 | 8236.1111 | 9288.8889 | 8822.2222 | 9325 | 10625
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 1944.4444 | 34391.6667 | 223611.1111 | 105650 | 75111.1111 | 433997.2222 | 49972.2222 | 156175 | 483005.5556 | 132452.7778 | 268630.5556 | 493394.4444 | 297269.4444 | 481372.2222 | 366191.6667 | 483738.8889
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2017658.3333 | 1928872.2222 | 1928780.5556 | 1813402.7778 | 1606827.7778 | 1961025 | 1386919.4444 | 1807522.2222 | 1905555.5556 | 1448527.7778 | 1713077.7778 | 1845611.1111 | 1737375 | 1795391.6667 | 1686705.5556 | 1823125
Gas (MJ)
| Heating | 4600670 | 4876050 | 4850510 | 5056160 | 4976400 | 4680300 | 5161920 | 5255210 | 4732340 | 5229720 | 5304980 | 4804140 | 5617340 | 5191320 | 5720620 | 7177150
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 35250 | 40670 | 37520 | 45910 | 44900 | 41310 | 49380 | 50010 | 49220 | 52160 | 53610 | 53450 | 56740 | 57310 | 61890 | 68130
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4824290 | 5105100 | 5076410 | 5290440 | 5209670 | 4909980 | 5399670 | 5493600 | 4969940 | 5470250 | 5546970 | 5045970 | 5862450 | 5437010 | 5970890 | 7433650
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 12087860 | 12049040 | 12020020 | 11818700 | 10994260 | 11969670 | 10392590 | 12000680 | 11829940 | 10684950 | 11714040 | 11690170 | 12117000 | 11900410 | 12043030 | 13996910
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 17.9495 | 55.3574 | 51.0488 | 72.0161 | 39.5819 | 53.8642 | 83.8194 | 106.5586 | 74.3899 | 114.8183 | 116.1774 | 87.2237 | 137.1395 | 124.3214 | 153.4328 | 222.5651
| Cooling (elec) | 936.9455 | 784.6693 | 603.1136 | 590.3507 | 467.9746 | 433.2113 | 240.073 | 507.2884 | 287.2968 | 186.4822 | 303.1143 | 213.8612 | 276.4004 | 152.1132 | 148.0832 | 93.7958
| Interior Lighting (elec) | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508 | 161.3508
| Exterior Lighting (elec) | 6.7087 | 6.7061 | 6.7061 | 6.7035 | 6.7008 | 6.6982 | 6.7008 | 6.6982 | 6.7008 | 6.6877 | 6.6982 | 6.6956 | 6.6929 | 6.6929 | 6.6877 | 6.6482
| Interior Equipment (elec) | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 254.8679 | 254.9704 | 262.3626 | 255.972 | 244.7417 | 260.9509 | 244.0688 | 250.788 | 287.147 | 246.5162 | 249.1318 | 280.7537 | 250.4752 | 268.7033 | 249.2948 | 251.1218
| Pumps (elec) | 7.7681 | 7.8102 | 7.1188 | 7.7576 | 7.2056 | 7.0373 | 7.2161 | 8.0836 | 7.358 | 7.6209 | 8.4884 | 7.7944 | 8.7907 | 8.3491 | 8.8249 | 10.0552
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 1.8402 | 32.5472 | 211.6188 | 99.984 | 71.0829 | 410.7218 | 47.2922 | 147.7993 | 457.1018 | 125.3493 | 254.2238 | 466.9336 | 281.3268 | 455.5561 | 346.5527 | 457.7959
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1909.4508 | 1825.4263 | 1825.3396 | 1716.1495 | 1520.6532 | 1855.8547 | 1312.5386 | 1710.5844 | 1803.3601 | 1370.8429 | 1621.205 | 1746.6305 | 1644.1991 | 1699.1044 | 1596.2471 | 1725.3504
Gas (MJ/m2)
| Heating (gas) | 1209.4264 | 1281.8184 | 1275.1044 | 1329.1658 | 1308.1985 | 1230.3595 | 1356.968 | 1381.4922 | 1244.0398 | 1374.7913 | 1394.5757 | 1262.9147 | 1476.6891 | 1364.6967 | 1503.8394 | 1886.7327
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 9.2665 | 10.6913 | 9.8633 | 12.0688 | 11.8033 | 10.8596 | 12.981 | 13.1467 | 12.939 | 13.7118 | 14.093 | 14.051 | 14.9158 | 15.0657 | 16.2697 | 17.91
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1268.2117 | 1342.0312 | 1334.4891 | 1390.7534 | 1369.5206 | 1290.7379 | 1419.4679 | 1444.1602 | 1306.5002 | 1438.022 | 1458.1902 | 1326.487 | 1541.1237 | 1429.2838 | 1569.6305 | 1954.1615
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 3177.6625 | 3167.4575 | 3159.8287 | 3106.9056 | 2890.1764 | 3146.5927 | 2732.0091 | 3154.7446 | 3109.8604 | 2808.8649 | 3079.3925 | 3073.1176 | 3185.3229 | 3128.3856 | 3165.8776 | 3679.5145
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 345.2005 | 339.8306 | 356.9782 | 313.689 | 349.0421 | 351.4765 | 329.773 | 335.9791 | 343.175 | 330.1683 | 332.9835 | 349.3408 | 351.2158 | 356.688 | 365.891 | 387.0668
| Feb | 348.2973 | 320.7514 | 361.1693 | 321.1572 | 333.7004 | 349.9494 | 280.4131 | 330.0502 | 347.5021 | 337.6723 | 309.9114 | 336.664 | 331.2056 | 355.2861 | 350.9819 | 373.6422
| Mar | 349.804 | 331.2294 | 369.4311 | 323.567 | 346.4759 | 347.6234 | 331.0778 | 314.9104 | 349.8935 | 321.4665 | 315.0129 | 351.0591 | 325.7687 | 345.7797 | 326.1647 | 351.2464
| Apr | 356.0858 | 346.1022 | 361.5862 | 323.2491 | 347.5053 | 350.2824 | 339.2549 | 302.9493 | 371.0527 | 309.1231 | 348.6365 | 347.2608 | 331.798 | 345.5797 | 314.1824 | 330.7336
| May | 373.034 | 375.2023 | 392.0703 | 346.3924 | 305.1274 | 395.4479 | 286.8442 | 339.8262 | 362.0191 | 291.6482 | 333.1016 | 352.5849 | 329.2224 | 344.1077 | 349.9461 | 350.043
| Jun | 381.5768 | 378.0314 | 447.9285 | 355.6426 | 303.1306 | 412.0798 | 290.7682 | 375.806 | 398.7109 | 294.6454 | 361.9746 | 360.2647 | 356.7723 | 345.3132 | 322.9728 | 335.329
| Jul | 374.7859 | 382.2426 | 422.3517 | 375.0107 | 305.5932 | 393.9476 | 306.6097 | 377.9382 | 383.038 | 311.7709 | 366.053 | 349.1723 | 354.5774 | 332.7861 | 334.3361 | 299.0696
| Aug | 377.2038 | 385.3658 | 419.5279 | 361.0359 | 317.8687 | 376.3349 | 303.2058 | 378.9726 | 335.6859 | 308.013 | 362.2302 | 347.8812 | 355.4427 | 324.9873 | 328.1655 | 334.5086
| Sep | 372.1367 | 376.973 | 389.9172 | 344.9854 | 316.1212 | 379.3477 | 325.3244 | 349.0296 | 346.6102 | 311.7753 | 335.8597 | 363.1559 | 331.7861 | 339.4289 | 328.7348 | 314.8904
| Oct | 368.2895 | 359.9703 | 356.6002 | 335.434 | 338.8484 | 356.2395 | 292.0908 | 327.1485 | 349.7628 | 278.1128 | 349.892 | 353.7995 | 323.0506 | 347.1486 | 326.8741 | 336.7789
| Nov | 353.5754 | 341.5724 | 351.8482 | 308.3837 | 347.9239 | 351.7727 | 320.414 | 311.914 | 350.6281 | 331.9901 | 309.7388 | 350.4017 | 337.1101 | 334.181 | 326.008 | 355.4972
| Dec | 344.0219 | 332.145 | 361.2719 | 329.9371 | 346.7965 | 351.481 | 316.8286 | 317.5096 | 336.9734 | 310.3277 | 323.7705 | 342.119 | 331.0464 | 371.342 | 334.4664 | 366.5752
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-11:00 | 27-JAN-09:09 | 30-JAN-07:10 | 25-JAN-09:09 | 17-JAN-13:00 | 17-JAN-14:00 | 17-JAN-07:10 | 26-JAN-15:00 | 03-JAN-09:09 | 09-JAN-09:09 | 27-JAN-10:50 | 09-JAN-07:10 | 17-JAN-09:09 | 09-JAN-07:10 | 13-JAN-09:09
| Feb | 23-FEB-11:00 | 24-FEB-14:00 | 13-FEB-11:39 | 02-FEB-09:09 | 10-FEB-08:50 | 08-FEB-10:39 | 15-FEB-15:00 | 21-FEB-06:19 | 14-FEB-17:40 | 22-FEB-11:00 | 06-FEB-09:09 | 16-FEB-09:09 | 07-FEB-08:09 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
| Mar | 13-MAR-15:30 | 24-MAR-15:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-08:09 | 31-MAR-09:09 | 13-MAR-12:00 | 20-MAR-08:09 | 03-MAR-14:00 | 23-MAR-15:39 | 20-MAR-08:09 | 30-MAR-13:00 | 06-MAR-07:10 | 27-MAR-13:20 | 27-MAR-06:10 | 13-MAR-08:09
| Apr | 04-APR-16:00 | 21-APR-14:00 | 26-APR-16:49 | 14-APR-16:00 | 11-APR-16:00 | 27-APR-08:00 | 05-APR-09:00 | 04-APR-15:00 | 21-APR-16:00 | 03-APR-14:00 | 27-APR-14:00 | 06-APR-13:09 | 13-APR-15:00 | 06-APR-13:09 | 25-APR-08:00 | 03-APR-08:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-16:40 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 15-MAY-09:30 | 31-MAY-12:09 | 02-MAY-12:00 | 30-MAY-10:30 | 23-MAY-13:00
| Jun | 28-JUN-14:00 | 13-JUN-15:20 | 08-JUN-15:00 | 19-JUN-16:00 | 28-JUN-12:00 | 08-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 28-JUN-13:09 | 08-JUN-12:00 | 15-JUN-16:00 | 29-JUN-16:10 | 07-JUN-15:00 | 14-JUN-15:00 | 08-JUN-14:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 19-JUL-16:00 | 03-JUL-15:00 | 20-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-16:49 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-13:00 | 13-JUL-16:00 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
| Aug | 21-AUG-14:00 | 31-AUG-13:00 | 01-AUG-16:00 | 17-AUG-14:00 | 08-AUG-14:00 | 04-AUG-15:50 | 15-AUG-12:09 | 17-AUG-15:39 | 01-AUG-15:20 | 18-AUG-16:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-15:30 | 11-AUG-14:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 12-SEP-16:00 | 11-SEP-13:00 | 25-SEP-14:00 | 20-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:00 | 01-SEP-15:00 | 06-SEP-12:50 | 06-SEP-12:00 | 14-SEP-14:00 | 15-SEP-16:00 | 27-SEP-14:00 | 07-SEP-15:00
| Oct | 06-OCT-15:30 | 06-OCT-15:00 | 17-OCT-08:39 | 12-OCT-15:00 | 30-OCT-07:00 | 16-OCT-08:30 | 30-OCT-07:10 | 03-OCT-09:00 | 13-OCT-10:09 | 16-OCT-15:00 | 26-OCT-15:00 | 16-OCT-08:00 | 25-OCT-12:09 | 19-OCT-13:09 | 25-OCT-14:00 | 30-OCT-08:09
| Nov | 07-NOV-14:00 | 03-NOV-14:30 | 16-NOV-10:39 | 03-NOV-13:00 | 29-NOV-09:00 | 13-NOV-09:00 | 20-NOV-09:39 | 03-NOV-13:00 | 01-NOV-12:00 | 20-NOV-09:09 | 02-NOV-12:09 | 10-NOV-10:39 | 01-NOV-14:00 | 21-NOV-10:00 | 24-NOV-07:10 | 06-NOV-09:09
| Dec | 15-DEC-15:30 | 19-DEC-14:00 | 04-DEC-10:00 | 18-DEC-07:10 | 14-DEC-11:30 | 04-DEC-11:39 | 29-DEC-09:09 | 11-DEC-09:09 | 05-DEC-13:00 | 11-DEC-07:10 | 26-DEC-09:09 | 11-DEC-07:10 | 30-DEC-07:10 | 11-DEC-07:10 | 21-DEC-08:09 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 29361.38 | 30795.17 | 27506.07 | 27738.21 | 23592.25 | 30614.22 | 21349.51 | 29268.32 | 28188.65 | 15057.52 | 27925.74 | 27555.65 | 27898.67 | 28404.01 | 27390.15 | 31561.49
| Total Source Energy (MJ/m2) | 7718.54 | 8095.45 | 7230.81 | 7291.84 | 6201.95 | 8047.88 | 5612.37 | 7694.07 | 7410.25 | 3958.33 | 7341.14 | 7243.85 | 7334.02 | 7466.86 | 7200.34 | 8296.91
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
| Total Building | 243.08 | 286.54 | 539.94 | 381.97 | 341.07 | 821.69 | 307.4 | 449.63 | 887.32 | 417.86 | 600.23 | 901.23 | 638.58 | 885.13 | 730.88 | 888.3
Emissions
| Carbon Equivalent (kg) | 640337.1545 | 735455.5784 | 673792.8195 | 653995.8969 | 281727.897 | 749945.2486 | 259454.3318 | 586834.0319 | 868037.0108 | 204145.7207 | 1013350 | 844920.8107 | 700406.7533 | 754146.944 | 685018.5381 | 647053.482
| CO2 (kg) | 1532640 | 1880440 | 1633760 | 1543420 | 772773.8407 | 1822360 | 714058.7436 | 1380060 | 2072720 | 535618.5886 | 2396290 | 2019620 | 1676430 | 1809280 | 1642100 | 1672380
| NOX (kg) | 2487.8848 | 2363.5404 | 2554.4188 | 2698.333 | 675.4601 | 2801.2642 | 625.7289 | 2446.8759 | 3417.4316 | 661.4222 | 4099.5256 | 3320.918 | 2779.1122 | 2965.9838 | 2711.2779 | 1961.578
| SO2 (kg) | 8637.6741 | 9202.094 | 7757.3708 | 6366.4649 | 4677.0747 | 10788.5262 | 4037.22 | 6599.6484 | 8322.5102 | 1121.0629 | 11546.251 | 8060.7646 | 4102.051 | 4795.3652 | 3982.4932 | 9282.4335
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0399 | 0.0264 | 0.0216 | 0.0238 | 0.0027 | 0.0207 | 0.0024 | 0.0272 | 0.0329 | 0.005 | 0.0354 | 0.0319 | 0.0305 | 0.0338 | 0.0297 | 0.0322
| Water for Electricity (m3) | 1068.87 | 3138.5 | 57293.3 | 11322.2 | 28212.3 | 53798.8 | 24351.2 | 410.3753 | 8652.74 | 14799.3 | 2657.74 | 8380.55 | 2695.43 | 113728 | 2616.82 | 1862.65

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12087.86 | 3177.66 | 3177.66
Net Site Energy | 12087.86 | 3177.66 | 3177.66
Total Source Energy | 29361.38 | 7718.54 | 7718.54
Net Source Energy | 29361.38 | 7718.54 | 7718.54
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 68.28 | 4600.67 | 0 | 0 | 0 | 0
Cooling | 3564.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.52 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 969.52 | 0 | 0 | 0 | 0 | 0
Pumps | 29.55 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 7 | 0 | 0 | 0 | 0 | 2.61
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 35.25 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7263.57 | 4824.29 | 0 | 0 | 0 | 243.08
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.251 | 0.11 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.251 | 0.11 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.251 | 0.11 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.251 | 0.11 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 97.22 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 168724.21 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 399514.04 | 272645.47 | 126868.56 | 0.68 | 3.27
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 329648.71 | 235074.42 | 94574.29 | 0.71 | 3.39
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2172.98 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 224.52 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12057.72 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1799.09 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2328.22 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1096.45 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 787.25 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2314.85 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148391.73 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 511.96 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 763.37 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 993.17 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 14190.79 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1186 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.8 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10783.87 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2471.45 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5365.73 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2314.29 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 770.77 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 68339.6 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.8 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 997.34 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2517.84 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2471.45 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 218.18 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3545.38 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.8 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3874.54 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33780.3 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35224.23 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28235.76 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1814.19 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2627.34 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2603.58 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4656.14 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.8 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9815.12 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7495.72 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 669.23 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10867.77 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1300.1 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 458.95 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2892.87 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1285.71 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4132.67 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7848.31 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3151.61 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1389.61 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 11063.03 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2945.9 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3988.97 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 173.65 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3983.85 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1935.48 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3058.81 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 262.68 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5369.94 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2780.05 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3725.13 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 570.69 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2928.7 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1955.51 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4033.98 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2377.46 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2020.73 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 425.26 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 425.26 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 425.26 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 482.58 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 482.58 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 482.19 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 408.9 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.3 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.02 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.84 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5485.14 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1003.14 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7113.54 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1966.4 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1036.76 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1089.79 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.65 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 175.12 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 209.3 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 722.72 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5555.47 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1904.53 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.47 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3754.75 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 203.4 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1042.64 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 465.06 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.33 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 805.44 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5541.54 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1335.02 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3768.61 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1013.24 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 19726.46 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2812.16 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.47 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9089.97 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3213.73 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 584.08 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 344.15 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 268.67 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2646.41 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12837.9 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9521.99 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 614.06 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5735.69 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2065.97 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2214.48 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2932.17 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1421.79 | 1
AHU-1_HEATC | Coil:Heating:Water | 51599.41 | -
AHU-2_HEATC | Coil:Heating:Water | 21045.53 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.51 | 27785.4 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.28 | 25889.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 929.07 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 122006.9387 | 195.0145 | 663.7173 | 0 | 0.0031 | 82129.0947 | 50670.388
February | 110292.446 | 176.4921 | 601.5797 | 0 | 0.0028 | 74440.2997 | 45825.5032
March | 125208.1501 | 201.2556 | 689.9807 | 0 | 0.0032 | 85379.9915 | 52112.5274
April | 123118.0736 | 198.5099 | 683.2943 | 0 | 0.0032 | 84553.1506 | 51304.1285
May | 134734.5075 | 219.9242 | 768.8933 | 0 | 0.0035 | 95147.8892 | 56413.7618
June | 133612.9997 | 219.3601 | 772.4616 | 0 | 0.0036 | 95590.5733 | 56071.0899
July | 136656.8554 | 225.5913 | 799.7709 | 0 | 0.0037 | 98971.1119 | 57472.091
August | 139706.0721 | 230.5382 | 816.9333 | 0 | 0.0038 | 101094.8736 | 58745.7695
September | 132779.5891 | 217.8973 | 766.899 | 0 | 0.0035 | 94902.1302 | 55711.8702
October | 133019.2516 | 216.0828 | 750.9068 | 0 | 0.0035 | 92921.2077 | 55591.2118
November | 122168.6606 | 196.7248 | 676.0233 | 0 | 0.0031 | 83653.1881 | 50883.0172
December | 119335.4062 | 190.494 | 647.2138 | 0 | 0.003 | 80086.7 | 49535.796
Annual Sum or Average | 1532640 | 2487.8848 | 8637.6741 | 0 | 0.0399 | 1068870 | 640337.1545
Minimum of Months | 110292.446 | 176.4921 | 601.5797 | 0 | 0.0028 | 74440.2997 | 45825.5032
Maximum of Months | 139706.0721 | 230.5382 | 816.9333 | 0 | 0.0038 | 101094.8736 | 58745.7695
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 558113000000 | 345200.461 | 06-JAN-13:00 | 40487.594 | 120867.849 | 32792.758 | 359.696 | 149755.428 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 505863000000 | 348297.335 | 23-FEB-11:00 | 40487.594 | 120867.849 | 32918.323 | 480.841 | 152605.592 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 580204000000 | 349803.956 | 13-MAR-15:30 | 40487.594 | 120867.849 | 32686.748 | 143.621 | 154681.008 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 574586000000 | 356085.751 | 04-APR-16:00 | 40487.594 | 120867.849 | 34246.828 | 52.376 | 159493.968 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 646583000000 | 373034.031 | 24-MAY-14:00 | 40487.594 | 120867.849 | 34573.104 | 50.125 | 176118.223 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 649591000000 | 381576.803 | 28-JUN-14:00 | 40487.594 | 120867.849 | 35751.994 | 42.146 | 183490.084 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 672564000000 | 374785.935 | 13-JUL-14:00 | 40487.594 | 120867.849 | 35053.755 | 53.238 | 177386.363 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 686996000000 | 377203.822 | 21-AUG-14:00 | 40487.594 | 120867.849 | 34060.769 | 81.675 | 180768.799 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 644913000000 | 372136.691 | 07-SEP-13:00 | 40487.594 | 120867.849 | 34810.288 | 66.406 | 174967.417 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 631451000000 | 368289.54 | 06-OCT-15:30 | 40487.594 | 120867.849 | 35467.808 | 56.495 | 170472.658 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 568470000000 | 353575.408 | 07-NOV-14:00 | 40487.594 | 120867.849 | 34265.193 | 88.775 | 156928.861 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 544234000000 | 344021.885 | 15-DEC-15:30 | 40487.594 | 120867.849 | 32996.487 | 202.196 | 148530.624 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7263570000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 505863000000 | 344021.885 |  | 40487.594 | 120867.849 | 32686.748 | 42.146 | 148530.624 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 686996000000 | 381576.803 |  | 40487.594 | 120867.849 | 35751.994 | 480.841 | 183490.084 | 0 | 937.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 158849.71 | 55243.58 | 0 | 214093.29
Cost per Total Building Area ($/m2) | 41.76 | 14.52 | 0 | 56.28
Cost per Net Conditioned Building Area ($/m2) | 41.76 | 14.52 | 0 | 56.28

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12049.04 | 3167.46 | 3167.46
Net Site Energy | 12049.04 | 3167.46 | 3167.46
Total Source Energy | 30795.17 | 8095.45 | 8095.45
Net Source Energy | 30795.17 | 8095.45 | 8095.45
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 210.58 | 4876.05 | 0 | 0 | 0 | 0
Cooling | 2984.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.51 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 969.91 | 0 | 0 | 0 | 0 | 0
Pumps | 29.71 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 123.81 | 0 | 0 | 0 | 0 | 46.06
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 40.67 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6943.94 | 5105.1 | 0 | 0 | 0 | 286.54
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.251 | 0.11 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.251 | 0.11 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.251 | 0.11 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.251 | 0.11 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 97.22 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 169609.03 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 397479.26 | 272190.16 | 125289.11 | 0.68 | 3.28
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 337044.92 | 240784.14 | 96260.78 | 0.71 | 3.39
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2302.41 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 210.37 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12386.64 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1783.57 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2307.57 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1074.31 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 984.89 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2311.51 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148415.19 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 496.73 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 727.25 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 968.04 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 14402.24 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1130.97 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10666.61 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2356.67 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5320.82 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2305.82 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 734.55 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 68289.57 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1075.75 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2495.82 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2356.67 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 204.41 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3513.43 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3807.33 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33772.67 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35141.8 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28151.2 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1800.83 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2505.25 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2594.05 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4639.09 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9779.17 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7627.81 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 637.81 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11411.1 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1350.58 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 437.2 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2882.28 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1281 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4117.53 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8115.47 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3187.12 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1305.47 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 11045.93 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2897.35 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3916.39 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 162.67 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3893.63 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2062.16 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3211.14 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 262.58 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5614.3 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2870.23 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3852.91 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 615.67 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2932.97 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1945.84 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4023.08 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2363.37 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2037.63 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 416.59 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 416.59 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 416.59 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 467.31 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 467.31 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 466.29 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 418.72 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.3 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.02 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.85 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5504.91 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 989.52 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7289.29 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2237.09 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1036.3 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1089.3 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.62 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 175.07 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 209.24 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 718.19 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5586.35 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1898.61 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 374.09 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3740.97 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 200.64 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 970.58 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 457.31 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 507.76 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 815.17 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5596.63 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1330.12 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3769.31 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 989.95 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 20040.13 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2757.52 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 374.09 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9574.97 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3258.61 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 581.93 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 338.28 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 265.47 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2683.41 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13285.21 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9915.54 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 604.59 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5740.35 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2136.05 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2337.47 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2978.11 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1518.95 | 1
AHU-1_HEATC | Coil:Heating:Water | 33497.54 | -
AHU-2_HEATC | Coil:Heating:Water | 41151.7 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.58 | 27902.03 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.69 | 26591.37 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 933.94 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 153307.9286 | 191.0388 | 727.046 | 0 | 0.0021 | 247960.895 | 59746.5912
February | 132165.7681 | 164.2022 | 619.9039 | 0 | 0.0018 | 211417.2612 | 51443.8491
March | 151699.8909 | 189.3361 | 723.6373 | 0 | 0.0021 | 246799.9084 | 59158.7258
April | 149274.2718 | 186.9017 | 720.3722 | 0 | 0.0021 | 245689.4014 | 58289.2419
May | 164667.8381 | 207.5409 | 813.7824 | 0 | 0.0023 | 277554.7396 | 64476.1872
June | 168743.4523 | 213.9246 | 851.3876 | 0 | 0.0024 | 290386.8473 | 66232.7314
July | 173621.4634 | 221.082 | 889.6311 | 0 | 0.0025 | 303435.5128 | 68272.8366
August | 175191.8833 | 222.9752 | 896.1867 | 0 | 0.0026 | 305670.9586 | 68876.6451
September | 161021.4537 | 203.4746 | 803.1765 | 0 | 0.0023 | 273940.0386 | 63116.6721
October | 156691.5105 | 196.6247 | 762.2741 | 0 | 0.0022 | 259982.6308 | 61241.7665
November | 144918.0024 | 180.8898 | 691.5409 | 0 | 0.002 | 235853.3936 | 56516.3212
December | 149139.1054 | 185.5497 | 703.1553 | 0 | 0.002 | 239811.385 | 58084.0103
Annual Sum or Average | 1880440 | 2363.5404 | 9202.094 | 0 | 0.0264 | 3138500 | 735455.5784
Minimum of Months | 132165.7681 | 164.2022 | 619.9039 | 0 | 0.0018 | 211417.2612 | 51443.8491
Maximum of Months | 175191.8833 | 222.9752 | 896.1867 | 0 | 0.0026 | 305670.9586 | 68876.6451
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 548614000000 | 339830.58 | 03-JAN-11:00 | 40487.594 | 120867.849 | 32275.104 | 957.052 | 144300.973 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 467761000000 | 320751.43 | 24-FEB-14:00 | 40487.594 | 120867.849 | 32896.848 | 321.066 | 125236.065 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 546045000000 | 331229.374 | 24-MAR-15:00 | 40487.594 | 120867.849 | 32273.218 | 170.305 | 136488.4 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 543588000000 | 346102.184 | 21-APR-14:00 | 40487.594 | 120867.849 | 33491.647 | 74.268 | 150238.818 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 614090000000 | 375202.311 | 26-MAY-14:00 | 40487.594 | 120867.849 | 34980.201 | 48.059 | 177876.6 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 642481000000 | 378031.414 | 13-JUN-15:20 | 40487.594 | 120867.849 | 35346.685 | 37.69 | 180349.589 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 671352000000 | 382242.637 | 18-JUL-12:00 | 40487.594 | 120867.849 | 34276.448 | 78.135 | 185590.603 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 676298000000 | 385365.844 | 31-AUG-13:00 | 40487.594 | 120867.849 | 35776.136 | 68.301 | 187223.956 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 606093000000 | 376972.963 | 15-SEP-14:00 | 40487.594 | 120867.849 | 34363.599 | 76.673 | 180235.24 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 575212000000 | 359970.286 | 06-OCT-15:00 | 40487.594 | 120867.849 | 34502.625 | 59.794 | 163110.416 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 521826000000 | 341572.417 | 03-NOV-14:30 | 40487.594 | 120867.849 | 32850.647 | 227.006 | 146197.313 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 530583000000 | 332145.023 | 19-DEC-14:00 | 40487.594 | 120867.849 | 32126.998 | 620.586 | 137099.988 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6943940000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 467761000000 | 320751.43 |  | 40487.594 | 120867.849 | 32126.998 | 37.69 | 125236.065 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 676298000000 | 385365.844 |  | 40487.594 | 120867.849 | 35776.136 | 957.052 | 187223.956 | 0 | 942.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 202706.7 | 41826.46 | 0 | 244533.17
Cost per Total Building Area ($/m2) | 53.29 | 11 | 0 | 64.28
Cost per Net Conditioned Building Area ($/m2) | 53.29 | 11 | 0 | 64.28

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12020.02 | 3159.83 | 3159.83
Net Site Energy | 12020.02 | 3159.83 | 3159.83
Total Source Energy | 27506.07 | 7230.81 | 7230.81
Net Source Energy | 27506.07 | 7230.81 | 7230.81
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 194.19 | 4850.51 | 0 | 0 | 0 | 0
Cooling | 2294.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.51 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 998.03 | 0 | 0 | 0 | 0 | 0
Pumps | 27.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 805 | 0 | 0 | 0 | 0 | 299.46
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 37.52 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6943.61 | 5076.41 | 0 | 0 | 0 | 539.94
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.251 | 0.11 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.251 | 0.11 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.251 | 0.11 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.251 | 0.11 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 97.22 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 154482.3 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 376991.26 | 264952.85 | 112038.41 | 0.7 | 3.34
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 333674.11 | 248579.87 | 85094.24 | 0.74 | 3.5
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2462.32 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 111.17 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12766.22 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1631.45 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2107.23 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 836.5 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 945.27 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2251.07 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148456.66 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 369.23 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 426.34 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 747.42 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 14307.95 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 696.42 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1191.15 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10337.21 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1446.04 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4863.31 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2223.49 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 439.45 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67766.13 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1191.15 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1085.56 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2273.34 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1446.04 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 107.2 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3201.35 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1191.15 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3065.9 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34168.73 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34900.69 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27259.74 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1671.74 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1537.51 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2501.43 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4473.45 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1191.15 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9430.01 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7444.8 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 382.14 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 12022.78 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1353.38 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 255.93 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2779.37 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.26 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3970.52 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8485.67 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2614.81 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 786.16 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 10876.73 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2889.36 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3910.05 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 83.38 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3827.6 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2171.5 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3605.87 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 261.55 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6057.76 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3061.95 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4132.58 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 712.92 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3103.5 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2108.31 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4192.77 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2556.63 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2123.25 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 455.64 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 455.64 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 455.64 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 501.12 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 501.12 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 499.7 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 469.84 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.32 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.05 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.88 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5866.41 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1008 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7758.99 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2658.47 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1031.41 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1084.21 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.4 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 174.6 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 208.67 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.81 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5796.02 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1933.43 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 360.71 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3607.13 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 207.29 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1102.84 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 473 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 558.69 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 823.02 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5772.96 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1282.53 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3966.56 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1042.91 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 20954.96 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2892.59 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 394.88 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10675.54 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3298.36 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 561.11 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 368.92 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 288.64 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2715.22 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 14125.18 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10671.39 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 640.01 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6174.31 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2471.74 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2437.41 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 3185.64 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1654.3 | 1
AHU-1_HEATC | Coil:Heating:Water | 10909.38 | -
AHU-2_HEATC | Coil:Heating:Water | 26115.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.84 | 28342.66 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.21 | 28977.92 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 850.65 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 130467.1538 | 201.1114 | 598.6697 | 0 | 0.0017 | 4421400 | 53516.1477
February | 122742.1616 | 190.0962 | 569.6799 | 0 | 0.0016 | 4207350 | 50437.7121
March | 131976.4298 | 204.8045 | 615.4814 | 0 | 0.0017 | 4545640 | 54273.4304
April | 133579.3445 | 208.8684 | 634.3609 | 0 | 0.0018 | 4685170 | 55092.0216
May | 139390.0184 | 218.4885 | 665.8209 | 0 | 0.0019 | 4917550 | 57542.5469
June | 144405.7489 | 228.3049 | 703.9183 | 0 | 0.002 | 5199040 | 59810.7664
July | 150604.7065 | 239.2929 | 742.7258 | 0 | 0.0021 | 5485740 | 62498.3638
August | 150639.3639 | 238.9628 | 740.1104 | 0 | 0.002 | 5466400 | 62473.7964
September | 137369.2095 | 215.9236 | 660.5274 | 0 | 0.0018 | 4878490 | 56769.2587
October | 132867.3681 | 206.9724 | 625.3175 | 0 | 0.0017 | 4618330 | 54719.2308
November | 123705.4525 | 191.1052 | 570.6574 | 0 | 0.0016 | 4214540 | 50784.7192
December | 136013.5604 | 210.4878 | 630.1012 | 0 | 0.0018 | 4653580 | 55874.8257
Annual Sum or Average | 1633760 | 2554.4188 | 7757.3708 | 0 | 0.0216 | 57293300 | 673792.8195
Minimum of Months | 122742.1616 | 190.0962 | 569.6799 | 0 | 0.0016 | 4207350 | 50437.7121
Maximum of Months | 150639.3639 | 239.2929 | 742.7258 | 0 | 0.0021 | 5485740 | 62498.3638
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 535848000000 | 356978.23 | 27-JAN-09:09 | 40487.594 | 120867.849 | 31602.342 | 12063.718 | 51098.013 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 509907000000 | 361169.302 | 13-FEB-11:39 | 40487.594 | 120867.849 | 31453.099 | 15731.889 | 51770.157 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 550905000000 | 369431.122 | 30-MAR-15:00 | 40487.594 | 120867.849 | 34811.943 | 47.686 | 115036.298 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 567815000000 | 361586.218 | 26-APR-16:49 | 40487.594 | 120867.849 | 35359.205 | 24.849 | 127854.303 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 595979000000 | 392070.273 | 19-MAY-16:40 | 40487.594 | 120867.849 | 37023.896 | 6.806 | 155075.737 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 630094000000 | 447928.474 | 08-JUN-15:00 | 40487.594 | 120867.849 | 40581.712 | 0 | 212942.89 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 664839000000 | 422351.736 | 19-JUL-16:00 | 40487.594 | 120867.849 | 40413.104 | 0 | 219724.475 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 662496000000 | 419527.888 | 01-AUG-16:00 | 40487.594 | 120867.849 | 40487.711 | 0 | 216826.02 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 591245000000 | 389917.182 | 12-SEP-16:00 | 40487.594 | 120867.849 | 38992.269 | 0 | 188710.756 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 559715000000 | 356600.232 | 17-OCT-08:39 | 40487.594 | 120867.849 | 31565.749 | 11230.822 | 51589.503 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 510778000000 | 351848.237 | 16-NOV-10:39 | 40487.594 | 120867.849 | 31661.024 | 10646.733 | 51999.311 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 563987000000 | 361271.9 | 04-DEC-10:00 | 40487.594 | 120867.849 | 31629.302 | 14899.997 | 52528.444 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6943610000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 509907000000 | 351848.237 |  | 40487.594 | 120867.849 | 31453.099 | 0 | 51098.013 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 664839000000 | 447928.474 |  | 40487.594 | 120867.849 | 40581.712 | 15731.889 | 219724.475 | 0 | 858.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 146258.91 | 43786.28 | 0 | 190045.19
Cost per Total Building Area ($/m2) | 38.45 | 11.51 | 0 | 49.96
Cost per Net Conditioned Building Area ($/m2) | 38.45 | 11.51 | 0 | 49.96

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11818.7 | 3106.91 | 3106.91
Net Site Energy | 11818.7 | 3106.91 | 3106.91
Total Source Energy | 27738.21 | 7291.84 | 7291.84
Net Source Energy | 27738.21 | 7291.84 | 7291.84
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 273.95 | 5056.16 | 0 | 0 | 0 | 0
Cooling | 2245.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.5 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 973.72 | 0 | 0 | 0 | 0 | 0
Pumps | 29.51 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 380.34 | 0 | 0 | 0 | 0 | 141.49
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 45.91 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6528.25 | 5290.44 | 0 | 0 | 0 | 381.97
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.252 | 0.162 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.252 | 0.162 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.252 | 0.162 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.252 | 0.162 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.252 | 0.162 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.252 | 0.162 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.252 | 0.162 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.252 | 0.162 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.252 | 0.162 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.252 | 0.162 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.252 | 0.162 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 97.22 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 168450.89 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 376908.55 | 264179.6 | 112728.95 | 0.7 | 3.34
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 312494.35 | 229381.24 | 83113.11 | 0.73 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2174.87 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 189.11 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 11895.79 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1761.03 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2277.92 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1024.47 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1025.29 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2286.61 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148315.37 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 472.78 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 672.33 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 921.73 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 12965.33 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1046.92 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10296.81 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2181.39 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5254.35 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2229.86 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 679.35 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 68219.48 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1225.97 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2464.05 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2181.39 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 183.75 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3467.21 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3705.4 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 32469.62 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33640.01 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28027.65 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1781.94 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2318.83 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2508.59 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4486.27 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9457.02 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7369.7 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 589.9 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10935.46 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1297.49 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 404.16 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2787.33 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1238.8 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3981.89 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7531.33 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2955.4 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1173.89 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 9847.7 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2491.2 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3818.46 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 146.19 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3541.06 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2045.26 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3062.23 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 261.62 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5051.64 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2811.37 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3754.87 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 573.57 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2704.15 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1829.37 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3920.92 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2208.35 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1984.93 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 422.36 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 422.36 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 422.36 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 467.47 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 467.47 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 465.97 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 396.86 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.31 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.05 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.88 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5009.23 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 988.6 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 6798.72 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2382.66 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1031.77 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1084.6 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.42 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 174.63 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 208.71 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 625.41 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5469.03 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1903.29 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 361.75 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3617.49 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 200.39 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 970.55 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 458.06 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 479.62 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 809.27 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5393.83 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1286.21 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3541.72 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 994.51 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 19085.8 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2763.36 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 361.75 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9069.21 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3230.59 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 562.72 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 340.88 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 266.29 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2660.74 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12436.88 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9310.6 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 607.43 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5238.32 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1934.63 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2265.86 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2583.3 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1494.28 | 1
AHU-1_HEATC | Coil:Heating:Water | 30438.41 | -
AHU-2_HEATC | Coil:Heating:Water | 50777.39 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.72 | 28138.64 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.56 | 26362.64 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 927.56 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 131538.4274 | 227.7293 | 531.6178 | 0 | 0.002 | 945408.4574 | 55530.4303
February | 118388.4386 | 204.9633 | 478.4729 | 0 | 0.0018 | 850897.6392 | 49979.0389
March | 127428.7947 | 220.9395 | 516.6024 | 0 | 0.0019 | 918709.2724 | 53825.5299
April | 120621.8799 | 209.148 | 489.0581 | 0 | 0.0018 | 869725.5361 | 50951.2763
May | 128069.5321 | 224.0342 | 528.9244 | 0 | 0.002 | 940644.209 | 54279.3782
June | 131778.4833 | 233.1058 | 556.9066 | 0 | 0.0021 | 990436.1785 | 56089.9241
July | 138770.997 | 247.1713 | 594.773 | 0 | 0.0022 | 1057800 | 59222.8626
August | 140905.4045 | 251.0436 | 604.2671 | 0 | 0.0022 | 1074680 | 60140.2761
September | 131475.1827 | 232.0203 | 552.9336 | 0 | 0.0021 | 983364.5786 | 55910.1269
October | 123598.4636 | 214.3681 | 501.4159 | 0 | 0.0019 | 891702.9083 | 52214.0506
November | 121280.6711 | 209.6874 | 488.7739 | 0 | 0.0018 | 869213.4007 | 51173.8769
December | 129562.664 | 224.1223 | 522.719 | 0 | 0.002 | 929581.0968 | 54679.1262
Annual Sum or Average | 1543420 | 2698.333 | 6366.4649 | 0 | 0.0238 | 11322200 | 653995.8969
Minimum of Months | 118388.4386 | 204.9633 | 478.4729 | 0 | 0.0018 | 850897.6392 | 49979.0389
Maximum of Months | 140905.4045 | 251.0436 | 604.2671 | 0 | 0.0022 | 1074680 | 60140.2761
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 545114000000 | 313689.026 | 30-JAN-07:10 | 40487.594 | 96785.431 | 30979.994 | 66297.677 | 21334.509 | 1622 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 490620000000 | 321157.247 | 02-FEB-09:09 | 40487.594 | 120867.849 | 31059.922 | 38470.994 | 16027.832 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 529719000000 | 323567.043 | 22-MAR-16:00 | 40487.594 | 120867.849 | 33391.941 | 218.114 | 83557.993 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 501476000000 | 323249.094 | 14-APR-16:00 | 40487.594 | 120867.849 | 33832.338 | 74.53 | 127051.152 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 542367000000 | 346392.363 | 31-MAY-16:00 | 40487.594 | 120867.849 | 34146.314 | 46.744 | 149908.232 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 571076000000 | 355642.621 | 19-JUN-16:00 | 40487.594 | 120867.849 | 35124.249 | 22.162 | 158205.136 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 609916000000 | 375010.729 | 03-JUL-15:00 | 40487.594 | 120867.849 | 36161.264 | 28.153 | 176530.238 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 619653000000 | 361035.947 | 17-AUG-14:00 | 40487.594 | 120867.849 | 34375.233 | 46.094 | 164323.545 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 566999000000 | 344985.381 | 11-SEP-13:00 | 40487.594 | 120867.849 | 33497.985 | 92.765 | 149103.557 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 514147000000 | 335433.978 | 12-OCT-15:00 | 40487.594 | 120867.849 | 33685.303 | 167.2 | 139290.401 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 501180000000 | 308383.688 | 03-NOV-13:00 | 40487.594 | 120867.849 | 31821.516 | 5016.325 | 57217.19 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 535988000000 | 329937.096 | 18-DEC-07:10 | 40487.594 | 96785.431 | 30980.044 | 71864.923 | 17532.043 | 1622 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6528250000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 490620000000 | 308383.688 |  | 40487.594 | 96785.431 | 30979.994 | 22.162 | 16027.832 | 0 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 619653000000 | 375010.729 |  | 40487.594 | 120867.849 | 36161.264 | 71864.923 | 176530.238 | 1622 | 935.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 179529.35 | 57761.12 | 0 | 237290.48
Cost per Total Building Area ($/m2) | 47.19 | 15.18 | 0 | 62.38
Cost per Net Conditioned Building Area ($/m2) | 47.19 | 15.18 | 0 | 62.38

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10994.26 | 2890.18 | 2890.18
Net Site Energy | 10994.26 | 2890.18 | 2890.18
Total Source Energy | 23592.25 | 6201.95 | 6201.95
Net Source Energy | 23592.25 | 6201.95 | 6201.95
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 150.57 | 4976.4 | 0 | 0 | 0 | 0
Cooling | 1780.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 931 | 0 | 0 | 0 | 0 | 0
Pumps | 27.41 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 270.4 | 0 | 0 | 0 | 0 | 100.59
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 44.9 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5784.58 | 5209.67 | 0 | 0 | 0 | 341.07
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.252 | 0.162 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.252 | 0.162 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.252 | 0.162 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.252 | 0.162 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.252 | 0.162 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.252 | 0.162 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.252 | 0.162 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.252 | 0.162 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.252 | 0.162 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.252 | 0.162 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.252 | 0.162 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 97.22 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 156379.72 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 329329.27 | 238820.55 | 90508.72 | 0.73 | 3.43
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 249060.87 | 192424.08 | 56636.8 | 0.77 | 3.63
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2214.01 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 191.84 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12037.66 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1763.24 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2280.83 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1034.06 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 682.65 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2189.13 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 147966.72 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 476.93 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 680.08 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 930.27 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 12442.18 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1059.19 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9753.56 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2206.87 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5260.91 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2306.09 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 687.31 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 68222.46 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 792.82 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2467.16 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2206.87 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 186.4 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3471.72 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3715.37 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31679.16 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32891.85 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28038.82 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1783.8 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2345.92 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2594.36 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4639.64 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9780.33 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7398.54 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 596.82 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11021.97 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1251.09 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 408.81 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2882.62 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1281.15 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4118.02 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7196.55 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3028.27 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1196.55 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 7274.69 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2121.51 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2779.41 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 148.29 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2894.02 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1868.16 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3006.24 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 262.59 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4820.54 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2830.39 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3788.24 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 589.02 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2473.24 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1596.51 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3693.75 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1936.24 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1871.47 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 398.63 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 398.63 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 398.63 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 401.03 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.35 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 396.81 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 305.6 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.3 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.02 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.84 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4525.24 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 940.88 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 6589.34 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2418.41 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1036.33 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1089.33 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.64 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 175.1 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 209.28 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 514.38 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5166.26 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1847.48 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 374.14 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3741.41 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 185.59 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 762.75 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 427.2 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 379.69 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 779.88 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4987.1 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1330.28 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3272.29 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 858.59 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 16994.12 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2418.82 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 374.14 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 8648.16 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3088.83 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 582 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 258.34 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 201.42 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2543.33 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11487.16 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 8599.69 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 490.23 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 4652.21 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1434.11 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2136.36 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1898.09 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1437.34 | 1
AHU-1_HEATC | Coil:Heating:Water | 27807.82 | -
AHU-2_HEATC | Coil:Heating:Water | 23713 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.92 | 26970.49 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.98 | 23685.25 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 861.09 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 64679.2638 | 56.591 | 381.3178 | 0 | 0.0002 | 2300070 | 23548.9877
February | 55410.9853 | 48.545 | 315.3681 | 0 | 0.0002 | 1902210 | 20140.011
March | 63081.708 | 55.2154 | 367.9393 | 0 | 0.0002 | 2219350 | 22955.2537
April | 60534.7995 | 52.9984 | 350.8735 | 0 | 0.0002 | 2116400 | 22021.6971
May | 65068.5256 | 56.8997 | 389.3273 | 0 | 0.0002 | 2348420 | 23708.1486
June | 65263.0261 | 57.0074 | 401.6396 | 0 | 0.0002 | 2422740 | 23813.0298
July | 67614.6899 | 59.022 | 423.2057 | 0 | 0.0002 | 2552870 | 24692.7419
August | 69128.2572 | 60.2809 | 443.8238 | 0 | 0.0002 | 2677290 | 25279.4951
September | 65493.0074 | 57.1535 | 412.8742 | 0 | 0.0002 | 2490560 | 23926.903
October | 67302.7716 | 58.7679 | 417.9984 | 0 | 0.0002 | 2521440 | 24568.8991
November | 63296.1058 | 55.3479 | 379.0515 | 0 | 0.0002 | 2286430 | 23063.3599
December | 65900.7004 | 57.631 | 393.6553 | 0 | 0.0002 | 2374520 | 24009.3701
Annual Sum or Average | 772773.8407 | 675.4601 | 4677.0747 | 0 | 0.0027 | 28212300 | 281727.897
Minimum of Months | 55410.9853 | 48.545 | 315.3681 | 0 | 0.0002 | 1902210 | 20140.011
Maximum of Months | 69128.2572 | 60.2809 | 443.8238 | 0 | 0.0002 | 2677290 | 25279.4951
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 471601000000 | 349042.123 | 25-JAN-09:09 | 40487.594 | 120867.849 | 29753.447 | 8859.11 | 48204.962 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 390025000000 | 333700.418 | 10-FEB-08:50 | 40487.594 | 108826.64 | 29791.608 | 9499.895 | 47307.013 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 455051000000 | 346475.865 | 30-MAR-08:09 | 40487.594 | 120867.849 | 29852.632 | 6006.727 | 48391.901 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 433942000000 | 347505.277 | 11-APR-16:00 | 40487.594 | 120867.849 | 32285.889 | 62.719 | 96436.98 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 481513000000 | 305127.362 | 30-MAY-08:00 | 40487.594 | 120867.849 | 29851.02 | 4357.211 | 108694.526 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 496753000000 | 303130.607 | 28-JUN-12:00 | 40487.594 | 120867.849 | 31407.845 | 216.845 | 109281.312 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 523433000000 | 305593.166 | 20-JUL-14:00 | 40487.594 | 120867.849 | 32469.622 | 58.737 | 110840.201 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 548946000000 | 317868.689 | 08-AUG-14:00 | 40487.594 | 120867.849 | 32984.037 | 50.441 | 122609.606 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 510658000000 | 316121.245 | 25-SEP-14:00 | 40487.594 | 120867.849 | 33023.73 | 81.73 | 120791.18 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 516990000000 | 338848.435 | 30-OCT-07:00 | 40487.594 | 108826.64 | 29580.659 | 14269.49 | 44814.889 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 468805000000 | 347923.896 | 29-NOV-09:00 | 40487.594 | 120867.849 | 29877.394 | 7172.465 | 48649.432 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 486866000000 | 346796.473 | 14-DEC-11:30 | 40487.594 | 120867.849 | 30280.001 | 4683.35 | 49608.516 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 5784580000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 390025000000 | 303130.607 |  | 40487.594 | 108826.64 | 29580.659 | 50.441 | 44814.889 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 548946000000 | 349042.123 |  | 40487.594 | 120867.849 | 33023.73 | 14269.49 | 122609.606 | 0 | 869.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 196951.33 | 43708.63 | 0 | 240659.95
Cost per Total Building Area ($/m2) | 51.77 | 11.49 | 0 | 63.26
Cost per Net Conditioned Building Area ($/m2) | 51.77 | 11.49 | 0 | 63.26

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11969.67 | 3146.59 | 3146.59
Net Site Energy | 11969.67 | 3146.59 | 3146.59
Total Source Energy | 30614.22 | 8047.88 | 8047.88
Net Source Energy | 30614.22 | 8047.88 | 8047.88
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 204.9 | 4680.3 | 0 | 0 | 0 | 0
Cooling | 1647.94 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.48 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 992.66 | 0 | 0 | 0 | 0 | 0
Pumps | 26.77 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1562.39 | 0 | 0 | 0 | 0 | 581.21
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.31 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7059.69 | 4909.98 | 0 | 0 | 0 | 821.69
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.252 | 0.162 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.252 | 0.162 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.252 | 0.162 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.252 | 0.162 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.252 | 0.162 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.252 | 0.162 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.252 | 0.162 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.252 | 0.162 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.252 | 0.162 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.252 | 0.162 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.252 | 0.162 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.252 | 0.162 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.252 | 0.162 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.252 | 0.162 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.252 | 0.162 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.252 | 0.162 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.252 | 0.162 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 97.22 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 152711 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 338975.51 | 248512.65 | 90462.86 | 0.73 | 3.45
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 288719.92 | 225691.15 | 63028.78 | 0.78 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2173.92 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 106.93 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 11731.43 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1603.85 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2075.49 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 803.84 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 894.99 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2163.69 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148377.14 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 354.91 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 397.79 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 718.3 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 12578.65 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 647.84 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9729.9 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1345.48 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4792.56 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2138.68 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 409.53 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67683.29 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1062.78 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2230.95 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1345.48 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 103.12 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3144.53 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 2945.18 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31631.23 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32656.05 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27110.01 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1651.34 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1430.38 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2406.02 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4302.82 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9070.31 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6925.84 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 356.08 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10855.68 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1218.33 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 238.79 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2673.35 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1188.15 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3819.07 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7635.84 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2203.68 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 756.18 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 9364.6 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2156.98 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3318.54 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 80.2 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2982.12 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2074.31 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3217.12 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 260.48 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5304.1 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2900.04 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3879.96 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 616.08 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2682.48 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1910.05 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4005.86 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2310.02 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2028.63 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 423.44 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 423.44 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 423.44 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 464.98 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 464.98 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 463.61 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 447.24 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.33 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.08 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.92 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4990.65 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 977.81 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7061.74 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2578.22 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1026.4 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1078.92 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.17 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 174.06 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 208.06 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 624.68 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5574.74 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1881.64 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 346.92 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3469.25 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 197.78 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 963.64 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 450.43 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 528.42 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 803.53 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5463.38 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1233.51 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3504.19 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 963.01 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 19351.27 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2695.29 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 380.75 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9468.67 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3205.85 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 539.66 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 334.62 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 261.46 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2637.9 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12707.81 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9597.62 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 581.39 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5191.86 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2008.85 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2347.88 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2753.08 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1554.95 | 1
AHU-1_HEATC | Coil:Heating:Water | 12449.63 | -
AHU-2_HEATC | Coil:Heating:Water | 35775.2 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.83 | 28327.33 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.64 | 28006.11 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 840.89 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 155070.1287 | 236.9718 | 904.9014 | 0 | 0.0017 | 4512380 | 63670.079
February | 135328.177 | 206.5534 | 787.3529 | 0 | 0.0015 | 3926210 | 55538.3145
March | 154989.0944 | 237.4466 | 910.0549 | 0 | 0.0018 | 4538110 | 63699.0241
April | 150399.0345 | 231.2818 | 891.2556 | 0 | 0.0017 | 4444400 | 61902.7027
May | 156789.4836 | 241.6689 | 934.3881 | 0 | 0.0018 | 4659510 | 64591.1452
June | 158425.3104 | 245.6911 | 958.2434 | 0 | 0.0018 | 4778530 | 65421.0325
July | 157805.9072 | 244.2392 | 949.8785 | 0 | 0.0018 | 4736790 | 65114.1824
August | 156952.0302 | 243.2061 | 947.4499 | 0 | 0.0018 | 4724700 | 64791.8344
September | 147311.8187 | 226.7838 | 875.3061 | 0 | 0.0017 | 4364870 | 60657.9682
October | 146928.3627 | 225.0119 | 861.9214 | 0 | 0.0017 | 4298080 | 60377.2617
November | 145209.0505 | 221.8921 | 847.2605 | 0 | 0.0016 | 4224950 | 59620.154
December | 157147.3135 | 240.5174 | 920.5135 | 0 | 0.0018 | 4590250 | 64561.5499
Annual Sum or Average | 1822360 | 2801.2642 | 10788.5262 | 0 | 0.0207 | 53798800 | 749945.2486
Minimum of Months | 135328.177 | 206.5534 | 787.3529 | 0 | 0.0015 | 3926210 | 55538.3145
Maximum of Months | 158425.3104 | 245.6911 | 958.2434 | 0 | 0.0018 | 4778530 | 65421.0325
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 592133000000 | 351476.55 | 17-JAN-13:00 | 40487.594 | 120867.849 | 31954.618 | 7679.971 | 49637.558 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 515213000000 | 349949.353 | 08-FEB-10:39 | 40487.594 | 120867.849 | 31776.141 | 7074.47 | 48894.34 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 595509000000 | 347623.434 | 31-MAR-09:09 | 40487.594 | 120867.849 | 31690.59 | 5797.793 | 47930.648 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 583212000000 | 350282.399 | 27-APR-08:00 | 40487.594 | 120867.849 | 31728.673 | 7222.083 | 49127.24 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 611439000000 | 395447.875 | 11-MAY-15:00 | 40487.594 | 120867.849 | 36059.311 | 16.329 | 128281.032 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 627058000000 | 412079.769 | 08-JUN-15:00 | 40487.594 | 120867.849 | 39133.895 | 0 | 169631.693 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 621581000000 | 393947.612 | 24-JUL-15:00 | 40487.594 | 120867.849 | 38981.997 | 0 | 174414.295 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 619994000000 | 376334.859 | 04-AUG-15:50 | 40487.594 | 120867.849 | 39478.657 | 0 | 174651.799 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 572776000000 | 379347.678 | 20-SEP-14:00 | 40487.594 | 120867.849 | 37393.425 | 24.271 | 140861.38 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 564011000000 | 356239.477 | 16-OCT-08:30 | 40487.594 | 120867.849 | 31351.349 | 14385.803 | 48297.921 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 554415000000 | 351772.743 | 13-NOV-09:00 | 40487.594 | 120867.849 | 31305.737 | 16043.917 | 42218.686 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 602351000000 | 351480.977 | 04-DEC-11:39 | 40487.594 | 120867.849 | 31499.969 | 12256.4 | 45520.204 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7059690000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 515213000000 | 347623.434 |  | 40487.594 | 120867.849 | 31305.737 | 0 | 42218.686 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 627058000000 | 412079.769 |  | 40487.594 | 120867.849 | 39478.657 | 16043.917 | 174651.799 | 0 | 848.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 174258.86 | 40324.53 | 0 | 214583.39
Cost per Total Building Area ($/m2) | 45.81 | 10.6 | 0 | 56.41
Cost per Net Conditioned Building Area ($/m2) | 45.81 | 10.6 | 0 | 56.41

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10392.59 | 2732.01 | 2732.01
Net Site Energy | 10392.59 | 2732.01 | 2732.01
Total Source Energy | 21349.51 | 5612.37 | 5612.37
Net Source Energy | 21349.51 | 5612.37 | 5612.37
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 318.85 | 5161.92 | 0 | 0 | 0 | 0
Cooling | 913.24 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 928.44 | 0 | 0 | 0 | 0 | 0
Pumps | 27.45 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 179.9 | 0 | 0 | 0 | 0 | 66.92
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 49.38 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4992.91 | 5399.67 | 0 | 0 | 0 | 307.4
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.39 | 0.223 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.39 | 0.223 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.39 | 0.223 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.39 | 0.223 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.39 | 0.223 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.39 | 0.223 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.39 | 0.223 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.39 | 0.223 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.39 | 0.223 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.39 | 0.223 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.39 | 0.223 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.39 | 0.223 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.39 | 0.223 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.39 | 0.223 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.39 | 0.223 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.39 | 0.223 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.39 | 0.223 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.39 | 0.223 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.39 | 0.223 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.39 | 0.223 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.39 | 0.223 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.39 | 0.223 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.39 | 0.223 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.39 | 0.223 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.39 | 0.223 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.39 | 0.223 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.39 | 0.223 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.39 | 0.223 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 97.22 | 5.83 | 0.39 | 0.223
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 156589.71 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 304792.88 | 227625.94 | 77166.93 | 0.75 | 3.52
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 251855.72 | 201145.89 | 50709.82 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 3201.95 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 115.67 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 15274.64 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1575.57 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2039.42 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 773.07 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 833.74 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1977.13 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 147708.51 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 341.34 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 369.86 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 690.82 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 14073.24 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 600.12 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8923.41 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1246.72 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4723.96 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2313.47 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 380.13 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67584.47 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 908.53 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2190.12 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1246.72 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 111.54 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3086.97 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 2834.76 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34650.58 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33818.53 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26954.1 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1631.21 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1325.19 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2602.66 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4654.49 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9811.64 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 8092.06 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 330.49 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 14741.57 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1414.02 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 222.03 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2891.85 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1285.25 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4131.2 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 9290.8 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3067.89 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 817.98 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 7091.55 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2187.98 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2159.66 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 86.76 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2414.65 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1616.96 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4278.68 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 263.45 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6215.19 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3544.39 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4898.15 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1019.99 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2715.45 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1589.32 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3705.24 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1945.14 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1880.02 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 431.87 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 431.87 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 431.87 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.69 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.69 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.69 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 290.67 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.54 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.67 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 955.66 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5099.69 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 897.04 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 8623.46 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2922.17 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1039.76 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1092.97 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 84.11 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 176.5 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 211.06 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 636.56 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5110.62 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1829.13 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.34 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3753.42 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 171.47 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 654.92 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.23 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 319.02 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 742.89 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4766.96 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1334.55 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3546.18 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 698.73 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 15716.21 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2079.53 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.34 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12611.67 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2908.46 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 583.87 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 220.04 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 172.05 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2398.38 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13965.1 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10746.65 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 387.06 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5154.73 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1476.59 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2034.37 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1536.84 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1691.86 | 1
AHU-1_HEATC | Coil:Heating:Water | 21003.35 | -
AHU-2_HEATC | Coil:Heating:Water | 27312.83 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.82 | 26798.05 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.21 | 25777.99 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 862.25 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 60424.3271 | 52.9961 | 333.3441 | 0 | 0.0002 | 2010580 | 21929.9809
February | 52471.2694 | 46.0469 | 284.7878 | 0 | 0.0002 | 1717680 | 19029.2709
March | 59520.4257 | 52.1922 | 330.3485 | 0 | 0.0002 | 1992520 | 21607.9998
April | 56190.0861 | 49.2975 | 307.2733 | 0 | 0.0002 | 1853320 | 20384.9621
May | 59752.9209 | 52.3753 | 335.3474 | 0 | 0.0002 | 2022690 | 21703.7183
June | 58991.1757 | 51.6666 | 338.4117 | 0 | 0.0002 | 2041220 | 21449.426
July | 61494.5051 | 53.8437 | 355.5327 | 0 | 0.0002 | 2144500 | 22368.0678
August | 63387.903 | 55.458 | 374.2662 | 0 | 0.0002 | 2257540 | 23080.5314
September | 61124.9003 | 53.4775 | 361.0194 | 0 | 0.0002 | 2177640 | 22256.8869
October | 61525.3555 | 53.8849 | 353.1661 | 0 | 0.0002 | 2130210 | 22371.525
November | 58504.9896 | 51.2839 | 327.9039 | 0 | 0.0002 | 1977800 | 21249.0973
December | 60670.8853 | 53.2061 | 335.8188 | 0 | 0.0002 | 2025510 | 22022.8654
Annual Sum or Average | 714058.7436 | 625.7289 | 4037.22 | 0 | 0.0024 | 24351200 | 259454.3318
Minimum of Months | 52471.2694 | 46.0469 | 284.7878 | 0 | 0.0002 | 1717680 | 19029.2709
Maximum of Months | 63387.903 | 55.458 | 374.2662 | 0 | 0.0002 | 2257540 | 23080.5314
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 412244000000 | 329772.984 | 17-JAN-14:00 | 40487.594 | 120867.849 | 30574.791 | 4263.078 | 32709.354 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 352190000000 | 280413.132 | 15-FEB-15:00 | 40487.594 | 120867.849 | 31826.655 | 491.129 | 85869.588 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 408542000000 | 331077.816 | 13-MAR-12:00 | 40487.594 | 120867.849 | 30098.909 | 3330.136 | 35423.01 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 380000000000 | 339254.908 | 05-APR-09:00 | 40487.594 | 120867.849 | 29919.23 | 5531.325 | 41578.592 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 414728000000 | 286844.198 | 17-MAY-13:00 | 40487.594 | 120867.849 | 31581.113 | 151.044 | 92886.28 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 418526000000 | 290768.161 | 15-JUN-12:00 | 40487.594 | 120867.849 | 31599.838 | 177.918 | 96764.644 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 439704000000 | 306609.737 | 03-JUL-12:00 | 40487.594 | 120867.849 | 31878.645 | 144.835 | 112360.495 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 462881000000 | 303205.754 | 15-AUG-12:09 | 40487.594 | 120867.849 | 31538.96 | 328.075 | 109112.957 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 446498000000 | 325324.439 | 28-SEP-14:00 | 40487.594 | 120867.849 | 35903.598 | 72.547 | 127122.533 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 436774000000 | 292090.782 | 30-OCT-07:10 | 40487.594 | 108826.64 | 29633.118 | 22778.53 | 46631.026 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 405522000000 | 320413.972 | 20-NOV-09:39 | 40487.594 | 120867.849 | 29692.942 | 16745.028 | 11750.24 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 415306000000 | 316828.567 | 29-DEC-09:09 | 40487.594 | 120867.849 | 29704.261 | 25673.793 | 0 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 4992910000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 352190000000 | 280413.132 |  | 40487.594 | 108826.64 | 29633.118 | 72.547 | 0 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 462881000000 | 339254.908 |  | 40487.594 | 120867.849 | 35903.598 | 25673.793 | 127122.533 | 0 | 870.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 201501.73 | 45307.78 | 0 | 246809.51
Cost per Total Building Area ($/m2) | 52.97 | 11.91 | 0 | 64.88
Cost per Net Conditioned Building Area ($/m2) | 52.97 | 11.91 | 0 | 64.88

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12000.68 | 3154.75 | 3154.75
Net Site Energy | 12000.68 | 3154.75 | 3154.75
Total Source Energy | 29268.32 | 7694.07 | 7694.07
Net Source Energy | 29268.32 | 7694.07 | 7694.07
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 405.35 | 5255.21 | 0 | 0 | 0 | 0
Cooling | 1929.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.48 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 954 | 0 | 0 | 0 | 0 | 0
Pumps | 30.75 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 562.23 | 0 | 0 | 0 | 0 | 209.15
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 50.01 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6507.08 | 5493.6 | 0 | 0 | 0 | 449.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 175590.3 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 380247.84 | 263432.11 | 116815.73 | 0.69 | 3.31
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 322835.39 | 233958.9 | 88876.49 | 0.72 | 3.43
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2294.84 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 173.06 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12202.57 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1742.93 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2254.02 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 991.33 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1123.84 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2260.27 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148293.93 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 456.74 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 632.18 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 891.68 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 14540.88 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 986.15 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10314 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2054.51 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5199.65 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2302 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 639.24 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 68154.66 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1363.88 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2438.46 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2054.51 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 168.13 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3430.11 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3620.62 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33150.87 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34891.38 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27924.45 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1766.55 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2183.91 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2589.75 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4631.4 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9762.97 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7467.73 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 555.11 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11421.41 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1344.63 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 379.99 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2877.5 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1278.88 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4110.71 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8139.06 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2977.53 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1085.91 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 9823.96 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2816.47 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3544.22 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 133.71 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3664.82 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2040.67 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3251.54 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 262.53 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5812.34 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2909.9 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3898.47 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 627.24 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2995.59 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1883.57 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3969.52 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2279.96 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2010.22 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 420.73 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 420.73 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 420.73 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 457.21 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 457.21 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 455.24 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 431.37 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.3 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.02 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.85 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5652.79 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 986.28 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7396.82 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2605.87 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1036.11 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1089.09 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.62 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 175.05 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 209.22 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 749.23 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5520.14 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1892.87 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 373.47 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3734.76 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 198.31 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 946.17 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 451.78 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 476.04 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.9 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5396.06 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1327.91 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3850.73 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 967.35 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 19050.34 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2705.26 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 373.47 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9685.52 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3186.63 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 580.97 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 334.33 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 261.36 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2624.33 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13323.51 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9910.08 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 579.34 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5912.14 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2051.62 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2317.35 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2587.88 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1588.08 | 1
AHU-1_HEATC | Coil:Heating:Water | 37264.1 | -
AHU-2_HEATC | Coil:Heating:Water | 60257.81 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.36 | 27533.8 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.58 | 26396.23 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 966.87 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 122843.4117 | 215.6371 | 575.489 | 0 | 0.0024 | 35783.9075 | 52037.8705
February | 108833.1298 | 191.4487 | 512.0908 | 0 | 0.0021 | 31841.956 | 46139.9869
March | 116545.7368 | 205.1575 | 549.162 | 0 | 0.0023 | 34147.1127 | 49422.6975
April | 106522.7497 | 186.3116 | 495.2953 | 0 | 0.002 | 30797.2088 | 45062.389
May | 111618.9533 | 196.6942 | 527.1031 | 0 | 0.0022 | 32775.5582 | 47352.576
June | 115906.0228 | 208.4724 | 570.6692 | 0 | 0.0023 | 35486.1004 | 49557.4937
July | 121134.0574 | 219.4467 | 605.0835 | 0 | 0.0025 | 37626.6592 | 51936.4624
August | 123234.1136 | 224.4029 | 621.9332 | 0 | 0.0025 | 38674.8557 | 52942.1812
September | 110284.8513 | 195.9126 | 529.4687 | 0 | 0.0022 | 32923.2372 | 46930.1073
October | 112191.3235 | 197.5364 | 528.887 | 0 | 0.0022 | 32886.4196 | 47580.1759
November | 111046.4354 | 195.1631 | 521.5162 | 0 | 0.0022 | 32427.9682 | 47061.9479
December | 119895.4622 | 210.6927 | 562.9503 | 0 | 0.0023 | 35004.3355 | 50810.1436
Annual Sum or Average | 1380060 | 2446.8759 | 6599.6484 | 0 | 0.0272 | 410375.3189 | 586834.0319
Minimum of Months | 106522.7497 | 186.3116 | 495.2953 | 0 | 0.002 | 30797.2088 | 45062.389
Maximum of Months | 123234.1136 | 224.4029 | 621.9332 | 0 | 0.0025 | 38674.8557 | 52942.1812
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 567404000000 | 335979.125 | 17-JAN-07:10 | 40487.594 | 96785.431 | 30400.649 | 92005.462 | 0 | 1622 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 504899000000 | 330050.157 | 21-FEB-06:19 | 26991.729 | 82335.981 | 30400.649 | 108441.838 | 7860.634 | 1622 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 541450000000 | 314910.364 | 20-MAR-08:09 | 40487.594 | 120867.849 | 30407.601 | 46124.403 | 25253.234 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 488333000000 | 302949.327 | 04-APR-15:00 | 40487.594 | 120867.849 | 31769.45 | 330.015 | 108519.476 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 519703000000 | 339826.205 | 31-MAY-15:00 | 40487.594 | 120867.849 | 32238.583 | 150.691 | 145106.545 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 562682000000 | 375805.96 | 30-JUN-16:00 | 40487.594 | 120867.849 | 35391.895 | 27.627 | 178056.051 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 596624000000 | 377938.175 | 25-JUL-12:00 | 40487.594 | 120867.849 | 34159.027 | 72.355 | 181376.406 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 613244000000 | 378972.623 | 17-AUG-15:39 | 40487.594 | 120867.849 | 35393.845 | 42.899 | 181205.491 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 522044000000 | 349029.648 | 08-SEP-14:00 | 40487.594 | 120867.849 | 34286.091 | 66.836 | 152346.335 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 521460000000 | 327148.473 | 03-OCT-09:00 | 40487.594 | 120867.849 | 30867.048 | 2444.125 | 131506.914 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 514191000000 | 311914.047 | 03-NOV-13:00 | 40487.594 | 120867.849 | 31945.2 | 1120.787 | 116517.674 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 555043000000 | 317509.585 | 11-DEC-09:09 | 40487.594 | 120867.849 | 30408.489 | 52864.173 | 22189.785 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6507080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 488333000000 | 302949.327 |  | 26991.729 | 82335.981 | 30400.649 | 27.627 | 0 | 0 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 613244000000 | 378972.623 |  | 40487.594 | 120867.849 | 35393.845 | 108441.838 | 181376.406 | 1622 | 974.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 121590.94 | 55756.18 | 0 | 177347.12
Cost per Total Building Area ($/m2) | 31.96 | 14.66 | 0 | 46.62
Cost per Net Conditioned Building Area ($/m2) | 31.96 | 14.66 | 0 | 46.62

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11829.94 | 3109.86 | 3109.86
Net Site Energy | 11829.94 | 3109.86 | 3109.86
Total Source Energy | 28188.65 | 7410.25 | 7410.25
Net Source Energy | 28188.65 | 7410.25 | 7410.25
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 282.98 | 4732.34 | 0 | 0 | 0 | 0
Cooling | 1092.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1092.31 | 0 | 0 | 0 | 0 | 0
Pumps | 27.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1738.82 | 0 | 0 | 0 | 0 | 646.84
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 49.22 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6860 | 4969.94 | 0 | 0 | 0 | 887.32
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 159715.73 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 309227.78 | 246966.39 | 62261.39 | 0.8 | 3.73
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 286819.93 | 229070.24 | 57749.68 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2012.28 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 121.96 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 11406.95 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1671.8 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2160.25 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 893.11 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1036.45 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2100.38 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148093.05 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 393.91 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 477.04 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 797.83 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13562.54 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 776.73 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9562.32 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1613.25 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4984.15 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1904.53 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 491.04 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67932.55 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1249.38 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2337.19 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1613.25 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 118.04 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3284.3 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3279.33 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31100.86 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33380.99 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26668.42 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1706 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1715.29 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2142.59 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 3831.73 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8077.26 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6856.72 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 426.96 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10121.46 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1109.56 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 286.39 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2380.66 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1058.06 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3400.94 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7221.68 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2399.18 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 793.74 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 9202.93 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2181.51 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2955.45 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 92.79 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3062.12 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1758.92 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 2891.69 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 258.27 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5330.93 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2748.47 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3672.88 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 546.52 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2673.93 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1703.08 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3805.97 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2077.25 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1927.99 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 372.43 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 372.43 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 372.43 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 382.07 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 382.07 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 380.5 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 391.59 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.63 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.84 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 955.86 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4990.66 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 909.56 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 6928.53 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2021.95 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1064.29 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1121.45 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 82.92 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 173.95 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 208 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 605.92 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5269.18 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1802.2 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 308.86 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3199.94 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 177.89 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 809.5 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 430.09 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 430.58 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 785.57 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5156.59 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1098.16 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3480.63 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 819.13 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 17798.26 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2404.21 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 328.33 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 8678.85 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3111.65 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 480.45 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 257.39 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 201.39 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2565.33 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12376.93 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9069.25 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 465.4 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5050.38 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1931.98 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2117.77 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2259.57 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1387.36 | 1
AHU-1_HEATC | Coil:Heating:Water | 25720.08 | -
AHU-2_HEATC | Coil:Heating:Water | 46303.03 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.68 | 31445.95 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.33 | 29167.25 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 879.46 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 183789.4802 | 302.4824 | 735.0195 | 0 | 0.0029 | 764180.7402 | 76916.1646
February | 164501.7641 | 270.8714 | 658.6027 | 0 | 0.0026 | 684733.1335 | 68857.2673
March | 186120.6005 | 307.3615 | 749.985 | 0 | 0.003 | 779747.5475 | 77994.0045
April | 177975.3557 | 294.0952 | 718.1638 | 0 | 0.0028 | 746664.8587 | 74598.8654
May | 183678.4793 | 304.3708 | 745.7855 | 0 | 0.0029 | 775388.9101 | 77072.8654
June | 166064.1899 | 274.4683 | 670.401 | 0 | 0.0027 | 697006.9652 | 69611.7221
July | 163354.5318 | 269.2867 | 655.6569 | 0 | 0.0026 | 681672.6625 | 68406.9113
August | 164989.5909 | 272.3051 | 663.9677 | 0 | 0.0026 | 690315.49 | 69123.2945
September | 154119.8882 | 253.1305 | 613.5414 | 0 | 0.0024 | 637879.2752 | 64448.2525
October | 170711.0564 | 280.7376 | 681.5237 | 0 | 0.0027 | 708560.9645 | 71421.224
November | 175826.6436 | 289.7772 | 705.3397 | 0 | 0.0028 | 733326.278 | 73622.9508
December | 181586.0073 | 298.5448 | 724.5232 | 0 | 0.0029 | 753265.7843 | 75963.4885
Annual Sum or Average | 2072720 | 3417.4316 | 8322.5102 | 0 | 0.0329 | 8652740 | 868037.0108
Minimum of Months | 154119.8882 | 253.1305 | 613.5414 | 0 | 0.0024 | 637879.2752 | 64448.2525
Maximum of Months | 186120.6005 | 307.3615 | 749.985 | 0 | 0.003 | 779747.5475 | 77994.0045
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 605852000000 | 343175.049 | 26-JAN-15:00 | 40487.594 | 120867.849 | 37014.624 | 2916.805 | 41000.645 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 542865000000 | 347502.122 | 14-FEB-17:40 | 40487.594 | 120867.849 | 36577.662 | 1081.407 | 47600.078 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 618193000000 | 349893.476 | 03-MAR-14:00 | 40487.594 | 120867.849 | 37192.329 | 1345.349 | 49112.823 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 591965000000 | 371052.73 | 21-APR-16:00 | 40487.594 | 120867.849 | 39841.461 | 0.39 | 90635.682 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 614738000000 | 362019.141 | 12-MAY-15:00 | 40487.594 | 120867.849 | 39629.988 | 20.977 | 90327.991 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 552596000000 | 398710.9 | 26-JUN-16:00 | 40487.594 | 120867.849 | 40237.616 | 0 | 111164.591 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 540438000000 | 383038.03 | 31-JUL-16:49 | 40487.594 | 120867.849 | 42318.087 | 0 | 125674.009 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 547290000000 | 335685.894 | 01-AUG-15:20 | 40487.594 | 120867.849 | 42707.92 | 0 | 130735 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 505718000000 | 346610.232 | 20-SEP-16:00 | 40487.594 | 120867.849 | 40524.33 | 4.897 | 100764.91 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 561756000000 | 349762.772 | 13-OCT-10:09 | 40487.594 | 120867.849 | 35855.742 | 2598.212 | 49065.843 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 581390000000 | 350628.118 | 01-NOV-12:00 | 40487.594 | 120867.849 | 36488.33 | 2722.841 | 49173.972 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 597198000000 | 336973.413 | 05-DEC-13:00 | 40487.594 | 120867.849 | 36101.17 | 5935.726 | 32693.542 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6860000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 505718000000 | 335685.894 |  | 40487.594 | 120867.849 | 35855.742 | 0 | 32693.542 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 618193000000 | 398710.9 |  | 40487.594 | 120867.849 | 42707.92 | 5935.726 | 130735 | 0 | 887.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 70560.47 | 36043.52 | 0 | 106603.99
Cost per Total Building Area ($/m2) | 18.55 | 9.48 | 0 | 28.02
Cost per Net Conditioned Building Area ($/m2) | 18.55 | 9.48 | 0 | 28.02

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10684.95 | 2808.87 | 2808.87
Net Site Energy | 10684.95 | 2808.87 | 2808.87
Total Source Energy | 15057.52 | 3958.33 | 3958.33
Net Source Energy | 15057.52 | 3958.33 | 3958.33
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 436.77 | 5229.72 | 0 | 0 | 0 | 0
Cooling | 709.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.44 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 937.75 | 0 | 0 | 0 | 0 | 0
Pumps | 28.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 476.83 | 0 | 0 | 0 | 0 | 177.38
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 52.16 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5214.7 | 5470.25 | 0 | 0 | 0 | 417.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 165501.54 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 312392.53 | 232093.14 | 80299.4 | 0.74 | 3.5
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 250554 | 200106.27 | 50447.73 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2777.29 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 114.08 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 13810.64 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1633.27 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2109.63 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 839.66 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 962.11 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2101.92 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 147936.09 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 370.43 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 428.02 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 750.17 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13570.07 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 699.64 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9336.28 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1452.67 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4868.85 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2281.62 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 441.3 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67767.97 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1149.71 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2277.11 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1452.67 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 110.01 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3205.33 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3080.21 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33139.64 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33534.24 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27267.09 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1673.1 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1544.5 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2566.83 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4590.41 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9676.55 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7702.76 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 383.75 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 13164.83 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1334.84 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 256.93 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2852.03 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1267.56 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4074.33 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8111.61 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2873.1 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 806.72 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 8408.14 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2267.75 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2696.58 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 85.56 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2809.91 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1823.14 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3881.08 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 263.05 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5863.49 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3279.76 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4472.48 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 852.37 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2776.69 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1698.88 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3794.14 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2065.9 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1922.37 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 439.35 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 439.35 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 439.35 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.31 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 399.5 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 396.86 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 365.9 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.55 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.68 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 955.67 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5215.22 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 941.93 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7660.35 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3031.29 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1037.95 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1091.12 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 84 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 176.27 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 210.78 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 653.55 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5268.05 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1871.54 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 370.16 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3701.64 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 183.35 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 765.53 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 422.27 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 399.36 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 766.8 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5009.53 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1316.13 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3583.92 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 830.29 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 17005.97 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2397.37 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 370.16 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11309.57 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3024 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 575.81 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 251.25 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 195.88 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2493.46 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12964.77 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9842.94 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 476.76 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5317.1 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1732.05 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2203.12 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1892.16 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1671.99 | 1
AHU-1_HEATC | Coil:Heating:Water | 32033.31 | -
AHU-2_HEATC | Coil:Heating:Water | 45437.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.01 | 27129.82 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.14 | 25644.75 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 911.32 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47718.9161 | 59.0534 | 100.6848 | 0 | 0.0004 | 1329180 | 18201.1442
February | 42485.9745 | 52.5938 | 89.7475 | 0 | 0.0004 | 1184800 | 16206.9196
March | 46454.3666 | 57.531 | 98.2876 | 0 | 0.0004 | 1297540 | 17723.3595
April | 43404.8519 | 53.2722 | 88.7569 | 0 | 0.0004 | 1171630 | 16508.2619
May | 43394.5456 | 52.9847 | 86.9811 | 0 | 0.0004 | 1148130 | 16474.909
June | 42933.9538 | 53.1494 | 90.7005 | 0 | 0.0004 | 1197380 | 16377.9199
July | 45280.1091 | 56.6239 | 99.2968 | 0 | 0.0004 | 1310980 | 17333.9589
August | 46338.5583 | 58.6049 | 105.8154 | 0 | 0.0005 | 1397170 | 17809.5597
September | 43030.2702 | 53.2181 | 90.5808 | 0 | 0.0004 | 1195790 | 16409.2403
October | 43540.2016 | 52.8317 | 85.1608 | 0 | 0.0004 | 1124030 | 16494.7763
November | 44918.6201 | 55.3038 | 92.962 | 0 | 0.0004 | 1227170 | 17102.6106
December | 46118.221 | 56.2552 | 92.0887 | 0 | 0.0004 | 1215530 | 17503.0608
Annual Sum or Average | 535618.5886 | 661.4222 | 1121.0629 | 0 | 0.005 | 14799300 | 204145.7207
Minimum of Months | 42485.9745 | 52.5938 | 85.1608 | 0 | 0.0004 | 1124030 | 16206.9196
Maximum of Months | 47718.9161 | 59.0534 | 105.8154 | 0 | 0.0005 | 1397170 | 18201.1442
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 468352000000 | 330168.325 | 03-JAN-09:09 | 40487.594 | 120867.849 | 30087.188 | 37806.304 | 0 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 417477000000 | 337672.3 | 22-FEB-11:00 | 40487.594 | 120867.849 | 30112.878 | 10158.961 | 35125.627 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 457204000000 | 321466.458 | 23-MAR-15:39 | 40487.594 | 120867.849 | 31176.473 | 1372.146 | 26643.005 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 412835000000 | 309123.065 | 03-APR-14:00 | 40487.594 | 120867.849 | 30080.844 | 7211.033 | 11153.958 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 404555000000 | 291648.208 | 05-MAY-15:00 | 40487.594 | 120867.849 | 31707.676 | 165.701 | 97499.997 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 421910000000 | 294645.407 | 28-JUN-13:09 | 40487.594 | 120867.849 | 32327.721 | 120.875 | 99921.977 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 461938000000 | 311770.907 | 24-JUL-14:00 | 40487.594 | 120867.849 | 32645.54 | 73.935 | 116776.598 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 492309000000 | 308012.958 | 18-AUG-16:00 | 40487.594 | 120867.849 | 33516.928 | 52.229 | 112168.967 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 421349000000 | 311775.319 | 01-SEP-15:00 | 40487.594 | 120867.849 | 33137.416 | 76.52 | 116286.55 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 396063000000 | 278112.831 | 16-OCT-15:00 | 40487.594 | 120867.849 | 30277.908 | 3222.869 | 37077.753 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 432407000000 | 331990.091 | 20-NOV-09:09 | 40487.594 | 120867.849 | 29983.192 | 39732.065 | 0 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 428306000000 | 310327.719 | 11-DEC-07:10 | 40487.594 | 96785.431 | 29976.251 | 72190.999 | 0 | 1622 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 5214700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 396063000000 | 278112.831 |  | 40487.594 | 96785.431 | 29976.251 | 52.229 | 0 | 0 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 492309000000 | 337672.3 |  | 40487.594 | 120867.849 | 33516.928 | 72190.999 | 116776.598 | 1622 | 919.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 105179.88 | 45223.98 | 0 | 150403.86
Cost per Total Building Area ($/m2) | 27.65 | 11.89 | 0 | 39.54
Cost per Net Conditioned Building Area ($/m2) | 27.65 | 11.89 | 0 | 39.54

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11714.04 | 3079.39 | 3079.39
Net Site Energy | 11714.04 | 3079.39 | 3079.39
Total Source Energy | 27925.74 | 7341.14 | 7341.14
Net Source Energy | 27925.74 | 7341.14 | 7341.14
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 441.94 | 5304.98 | 0 | 0 | 0 | 0
Cooling | 1153.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.48 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 947.7 | 0 | 0 | 0 | 0 | 0
Pumps | 32.29 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 967.07 | 0 | 0 | 0 | 0 | 359.75
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 53.61 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6167.08 | 5546.97 | 0 | 0 | 0 | 600.23
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 184481.49 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 373501.29 | 260100.11 | 113401.18 | 0.7 | 3.32
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 314350.02 | 227716.4 | 86633.61 | 0.72 | 3.43
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2188.91 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 154.83 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12028.55 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1723.61 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2228.51 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 948.12 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1272.08 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2073.39 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148610.49 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 436.48 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 585.27 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 852.71 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13913.34 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 914.5 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1212.46 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10079.72 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1905.08 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5140.76 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2263.27 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 592.14 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 68091.06 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1212.46 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1464.18 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2411.09 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1905.08 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 150.4 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3390.5 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1212.46 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3529.64 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31865.1 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33886.15 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27814.25 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1750.13 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2024.98 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2546.19 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4553.49 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1212.46 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9598.74 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7264.22 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 514.24 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10855.21 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1224.71 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 351.76 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2829.1 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1257.36 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4041.56 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7654.25 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2807.42 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 975.71 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 11170.5 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2416.69 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3662.17 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 119.57 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3651.52 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1857.42 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3142.57 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 262.04 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5422.42 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2845.17 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3823.25 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 609.43 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2779.85 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1828.45 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3912.35 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2222.63 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1981.17 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 424.35 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 424.35 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 424.35 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 454.59 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 454.59 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 453.09 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 451.15 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.31 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.04 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.86 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5171.59 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 985.99 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7259.17 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2073.89 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1033.78 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1086.74 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.51 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 174.83 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 208.95 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 667.97 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5420.89 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1875.32 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 367.18 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3671.81 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 196.87 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 955.4 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 448.64 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 503.31 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 788.11 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5269.18 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1305.53 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3611.87 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 956.1 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 18402.34 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2677.23 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 367.18 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9390.89 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3130.91 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 571.17 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 322.83 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 251.8 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2578.49 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12860.33 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9462.39 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 567.75 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5367.87 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2213.41 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1588.3 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2349.8 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1233.52 | 1
AHU-1_HEATC | Coil:Heating:Water | 48201.54 | -
AHU-2_HEATC | Coil:Heating:Water | 77423.52 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.29 | 27416.46 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.15 | 25676.5 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1015.83 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 219383.0677 | 372.9934 | 1043.1459 | 0 | 0.0032 | 240109.6577 | 92551.5465
February | 192880.9594 | 328.8683 | 922.7278 | 0 | 0.0028 | 212393.3963 | 81460.3178
March | 208344.4466 | 356.3914 | 1003.6416 | 0 | 0.0031 | 231019.8448 | 88101.7341
April | 180889.4735 | 307.6836 | 860.9321 | 0 | 0.0026 | 198168.1837 | 76325.2542
May | 185642.6155 | 316.2748 | 886.5895 | 0 | 0.0027 | 204074.7216 | 78379.2219
June | 201628.214 | 347.5505 | 987.1606 | 0 | 0.003 | 227230.1426 | 85514.824
July | 215897.7498 | 373.5354 | 1065.3461 | 0 | 0.0033 | 245229.3203 | 91699.5762
August | 218446.2278 | 378.1501 | 1079.1526 | 0 | 0.0033 | 248407.7113 | 92801.6419
September | 189128.8325 | 323.9562 | 913.6822 | 0 | 0.0028 | 210313.4924 | 80017.6804
October | 187574.0181 | 319.4308 | 895.0074 | 0 | 0.0027 | 206012.1377 | 79181.8127
November | 185580.8648 | 315.7272 | 883.643 | 0 | 0.0027 | 203395.8484 | 78310.8605
December | 210890.0516 | 358.964 | 1005.2222 | 0 | 0.0031 | 231381.0508 | 89007.8132
Annual Sum or Average | 2396290 | 4099.5256 | 11546.251 | 0 | 0.0354 | 2657740 | 1013350
Minimum of Months | 180889.4735 | 307.6836 | 860.9321 | 0 | 0.0026 | 198168.1837 | 76325.2542
Maximum of Months | 219383.0677 | 378.1501 | 1079.1526 | 0 | 0.0033 | 248407.7113 | 92801.6419
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 557156000000 | 332983.496 | 09-JAN-09:09 | 40487.594 | 120867.849 | 30235.727 | 58424.379 | 0 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 492843000000 | 309911.434 | 06-FEB-09:09 | 40487.594 | 120867.849 | 30235.173 | 54067.316 | 0 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 536064000000 | 315012.915 | 20-MAR-08:09 | 40487.594 | 120867.849 | 30232.711 | 43953.135 | 0 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 459834000000 | 348636.461 | 27-APR-14:00 | 40487.594 | 120867.849 | 31506.601 | 862.135 | 53888.38 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 473540000000 | 333101.614 | 30-MAY-15:00 | 40487.594 | 120867.849 | 31239.884 | 466.983 | 139015.401 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 527270000000 | 361974.581 | 08-JUN-12:00 | 40487.594 | 120867.849 | 33223.952 | 123.803 | 166247.48 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 569036000000 | 366052.986 | 13-JUL-14:00 | 40487.594 | 120867.849 | 34684.295 | 41.627 | 168947.719 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 576411000000 | 362230.18 | 04-AUG-15:00 | 40487.594 | 120867.849 | 34315.689 | 51.378 | 165483.767 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 488017000000 | 335859.731 | 06-SEP-12:50 | 40487.594 | 120867.849 | 32527.675 | 303.228 | 140649.482 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 478036000000 | 349892.038 | 26-OCT-15:00 | 40487.594 | 120867.849 | 31327.166 | 2647.84 | 53537.687 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 471965000000 | 309738.846 | 02-NOV-12:09 | 40487.594 | 120867.849 | 30938.262 | 2778.831 | 113642.408 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 536902000000 | 323770.46 | 26-DEC-09:09 | 40487.594 | 120867.849 | 30228.298 | 60817.683 | 0 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6167080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 459834000000 | 309738.846 |  | 40487.594 | 120867.849 | 30228.298 | 41.627 | 0 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 576411000000 | 366052.986 |  | 40487.594 | 120867.849 | 34684.295 | 60817.683 | 168947.719 | 0 | 1023.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 166448.05 | 50047.81 | 0 | 216495.85
Cost per Total Building Area ($/m2) | 43.76 | 13.16 | 0 | 56.91
Cost per Net Conditioned Building Area ($/m2) | 43.76 | 13.16 | 0 | 56.91

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11690.17 | 3073.12 | 3073.12
Net Site Energy | 11690.17 | 3073.12 | 3073.12
Total Source Energy | 27555.65 | 7243.85 | 7243.85
Net Source Energy | 27555.65 | 7243.85 | 7243.85
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 331.8 | 4804.14 | 0 | 0 | 0 | 0
Cooling | 813.53 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1067.99 | 0 | 0 | 0 | 0 | 0
Pumps | 29.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1776.22 | 0 | 0 | 0 | 0 | 660.75
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 53.45 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6644.2 | 5045.97 | 0 | 0 | 0 | 901.23
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 169299.87 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 304108.73 | 242878.03 | 61230.69 | 0.8 | 3.73
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 272445.2 | 217589.8 | 54855.41 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 1925.85 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 119.95 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 11232.11 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1667.54 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2154.64 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 886.91 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1174.05 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1941.88 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148390.74 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 391.21 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 470.93 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 792.32 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 12945.67 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 767.46 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1018.4 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9356.98 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1592.99 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4971.29 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1901.02 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 484.71 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67917.57 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1018.4 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1344.52 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2331.12 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1592.99 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 116.1 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3275.56 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1018.4 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3255.78 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29874.51 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32438.88 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26637.23 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1702.37 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1693.91 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2138.65 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 3824.68 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1018.4 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8062.4 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6710.34 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 421.45 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9675.65 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1018.67 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 282.72 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2376.28 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1056.12 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3394.68 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 6777.29 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2318.77 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 779.67 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 10496.13 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2019.76 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3410.03 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 91.27 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3406.45 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1548.79 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 2782.12 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 258.23 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4935.73 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2696.92 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3610.72 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 529.8 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2441.45 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1623.82 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3730.81 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1987.97 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1889.41 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 360.23 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 360.23 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 360.23 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 392.12 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 392.12 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 390.68 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 410.3 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.63 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.84 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 955.86 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4471.52 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 908.41 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 6761.17 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1886.33 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1064.3 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1121.45 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 82.91 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 173.88 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 207.9 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 516.28 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5142.58 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1803.71 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 308.29 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3199.18 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 172.93 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 884.41 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 415.01 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 462.27 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 769 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4974.42 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1096.14 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3213.8 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 772.42 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 16851.56 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2142.05 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 308.29 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 8341.4 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3031.6 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 479.56 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 283.59 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 221.83 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2500.71 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11782.96 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 8535.95 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 498.27 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 4425.65 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2096.67 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1392.29 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2226.21 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1076.74 | 1
AHU-1_HEATC | Coil:Heating:Water | 39033.05 | -
AHU-2_HEATC | Coil:Heating:Water | 62341.92 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.37 | 30925.38 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.46 | 27705.46 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 932.24 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 185317.271 | 304.2736 | 737.2151 | 0 | 0.0029 | 766458.2206 | 77484.6076
February | 164135.0351 | 269.8206 | 654.7151 | 0 | 0.0026 | 680688.0295 | 68659.9158
March | 182278.2978 | 300.6869 | 732.7192 | 0 | 0.0029 | 761794.1242 | 76351.57
April | 168947.904 | 278.2857 | 676.9076 | 0 | 0.0027 | 703764.9729 | 70727.4741
May | 161064.5837 | 263.9573 | 638.052 | 0 | 0.0025 | 663357.9976 | 67295.485
June | 150033.7609 | 245.8262 | 594.0645 | 0 | 0.0024 | 617625.4972 | 62681.3799
July | 159850.7016 | 263.2671 | 640.2747 | 0 | 0.0025 | 665678.3022 | 66915.7329
August | 159160.7901 | 261.9441 | 636.5005 | 0 | 0.0025 | 661752.9996 | 66608.6079
September | 157547.9017 | 259.0026 | 628.4971 | 0 | 0.0025 | 653430.0055 | 65905.4663
October | 171946.3347 | 283.0736 | 688.1039 | 0 | 0.0027 | 715404.4093 | 71967.9111
November | 171366.1843 | 282.0339 | 685.3241 | 0 | 0.0027 | 712513.7099 | 71716.7875
December | 187972.3776 | 308.7464 | 748.3908 | 0 | 0.003 | 778078.0296 | 78605.8725
Annual Sum or Average | 2019620 | 3320.918 | 8060.7646 | 0 | 0.0319 | 8380550 | 844920.8107
Minimum of Months | 150033.7609 | 245.8262 | 594.0645 | 0 | 0.0024 | 617625.4972 | 62681.3799
Maximum of Months | 187972.3776 | 308.7464 | 748.3908 | 0 | 0.003 | 778078.0296 | 78605.8725
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 607657000000 | 349340.836 | 27-JAN-10:50 | 40487.594 | 120867.849 | 34539.19 | 8423 | 44082.897 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 539658000000 | 336664.013 | 16-FEB-09:09 | 40487.594 | 120867.849 | 34026.072 | 43004.924 | 0 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 603960000000 | 351059.121 | 30-MAR-13:00 | 40487.594 | 120867.849 | 36391.531 | 654.863 | 69209.96 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 557953000000 | 347260.761 | 06-APR-13:09 | 40487.594 | 120867.849 | 35105.4 | 2026.483 | 47833.129 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 525918000000 | 352584.86 | 15-MAY-09:30 | 40487.594 | 120867.849 | 34046.358 | 10134.048 | 46108.705 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 489661000000 | 360264.728 | 15-JUN-16:00 | 40487.594 | 120867.849 | 38729.598 | 12.143 | 84266.711 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 527758000000 | 349172.268 | 17-JUL-13:00 | 40487.594 | 120867.849 | 38355.348 | 50.364 | 114835.561 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 524646000000 | 347881.194 | 29-AUG-15:00 | 40487.594 | 120867.849 | 40466.876 | 7.264 | 116109.763 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 518047000000 | 363155.946 | 06-SEP-12:00 | 40487.594 | 120867.849 | 37038.905 | 291.388 | 94995.465 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 567181000000 | 353799.472 | 16-OCT-08:00 | 40487.594 | 120867.849 | 34090.096 | 13627.194 | 43786.434 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 564889000000 | 350401.736 | 10-NOV-10:39 | 40487.594 | 120867.849 | 34559.889 | 8857.463 | 44688.636 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 616870000000 | 342119.036 | 11-DEC-07:10 | 40487.594 | 96785.431 | 33918.55 | 81274.602 | 0 | 1622 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6644200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 489661000000 | 336664.013 |  | 40487.594 | 96785.431 | 33918.55 | 7.264 | 0 | 0 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 616870000000 | 363155.946 |  | 40487.594 | 120867.849 | 40466.876 | 81274.602 | 116109.763 | 1622 | 940.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 68346.85 | 36577.14 | 0 | 104923.99
Cost per Total Building Area ($/m2) | 17.97 | 9.62 | 0 | 27.58
Cost per Net Conditioned Building Area ($/m2) | 17.97 | 9.62 | 0 | 27.58

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12117 | 3185.32 | 3185.32
Net Site Energy | 12117 | 3185.32 | 3185.32
Total Source Energy | 27898.67 | 7334.02 | 7334.02
Net Source Energy | 27898.67 | 7334.02 | 7334.02
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 521.68 | 5617.34 | 0 | 0 | 0 | 0
Cooling | 1051.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.46 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 952.81 | 0 | 0 | 0 | 0 | 0
Pumps | 33.44 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1070.17 | 0 | 0 | 0 | 0 | 398.1
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 56.74 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6254.55 | 5862.45 | 0 | 0 | 0 | 638.58
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 191111.53 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 366419.44 | 257600.43 | 108819.01 | 0.7 | 3.34
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 302803.33 | 222431.86 | 80371.47 | 0.73 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2262.52 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 147.17 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12348.93 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1715.46 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2217.72 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 929.84 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1389.57 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2066.92 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148548.34 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 427.86 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 565.58 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 836.2 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13772.62 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 884.61 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1203.13 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9999.97 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1842.78 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5115.73 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2245.85 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 572.45 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 68063.89 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1203.13 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1616.96 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2399.49 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1842.78 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 142.95 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3373.77 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1203.13 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3491.28 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31922.72 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33904.99 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27767.05 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1743.2 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1958.72 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2526.58 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4518.43 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1203.13 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9524.83 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7328.56 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 497.15 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11092.33 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1221.87 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 339.91 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2807.32 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1247.68 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4010.44 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7630.33 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2841.77 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 929.28 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 12265.19 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2433.38 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3995.54 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 113.62 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3960.76 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1802.9 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3252.28 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 261.84 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5397.73 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2897.12 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3909.29 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 644.79 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2793.71 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1812.56 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3895.72 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2203.82 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1972.44 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 427.61 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 427.61 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 427.61 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 453.21 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 453.21 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 451.66 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 495.15 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.31 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.04 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.87 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5198.38 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 985.1 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7286.91 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2115.87 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1032.69 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1085.61 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.51 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 174.75 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 208.86 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 673.41 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5394.61 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1877.32 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 364.35 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3643.48 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 196.62 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 987.56 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 448.35 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 553.75 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 777.07 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5179.41 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1295.46 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3624.15 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 951.57 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 17924.09 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2669.77 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 364.35 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9506.01 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3076.88 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 566.77 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 319.23 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 248.98 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2536.06 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12663.83 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9303.53 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 564.61 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5385.94 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2422.4 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1506.47 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2573.89 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1215.85 | 1
AHU-1_HEATC | Coil:Heating:Water | 54881.53 | -
AHU-2_HEATC | Coil:Heating:Water | 86409.65 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.38 | 27569.3 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.1 | 25590.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1052.34 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 166856.3278 | 271.382 | 391.2663 | 0 | 0.0029 | 257075.0358 | 69212.5482
February | 143391.3307 | 235.9054 | 344.9947 | 0 | 0.0026 | 226685.6455 | 59736.1142
March | 143737.3056 | 238.4355 | 352.2121 | 0 | 0.0026 | 231437.0084 | 60067.6828
April | 129550.1101 | 214.6479 | 316.6227 | 0 | 0.0024 | 208050.2169 | 54114.6403
May | 129416.2928 | 214.5934 | 316.8402 | 0 | 0.0024 | 208193.888 | 54074.7288
June | 134561.1657 | 225.9487 | 338.6322 | 0 | 0.0025 | 222526.0061 | 56494.3995
July | 142117.4504 | 239.6605 | 360.9811 | 0 | 0.0027 | 237216.6652 | 59764.6859
August | 146334.9121 | 247.3668 | 373.6284 | 0 | 0.0028 | 245530.3459 | 61595.0552
September | 122088.4353 | 201.7916 | 296.78 | 0 | 0.0022 | 195009.494 | 50950.6559
October | 128127.9441 | 211.3706 | 310.1481 | 0 | 0.0023 | 203791.65 | 53432.5526
November | 132682.8885 | 219.1212 | 321.9436 | 0 | 0.0024 | 211543.2965 | 55354.6745
December | 157565.9952 | 258.8885 | 378.0018 | 0 | 0.0028 | 248372.0705 | 65609.0153
Annual Sum or Average | 1676430 | 2779.1122 | 4102.051 | 0 | 0.0305 | 2695430 | 700406.7533
Minimum of Months | 122088.4353 | 201.7916 | 296.78 | 0 | 0.0022 | 195009.494 | 50950.6559
Maximum of Months | 166856.3278 | 271.382 | 391.2663 | 0 | 0.0029 | 257075.0358 | 69212.5482
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 596523000000 | 351215.843 | 09-JAN-07:10 | 40487.594 | 96785.431 | 30401.298 | 99254.768 | 0 | 1622 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 526007000000 | 331205.553 | 07-FEB-08:09 | 40487.594 | 108826.64 | 30440.817 | 70428.378 | 0 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 537032000000 | 325768.679 | 06-MAR-07:10 | 40487.594 | 96785.431 | 30401.298 | 83357.652 | 0 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 482765000000 | 331798.045 | 13-APR-15:00 | 40487.594 | 120867.849 | 31326.372 | 2274.047 | 35781.772 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 483098000000 | 329222.441 | 31-MAY-12:09 | 40487.594 | 120867.849 | 32161.493 | 425.029 | 134220.066 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 516355000000 | 356772.337 | 29-JUN-16:10 | 40487.594 | 120867.849 | 35219.574 | 28.153 | 159108.757 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 550443000000 | 354577.45 | 13-JUL-16:00 | 40487.594 | 120867.849 | 33770.578 | 64.2 | 158326.819 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 569735000000 | 355442.708 | 25-AUG-16:00 | 40487.594 | 120867.849 | 34665.603 | 43.318 | 158317.935 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 452505000000 | 331786.065 | 14-SEP-14:00 | 40487.594 | 120867.849 | 33697.592 | 233.003 | 135439.617 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 472883000000 | 323050.567 | 25-OCT-12:09 | 40487.594 | 120867.849 | 31007.267 | 9582.523 | 29582.46 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 490870000000 | 337110.116 | 01-NOV-14:00 | 40487.594 | 120867.849 | 31037.659 | 5562.144 | 38094.46 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 576329000000 | 331046.386 | 30-DEC-07:10 | 13495.865 | 67434.081 | 30401.298 | 129507.901 | 0 | 1622 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6254550000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 452505000000 | 323050.567 |  | 13495.865 | 67434.081 | 30401.298 | 28.153 | 0 | 0 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 596523000000 | 356772.337 |  | 40487.594 | 120867.849 | 35219.574 | 129507.901 | 159108.757 | 1622 | 1060.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 92531.37 | 46917.29 | 0 | 139448.66
Cost per Total Building Area ($/m2) | 24.32 | 12.33 | 0 | 36.66
Cost per Net Conditioned Building Area ($/m2) | 24.32 | 12.33 | 0 | 36.66

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11900.41 | 3128.39 | 3128.39
Net Site Energy | 11900.41 | 3128.39 | 3128.39
Total Source Energy | 28404.01 | 7466.86 | 7466.86
Net Source Energy | 28404.01 | 7466.86 | 7466.86
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 472.92 | 5191.32 | 0 | 0 | 0 | 0
Cooling | 578.64 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.46 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1022.15 | 0 | 0 | 0 | 0 | 0
Pumps | 31.76 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1732.94 | 0 | 0 | 0 | 0 | 644.65
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 57.31 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6463.41 | 5437.01 | 0 | 0 | 0 | 885.13
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 181414.8 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 295020.96 | 234184.31 | 60836.65 | 0.79 | 3.71
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 264318.99 | 211099.75 | 53219.24 | 0.8 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2130.98 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 112.98 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 11952.95 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1651.7 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2133.81 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 864.17 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1368.9 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1950.81 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148360.64 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 381.38 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 450.08 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 772.1 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 12900.03 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 736.45 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1075.43 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9349.72 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1528.86 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4923.33 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2007.48 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 464.11 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67853.66 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1075.43 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1601.84 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2307.9 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1528.86 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 109.38 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3242.95 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1075.43 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3168.88 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30752.93 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32655.17 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27388.53 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1688.98 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1625.68 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2258.41 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4038.85 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1075.43 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8513.88 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6911.68 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 403.6 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10442.76 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1128.52 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 270.2 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2509.35 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1115.26 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3584.78 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7032.83 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2402.69 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 730.65 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 12281.35 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2347.4 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3974.08 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 86.05 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3922.11 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1591.15 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3100.97 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 258.83 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5106.78 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2842.24 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3835.06 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 617.8 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2541.98 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1658.06 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3757.99 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2027.14 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1903.14 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 377.28 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 377.28 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 377.28 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 399.28 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 399.28 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 397.61 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 485.71 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.36 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.14 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.99 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4679.03 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 916.81 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7007 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2114.27 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1062.03 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1119.01 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 82.84 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 173.27 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 207.07 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 557.3 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5173.3 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1813.63 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 325.59 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3255.96 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 178.1 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 983.44 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 408.93 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 548.6 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 767.24 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4984.03 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1157.67 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3325.76 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 829.66 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 16897.65 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2329.38 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 325.59 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9050.01 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3023.8 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 506.48 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 310.57 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 242.86 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2494.38 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12062.54 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 8808.15 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 549.94 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 4685.1 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2432.31 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1418.34 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2588.01 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1148.58 | 1
AHU-1_HEATC | Coil:Heating:Water | 46290.1 | -
AHU-2_HEATC | Coil:Heating:Water | 79679.56 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.59 | 29604.11 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.97 | 27053.63 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 998.95 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 172686.0985 | 280.8285 | 449.5223 | 0 | 0.0032 | 10660600 | 71760.9903
February | 148262.0805 | 241.1546 | 386.1077 | 0 | 0.0027 | 9156670 | 61615.793
March | 166319.1751 | 274.5617 | 447.7306 | 0 | 0.0032 | 10618800 | 69510.2728
April | 149685.882 | 246.3859 | 400.3593 | 0 | 0.0028 | 9495140 | 62489.3224
May | 142019.7915 | 232.4243 | 374.9978 | 0 | 0.0026 | 8893430 | 59159.1351
June | 137662.3292 | 226.0332 | 366.169 | 0 | 0.0026 | 8684170 | 57415.5588
July | 139584.5366 | 229.3625 | 371.9081 | 0 | 0.0026 | 8820310 | 58234.0003
August | 136507.5527 | 223.7611 | 361.7376 | 0 | 0.0026 | 8579010 | 56897.5852
September | 135916.64 | 222.5391 | 359.2552 | 0 | 0.0025 | 8520100 | 56626.7894
October | 154690.9848 | 254.7742 | 414.2879 | 0 | 0.0029 | 9825500 | 64593.2789
November | 155277.9609 | 255.6912 | 415.6802 | 0 | 0.0029 | 9858520 | 64833.5756
December | 170665.1117 | 278.4676 | 447.6095 | 0 | 0.0032 | 10615300 | 71010.6422
Annual Sum or Average | 1809280 | 2965.9838 | 4795.3652 | 0 | 0.0338 | 113728000 | 754146.944
Minimum of Months | 135916.64 | 222.5391 | 359.2552 | 0 | 0.0025 | 8520100 | 56626.7894
Maximum of Months | 172686.0985 | 280.8285 | 449.5223 | 0 | 0.0032 | 10660600 | 71760.9903
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 605865000000 | 356687.968 | 17-JAN-09:09 | 40487.594 | 120867.849 | 32580.749 | 78174.924 | 0 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 520395000000 | 355286.1 | 27-FEB-07:10 | 40487.594 | 96785.431 | 32579.585 | 93046.918 | 0 | 1622 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 603489000000 | 345779.705 | 27-MAR-13:20 | 40487.594 | 120867.849 | 33234.23 | 5059.815 | 45123.202 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 539631000000 | 345579.717 | 06-APR-13:09 | 40487.594 | 120867.849 | 33440.761 | 3666.364 | 46110.133 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 505435000000 | 344107.665 | 02-MAY-12:00 | 40487.594 | 120867.849 | 33491.549 | 2633.198 | 45620.459 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 493542000000 | 345313.169 | 07-JUN-15:00 | 40487.594 | 120867.849 | 34103.117 | 1045.588 | 47802.005 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 501279000000 | 332786.053 | 21-JUL-16:00 | 40487.594 | 120867.849 | 39390.244 | 1.336 | 118666.594 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 487566000000 | 324987.281 | 18-AUG-16:00 | 40487.594 | 120867.849 | 37785.764 | 38.894 | 100178.559 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 484217000000 | 339428.914 | 15-SEP-16:00 | 40487.594 | 120867.849 | 34224.547 | 1635.115 | 41206.793 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 558407000000 | 347148.557 | 19-OCT-13:09 | 40487.594 | 120867.849 | 33602.207 | 5486.308 | 45697.584 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 560283000000 | 334181 | 21-NOV-10:00 | 40487.594 | 120867.849 | 32729.403 | 11651.72 | 27437.418 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 603295000000 | 371341.97 | 11-DEC-07:10 | 40487.594 | 96785.431 | 32579.327 | 106779.339 | 0 | 1622 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6463410000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 484217000000 | 324987.281 |  | 40487.594 | 96785.431 | 32579.327 | 1.336 | 0 | 0 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 605865000000 | 371341.97 |  | 40487.594 | 120867.849 | 39390.244 | 106779.339 | 118666.594 | 1622 | 1007.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 125670.39 | 48261.43 | 0 | 173931.82
Cost per Total Building Area ($/m2) | 33.04 | 12.69 | 0 | 45.72
Cost per Net Conditioned Building Area ($/m2) | 33.04 | 12.69 | 0 | 45.72

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12043.03 | 3165.88 | 3165.88
Net Site Energy | 12043.03 | 3165.88 | 3165.88
Total Source Energy | 27390.15 | 7200.34 | 7200.34
Net Source Energy | 27390.15 | 7200.34 | 7200.34
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 583.66 | 5720.62 | 0 | 0 | 0 | 0
Cooling | 563.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.44 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 948.32 | 0 | 0 | 0 | 0 | 0
Pumps | 33.57 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1318.29 | 0 | 0 | 0 | 0 | 490.4
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 61.89 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6072.14 | 5970.89 | 0 | 0 | 0 | 730.88
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.487 | 0.409 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 3.241 | 0.487 | 0.409 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 3.241 | 0.487 | 0.409 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.487 | 0.409 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.487 | 0.409 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.487 | 0.409 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 3.241 | 0.487 | 0.409 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 3.241 | 0.487 | 0.409 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.487 | 0.409 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.487 | 0.409 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.487 | 0.409 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 3.241 | 0.487 | 0.409 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 3.241 | 0.487 | 0.409 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 3.241 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.487 | 0.409 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.487 | 0.409 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.487 | 0.409 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.487 | 0.409 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 3.241 | 0.487 | 0.409 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.487 | 0.409 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.487 | 0.409 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.487 | 0.409 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 3.241 | 0.487 | 0.409 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 3.241 | 0.487 | 0.409 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 3.241 | 0.487 | 0.409 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 3.241 | 0.487 | 0.409 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 3.241 | 0.487 | 0.409 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 3.241 | 0.487 | 0.409 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 97.22 | 3.24 | 0.487 | 0.409
Non-North Total or Average |  |  | 211.08 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 191834.79 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 332997 | 242621.15 | 90375.85 | 0.73 | 3.44
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 269159.42 | 207424.64 | 61734.78 | 0.77 | 3.62
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2329.47 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 109.95 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12839.42 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1621.06 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2094.42 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 823.17 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1397.06 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1854.17 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148443.1 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 363.39 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 414.74 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 735.54 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13931.75 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 676.69 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1178 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9289.19 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1405.19 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4834.46 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2198.95 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 427.3 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67731.91 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1178 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1565.87 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2256.09 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1405.19 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 106.02 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3179.9 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1178 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3016.52 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31298.61 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33723.61 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27198.99 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1663.43 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1493.99 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2473.82 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4424.07 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1178 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9325.92 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7105.21 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 371.55 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11042 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1115.97 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 248.96 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2748.69 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1221.63 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3926.69 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 7236.48 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2458.75 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 777.49 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 12476.48 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2375.44 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 4104.94 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 82.46 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3999.65 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1640.96 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3405.65 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 261.24 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5551.93 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2974.79 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4064.61 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 723.64 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2856.34 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1727.08 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3807.83 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2115.52 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1928.24 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 411.19 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 411.19 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 411.19 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 429.27 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 429.27 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 427.95 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 469.43 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.32 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.06 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 954.89 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5342.92 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 956.28 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7498.21 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1876.25 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1029.95 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1082.67 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.34 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 174.45 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 208.5 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 689.94 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5241.34 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1845.73 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 356.72 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3567.23 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 183.93 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1000.38 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 422.13 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 534.74 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 771.66 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5052.96 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1268.35 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3669.86 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 863.64 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 17272.79 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2389 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 356.72 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10271.9 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3047.4 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 554.91 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 312.91 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 244.68 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2512.73 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12961.09 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9294.76 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 554.44 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5445.71 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2352.65 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1272.69 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2476.8 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1025.04 | 1
AHU-1_HEATC | Coil:Heating:Water | 59246.28 | -
AHU-2_HEATC | Coil:Heating:Water | 89507.25 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.28 | 27410.48 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.02 | 25449.72 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1056.32 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 167246.9575 | 272.6972 | 394.3961 | 0 | 0.0029 | 259134.5738 | 69439.5683
February | 146493.9677 | 239.5641 | 347.7521 | 0 | 0.0026 | 228490.8285 | 60890.4677
March | 151754.7884 | 251.5462 | 371.2429 | 0 | 0.0028 | 243941.2145 | 63400.1235
April | 131623.6213 | 218.8492 | 324.1837 | 0 | 0.0024 | 213021.9688 | 55053.9645
May | 127683.41 | 211.5996 | 312.2055 | 0 | 0.0023 | 205147.8929 | 53339.1543
June | 119944.2613 | 198.7343 | 293.1524 | 0 | 0.0022 | 192628.1167 | 50102.3558
July | 130973.311 | 219.0198 | 326.6582 | 0 | 0.0024 | 214653.5465 | 54901.6182
August | 127028.1242 | 211.4216 | 313.5596 | 0 | 0.0023 | 206041.7975 | 53152.1997
September | 111448.1712 | 182.5394 | 265.4914 | 0 | 0.002 | 174442.685 | 46350.9858
October | 130334.88 | 216.032 | 318.8137 | 0 | 0.0024 | 209490.2708 | 54450.4619
November | 137853.7262 | 227.7326 | 334.7242 | 0 | 0.0025 | 219941.5471 | 57518.7941
December | 159710.6176 | 261.5421 | 380.3135 | 0 | 0.0028 | 249887.0177 | 66418.8444
Annual Sum or Average | 1642100 | 2711.2779 | 3982.4932 | 0 | 0.0297 | 2616820 | 685018.5381
Minimum of Months | 111448.1712 | 182.5394 | 265.4914 | 0 | 0.002 | 174442.685 | 46350.9858
Maximum of Months | 167246.9575 | 272.6972 | 394.3961 | 0 | 0.0029 | 259134.5738 | 69439.5683
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 601302000000 | 365890.992 | 09-JAN-07:10 | 40487.594 | 96785.431 | 30292.681 | 111267.933 | 0 | 1622 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 530196000000 | 350981.851 | 02-FEB-07:10 | 40487.594 | 96785.431 | 30322.564 | 95651.934 | 0 | 1622 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 566047000000 | 326164.741 | 27-MAR-06:10 | 40487.594 | 96785.431 | 30292.784 | 78341.489 | 0 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 494301000000 | 314182.42 | 25-APR-08:00 | 40487.594 | 120867.849 | 30369.681 | 21392.903 | 0 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 476030000000 | 349946.117 | 30-MAY-10:30 | 40487.594 | 120867.849 | 30407.354 | 10571.593 | 46547.333 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 446979000000 | 322972.788 | 14-JUN-15:00 | 40487.594 | 120867.849 | 33688.781 | 224.66 | 126639.51 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 498087000000 | 334336.137 | 06-JUL-16:00 | 40487.594 | 120867.849 | 35202.309 | 53.999 | 136659.993 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 478104000000 | 328165.489 | 11-AUG-15:30 | 40487.594 | 120867.849 | 34290.089 | 227.577 | 131227.987 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 404781000000 | 328734.843 | 27-SEP-14:00 | 40487.594 | 120867.849 | 32203.997 | 3160.287 | 30950.723 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 486106000000 | 326874.102 | 25-OCT-14:00 | 40487.594 | 120867.849 | 31363.953 | 5968.374 | 27121.939 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 510358000000 | 326008.017 | 24-NOV-07:10 | 40487.594 | 96785.431 | 30294.343 | 78590.568 | 0 | 1622 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 579844000000 | 334466.445 | 21-DEC-08:09 | 40487.594 | 108826.64 | 30374.191 | 72818.975 | 0 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6072140000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 404781000000 | 314182.42 |  | 40487.594 | 96785.431 | 30292.681 | 53.999 | 0 | 0 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 601302000000 | 365890.992 |  | 40487.594 | 120867.849 | 35202.309 | 111267.933 | 136659.993 | 1622 | 1064.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 90198.79 | 47790.49 | 0 | 137989.28
Cost per Total Building Area ($/m2) | 23.71 | 12.56 | 0 | 36.27
Cost per Net Conditioned Building Area ($/m2) | 23.71 | 12.56 | 0 | 36.27

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13996.91 | 3679.52 | 3679.52
Net Site Energy | 13996.91 | 3679.52 | 3679.52
Total Source Energy | 31561.49 | 8296.91 | 8296.91
Net Source Energy | 31561.49 | 8296.91 | 8296.91
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 846.64 | 7177.15 | 0 | 0 | 0 | 0
Cooling | 356.8 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 613.78 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 25.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 955.27 | 0 | 0 | 0 | 0 | 0
Pumps | 38.25 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1741.46 | 0 | 0 | 0 | 0 | 647.82
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 68.13 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6563.25 | 7433.65 | 0 | 0 | 0 | 888.3
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 32.29 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 9.69 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 11.84 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 9.69 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 9.69 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 13.99 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 4.31 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 4.31 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 9.69 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 23.68 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 23.68 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 8.61 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 7.53 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 23.68 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 13.99 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 8.61 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 11.84 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 12.92 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 8.61 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 10.76 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 9.69 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 10.76 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 10.76 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 9.69 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 10.76 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 13.99 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 16.15 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 16.15 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 10.76 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 11.84 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 13.99 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 10.76 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 9.69 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 11.84 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 4.31 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 10.76 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 11.84 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 9.69 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 8.61 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 9.69 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 9.69 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 11.84 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 10.76 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 9.69 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 9.69 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 16.15 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 11.84 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 11.84 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 9.69 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 11.84 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 10.76 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 10.76 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 10.76 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 10.76 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 11.826 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 2.615 | 0.702 | 0.633 | No | 5F762C | 180 | S
4A8120 | WINDOW-90.1-2004-NONRES-FIXED | 2.32 | 2.32 | 2.615 | 0.702 | 0.633 | No | 84FB73 | 0 | N
AAE778 | WINDOW-90.1-2004-NONRES-FIXED | 8.92 | 8.92 | 2.615 | 0.702 | 0.633 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | F629C1 | 0 | N
8128A9 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | F629C1 | 0 | N
9B1541 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 879583 | 180 | S
CF850A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 879583 | 180 | S
A6BA23 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | E326E4 | 90 | E
D10D28 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | E326E4 | 90 | E
38B811 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 1D96D7 | 90 | E
591336 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 1D96D7 | 90 | E
18748E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 6D2616 | 0 | N
1D94BE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 6D2616 | 0 | N
137A56 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 2.615 | 0.702 | 0.633 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 28B002 | 180 | S
44E54A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 28B002 | 180 | S
8D508E | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 28B002 | 180 | S
B2D381 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 28B002 | 180 | S
757D10 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 2.615 | 0.702 | 0.633 | No | EA6DC8 | 180 | S
24167A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 997723 | 180 | S
2C0938 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 997723 | 180 | S
E33BAE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | B40F89 | 270 | W
8600DD | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | CEC7BD | 180 | S
88E1FC | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 859BC1 | 0 | N
E8D997 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 859BC1 | 0 | N
F83F33 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | 61E610 | 90 | E
B1F5EE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | D95F04 | 90 | E
F52F3D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 208CCF | 90 | E
80885D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 2.615 | 0.702 | 0.633 | No | AEF992 | 180 | S
2BE8DE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 1775A6 | 270 | W
513E2A | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 54D065 | 180 | S
1AD478 | WINDOW-90.1-2004-NONRES-FIXED | 3.72 | 3.72 | 2.615 | 0.702 | 0.633 | No | 97F00A | 180 | S
27F0AC | WINDOW-90.1-2004-NONRES-FIXED | 5.95 | 5.95 | 2.615 | 0.702 | 0.633 | No | A497E9 | 180 | S
724114 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 88A75F | 180 | S
5635BC | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | B4E619 | 90 | E
D538C4 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | B4E619 | 90 | E
831C1D | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 2.615 | 0.702 | 0.633 | No | 9EC269 | 0 | N
9BB95F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | B316F7 | 0 | N
C0778D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | B316F7 | 0 | N
2EF63B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 9621FD | 0 | N
7D2D69 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 9621FD | 0 | N
C417C0 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 4B1439 | 90 | E
D23C8B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 4B1439 | 90 | E
EB042B | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 4B1439 | 90 | E
E55A57 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 2.615 | 0.702 | 0.633 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 2.615 | 0.702 | 0.633 | No | 4ABC66 | 180 | S
93D018 | WINDOW-90.1-2004-NONRES-FIXED | 6.69 | 6.69 | 2.615 | 0.702 | 0.633 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | 4B55FA | 90 | E
15B02B | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 9C3A6A | 0 | N
820282 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 68A2D7 | 0 | N
A2790A | WINDOW-90.1-2004-NONRES-FIXED | 4.18 | 4.18 | 2.615 | 0.702 | 0.633 | No | CE3FEF | 0 | N
79FCEE | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | CE618F | 90 | E
EDE617 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | CE618F | 90 | E
29FA28 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 5ADC59 | 0 | N
944FCE | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 5ADC59 | 0 | N
C41399 | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-90.1-2004-NONRES-FIXED | 2.79 | 2.79 | 2.615 | 0.702 | 0.633 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | C1BC97 | 180 | S
3DB407 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | C1BC97 | 180 | S
5031C8 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | C1BC97 | 180 | S
95BA33 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 2.615 | 0.702 | 0.633 | No | D22917 | 90 | E
F27282 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 2.615 | 0.702 | 0.633 | No | D22917 | 90 | E
9DF7DE | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 2.615 | 0.702 | 0.633 | No | 38B339 | 270 | W
D0BE44 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 2.615 | 0.702 | 0.633 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-90.1-2004-NONRES-FIXED | 3.34 | 3.34 | 2.615 | 0.702 | 0.633 | No | 38B339 | 270 | W
B0FB49 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 2.615 | 0.702 | 0.633 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | 8DA7DB | 180 | S
44F571 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 2.615 | 0.702 | 0.633 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 2.615 | 0.702 | 0.633 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-90.1-2004-NONRES-FIXED | 4.46 | 4.46 | 2.615 | 0.702 | 0.633 | No | BE5F2F | 270 | W
3833A2 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | C86329 | 90 | E
6BD844 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | C86329 | 90 | E
86D536 | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | C86329 | 90 | E
BAF71D | WINDOW-90.1-2004-NONRES-FIXED | 2.23 | 2.23 | 2.615 | 0.702 | 0.633 | No | C86329 | 90 | E
142781 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | 88E360 | 0 | N
9BC521 | WINDOW-90.1-2004-NONRES-FIXED | 5.71 | 5.71 | 2.615 | 0.702 | 0.633 | No | 88E360 | 0 | N
2111A1 | WINDOW-90.1-2004-NONRES-FIXED | 0.74 | 0.74 | 2.615 | 0.702 | 0.633 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | 2E2D0C | 0 | N
E74902 | WINDOW-90.1-2004-NONRES-FIXED | 5.57 | 5.57 | 2.615 | 0.702 | 0.633 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-90.1-2004-NONRES-FIXED | 1.11 | 1.11 | 2.615 | 0.702 | 0.633 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 97.22 | 2.61 | 0.702 | 0.633
Non-North Total or Average |  |  | 211.08 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 218794.07 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 297515.85 | 227197.15 | 70318.7 | 0.76 | 3.58
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 268446.17 | 214395.95 | 54050.22 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 3662.17 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 113.86 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 17547.25 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1498.8 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 1940.43 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 698.57 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1620.02 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1772.37 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148195.25 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 308.05 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 296.85 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 624.04 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 15238.82 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 487.99 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1219.97 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8866.98 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1008.52 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4543.77 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2277.29 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 304.4 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 67350.01 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1219.97 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1913.41 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2073.74 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1008.52 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 109.8 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 2929.36 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1219.97 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 2571.02 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 35850.52 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36243.64 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 25690.71 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1578.41 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1073.58 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2561.96 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4581.7 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1219.97 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9658.2 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 8356.06 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 264.6 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 15942.02 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1332.07 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 178.19 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2846.62 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1265.15 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4066.6 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 9547.11 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3154 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 805.19 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 14015.09 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3022.57 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 4362.85 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 85.4 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 4433.76 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1768 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5225.74 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 262.99 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6844.4 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3900.91 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5535.68 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1311.3 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3619.86 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1803.88 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3881.29 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2218.16 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1964.04 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 437.28 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 437.28 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 437.28 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 433.87 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 433.87 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 432.42 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 581.73 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.56 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 799.69 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 955.69 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 6994.34 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1005.87 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 9839.27 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2141.81 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1037.76 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1090.93 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 83.94 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 176.23 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 210.74 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 1026.62 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5326.84 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1874.07 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.46 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 3694.6 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 196.2 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1024.46 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 450.68 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 646.2 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 701.97 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4693.24 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1313.63 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 4528.17 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 936.62 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 15270.55 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2584.71 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.46 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 16110.19 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2719.03 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 574.72 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 314.69 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 246.07 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2246.44 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 15390.21 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11495.41 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 558.12 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 7308.68 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2561.11 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1456.89 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2721.33 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1163.78 | 1
AHU-1_HEATC | Coil:Heating:Water | 85302.49 | -
AHU-2_HEATC | Coil:Heating:Water | 116095.66 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.26 | 27374.07 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.22 | 27298.79 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1204.77 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 180396.1512 | 209.0914 | 948.9727 | 0 | 0.0033 | 190415.056 | 69411.6451
February | 159995.2226 | 185.6273 | 845.46 | 0 | 0.0029 | 169645.5794 | 61589.907
March | 154568.7437 | 181.017 | 852.0485 | 0 | 0.003 | 170974.4796 | 59760.3754
April | 134854.8446 | 159.9381 | 785.3905 | 0 | 0.0027 | 157606.5827 | 52447.4917
May | 132860.2752 | 158.2341 | 787.6164 | 0 | 0.0027 | 158055.7 | 51773.5842
June | 112909.4326 | 133.5439 | 649.9058 | 0 | 0.0022 | 130417.1092 | 43856.0672
July | 111957.8553 | 132.0053 | 635.7852 | 0 | 0.0022 | 127581.9703 | 43422.881
August | 108582.651 | 127.6529 | 608.8183 | 0 | 0.0021 | 122169.1498 | 42056.4352
September | 108383.0564 | 127.4156 | 607.6439 | 0 | 0.0021 | 121933.4619 | 41978.7206
October | 135442.629 | 159.9816 | 775.1404 | 0 | 0.0027 | 155547.2223 | 52575.516
November | 157229.7185 | 183.4357 | 852.1229 | 0 | 0.003 | 170986.682 | 60681.832
December | 175197.8665 | 203.6351 | 933.5289 | 0 | 0.0033 | 187318.5219 | 67499.0268
Annual Sum or Average | 1672380 | 1961.578 | 9282.4335 | 0 | 0.0322 | 1862650 | 647053.482
Minimum of Months | 108383.0564 | 127.4156 | 607.6439 | 0 | 0.0021 | 121933.4619 | 41978.7206
Maximum of Months | 180396.1512 | 209.0914 | 948.9727 | 0 | 0.0033 | 190415.056 | 69411.6451
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 670948000000 | 387066.776 | 13-JAN-09:09 | 40487.594 | 120867.849 | 30599.064 | 105894.469 | 0 | 1622 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 597765000000 | 373642.193 | 03-FEB-09:09 | 40487.594 | 120867.849 | 30623.67 | 95083.006 | 0 | 1622 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 602447000000 | 351246.444 | 13-MAR-08:09 | 40487.594 | 120867.849 | 30565.632 | 79767.046 | 0 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 555344000000 | 330733.556 | 03-APR-08:09 | 40487.594 | 120867.849 | 30564.903 | 60774.394 | 0 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 556926000000 | 350042.982 | 23-MAY-13:00 | 40487.594 | 120867.849 | 33263.677 | 1503.307 | 52707.712 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 459539000000 | 335329.026 | 08-JUN-14:00 | 40487.594 | 120867.849 | 32520.371 | 2530.765 | 37709.606 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 449549000000 | 299069.616 | 21-JUL-16:00 | 40487.594 | 120867.849 | 34183.324 | 376.991 | 101941.016 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 430476000000 | 334508.568 | 11-AUG-14:00 | 40487.594 | 120867.849 | 33032.93 | 2220.979 | 52572.365 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 429646000000 | 314890.413 | 07-SEP-15:00 | 40487.594 | 120867.849 | 32222.972 | 4174.114 | 44953.209 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 548087000000 | 336778.897 | 30-OCT-08:09 | 40487.594 | 120867.849 | 30564.88 | 70857.694 | 0 | 1622 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 602490000000 | 355497.224 | 06-NOV-09:09 | 40487.594 | 120867.849 | 30564.331 | 83877.062 | 0 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 660037000000 | 366575.22 | 29-DEC-09:09 | 40487.594 | 120867.849 | 30638.214 | 89524.231 | 0 | 1622 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6563250000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 429646000000 | 299069.616 |  | 40487.594 | 120867.849 | 30564.331 | 376.991 | 0 | 0 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 670948000000 | 387066.776 |  | 40487.594 | 120867.849 | 34183.324 | 105894.469 | 101941.016 | 1622 | 1212.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 162747.29 | 31181.15 | 0 | 193928.44
Cost per Total Building Area ($/m2) | 42.78 | 8.2 | 0 | 50.98
Cost per Net Conditioned Building Area ($/m2) | 42.78 | 8.2 | 0 | 50.98

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Floor 1 Anesthesia Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Anesthesia Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Anesthesia Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 MRI Control Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 MRI Control Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 MRI Control Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 MRI Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 MRI Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 MRI Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Operating Room 1 humidity sched | Any number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Floor 1 Operating Room 1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Operating Room 1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Operating Room 2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Operating Room 2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Operating Room 3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Operating Room 3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 PACU Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 PACU Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 PACU Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 PACU Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Procedure Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Procedure Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Procedure Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Recovery Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Recovery Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Recovery Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Step Down Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Step Down Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Step Down Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 2 X-Ray Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 2 X-Ray Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 2 X-Ray Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
AHU-1_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
HeatSys1 Loop Setpoint Sched | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_SCH | fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5
|  |  | WinterDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
HTGSETP_SCH | Temperature | Through 12/31 | WD | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6
|  |  | WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sats | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sun, Hol, Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
CLGSETP_SCH | Temperature | Through 12/31 | WD | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6
|  |  | WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sats | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sun, Hol, Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
BLDG_OA_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_CAV_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6 | 109.2 | 5694
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
BLDG_CAV_SCH_HUMID | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
BLDG_OA_FRAC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 938.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0