## BuildingSummary
Building Summary - Primary School new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Primary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 6871 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.35
| Total | 0.35
| Skylight/TDD Percentage | 0.19%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Flat built-up | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2512
| Net Dimensions - Total Area (m2) | 1619.42
| Wall to Skin Ratio | 0.27
Roof
| Construction Type | Insulation Entirely Above Deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6871
| Net Dimensions - Total Area (m2) | 6871
| Roof to Skin Ratio | 0.73
Window Dimensions (m2)
| South | 324.79 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| East | 114.8
| North | 324.79
| West | 114.8
| Total Area (m2) | 879.18
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 13.38
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 10 cm concrete slab-on-grade
| Dimensions - Total Area (m2) | 6871
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 2932
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 13742
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.37 | 2003 CBECS
HVAC |  |  | 2003 CBECS
| System Type | CAV, PSZ-AC (gym, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | gas boiler, gas furnace (gym, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | PACU
| Fan Control | Constant
Service Water Heating
| SWH Type | Storage Tank | Standard 90.1-2004
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 589.92

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 57.6 | 0 | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 57.6 | 0 | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 57.6 | 0 | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140 | 49 | 4 | 78.75 | 15.064 | 8.07 | 0 | 0 | 5 | 0.6 | 582.75 | 0 | 0.39302
COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72 | 25.2 | 3.33 | 48.6486 | 15.064 | 20 | 0 | 0 | 5 | 0.6 | 340.4432 | 0 | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 | 0 | 0 | 5.38 | 4 | 0 | 0 | 2.5 | 0.3 | 163.8 | 0 | 0.29003
LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76 | 26.6 | 0 | 0 | 13.988 | 4 | 0 | 0 | 2.5 | 0.3 | 51.3 | 0 | 0.39302
MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 16.14 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27209
BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 100 | 1.9 | 9.684 | 4 | 0 | 213.9574 | 0 | 0 | 0 | 283.1682 | 0.32937
OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168 | 58.8 | 20 | 22.05 | 11.836 | 10.8 | 0 | 0 | 2.5 | 0.3 | 187.425 | 0 | 0.37575
GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68 | 37.18 | 3.33 | 107.2072 | 15.064 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32392
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 12.912 | 190.452 | 1431.08 | 378.54 | 0 | 0 | 0 | 2359.735 | 0.32392
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144 | 50.4 | 1.3935 | 226.0419 | 15.064 | 25.3936 | 0 | 0 | 3.8 | 0.9 | 1142.4592 | 0 | 0.39648
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160 | 56 | 4.35 | 91.7241 | 13.988 | 15 | 0 | 0 | 5 | 0.6 | 698.0207 | 0 | 0.3812
Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512 | 892.58 |  | 1406.3793
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 45.6 | 310.9 | 58.3 | 331.2 | 294.4 | 45 | 13.5 | 725.5 | 19.8 | 78.2 | 849.9 | 131.1 | 146 | 19 | 32.3 | 3.69
Fabric
Exterior walls
| Construction Type | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.262 | 0.262 | 0.262 | 0.34 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.23
| SHGC | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.501
| Visible transmittance | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.775 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_POD_1_COOLC DXCOIL | 260.6977 | 279.8594 | 313.6384 | 267.1519 | 239.791 | 291.4157 | 327.8641 | 277.3761 | 313.3442 | 251.5777 | 267.4908 | 293.627 | 268.0772 | 283.0664 | 254.5615 | 223.3529
| VAV_POD_2_COOLC DXCOIL | 211.3105 | 227.1324 | 253.0068 | 215.8897 | 190.9743 | 234.0635 | 260.9284 | 219.7677 | 247.6906 | 193.9585 | 211.7995 | 231.7025 | 211.2815 | 221.5325 | 197.8522 | 169.0064
| VAV_POD_3_COOLC DXCOIL | 209.1043 | 225.4864 | 252.8085 | 215.7453 | 194.5759 | 234.7748 | 265.6001 | 223.8032 | 251.8652 | 204.0504 | 216.0148 | 236.7965 | 216.6519 | 228.7208 | 205.9072 | 180.8801
| VAV_OTHER_COOLC DXCOIL | 298.6742 | 315.5089 | 340.4706 | 301.9489 | 268.2445 | 318.2906 | 302.7929 | 303.1974 | 341.0012 | 256.3978 | 292.1528 | 318.0518 | 289.1626 | 300.3109 | 265.6566 | 206.9923
| PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | 75.1492 | 75.8083 | 65.8768 | 69.0854 | 52.9061 | 62.8531 | 67.0215 | 69.9924 | 70.2496 | 50.5941 | 68.4273 | 66.2866 | 63.8062 | 61.667 | 54.3931 | 43.7957
| PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | 88.8682 | 89.8586 | 86.1396 | 91.3235 | 56.4463 | 72.06 | 63.7844 | 88.7141 | 68.8593 | 55.373 | 88.2163 | 67.0315 | 88.7955 | 63.6855 | 73.4392 | 53.798
| PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | 101.4164 | 106.1231 | 90.447 | 100.5422 | 56.3318 | 73.2425 | 92.2771 | 96.7822 | 75.3525 | 52.8121 | 93.6768 | 70.1211 | 89.5015 | 64.9859 | 68.7567 | 45.3053
Heating (kW)
| HEATSYS1 BOILER | 1165.4976 | 1344.2076 | 1353.6497 | 1303.1863 | 1086.5501 | 1269.1294 | 1402.4442 | 1409.5472 | 1259.5835 | 1205.9491 | 1449.6198 | 1279.0455 | 1492.6941 | 1390.0717 | 1431.3931 | 1477.9212
| PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 41.4648 | 54.7392 | 46.1832 | 59.0495 | 43.1251 | 49.9252 | 47.6675 | 65.7326 | 52.2282 | 56.8462 | 76.7893 | 62.3454 | 82.9866 | 75.6209 | 84.9432 | 108.2105
| PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 91.3595 | 120.6071 | 101.7557 | 130.104 | 95.0178 | 110.0005 | 105.0261 | 144.8291 | 115.0747 | 125.2496 | 169.1903 | 137.3661 | 182.8449 | 166.6161 | 187.1557 | 231.763
| PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 87.5151 | 115.5319 | 97.4737 | 124.6291 | 91.0194 | 105.3716 | 100.6065 | 138.7345 | 110.2322 | 119.979 | 162.0706 | 131.5856 | 175.1506 | 159.6047 | 179.28 | 222.0102
HVAC Efficiency
Air Conditioning (COP)
| VAV_POD_1_COOLC DXCOIL | 4.56 | 4.56 | 4.54 | 4.56 | 4.59 | 4.56 | 4.54 | 4.56 | 4.54 | 4.59 | 4.56 | 4.56 | 4.56 | 4.56 | 4.59 | 4.58
| VAV_POD_2_COOLC DXCOIL | 4.86 | 4.59 | 4.58 | 4.86 | 4.86 | 4.59 | 4.56 | 4.86 | 4.58 | 4.86 | 4.86 | 4.59 | 4.86 | 4.86 | 4.86 | 4.86
| VAV_POD_3_COOLC DXCOIL | 4.86 | 4.58 | 4.58 | 4.86 | 4.86 | 4.58 | 4.56 | 4.59 | 4.59 | 4.86 | 4.86 | 4.58 | 4.86 | 4.59 | 4.86 | 4.86
| VAV_OTHER_COOLC DXCOIL | 4.56 | 4.54 | 4.54 | 4.56 | 4.56 | 4.54 | 4.56 | 4.56 | 4.54 | 4.59 | 4.56 | 4.54 | 4.56 | 4.56 | 4.56 | 4.86
| PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | 3.75 | 3.8 | 4.32 | 4.05 | 3.47 | 4.37 | 4.32 | 4.05 | 4.32 | 3.47 | 4.04 | 4.32 | 4.16 | 4.37 | 3.47 | 3.47
| PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | 3.53 | 3.53 | 3.63 | 3.53 | 3.47 | 3.9 | 4.36 | 3.52 | 4.32 | 3.47 | 3.52 | 4.32 | 3.53 | 4.37 | 3.2 | 3.47
| PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | 3.51 | 3.51 | 3.84 | 3.51 | 3.47 | 4.11 | 4.18 | 3.53 | 4.18 | 3.47 | 3.52 | 4.32 | 3.56 | 4.37 | 3.32 | 3.47
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
| PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_1:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26 | 2.26
| VAV_POD_1_FAN | 15.75 | 16.91 | 18.95 | 16.14 | 14.49 | 17.6 | 19.81 | 16.76 | 18.93 | 15.2 | 16.16 | 17.74 | 16.19 | 17.1 | 15.38 | 13.49
| VAV_POD_2_FAN | 12.77 | 13.72 | 15.28 | 13.04 | 11.54 | 14.14 | 15.76 | 13.28 | 14.96 | 11.72 | 12.79 | 14 | 12.76 | 13.38 | 11.95 | 10.21
| VAV_POD_3_FAN | 12.63 | 13.62 | 15.27 | 13.03 | 11.75 | 14.18 | 16.04 | 13.52 | 15.22 | 12.33 | 13.05 | 14.3 | 13.09 | 13.82 | 12.44 | 10.93
| VAV_OTHER_FAN | 18.04 | 19.06 | 20.57 | 18.24 | 16.2 | 19.23 | 18.29 | 18.32 | 20.6 | 15.49 | 17.65 | 19.21 | 17.47 | 18.14 | 16.05 | 12.5
| PSZ-AC_2:5_UNITARY_PACKAGE_FAN | 3.6 | 3.74 | 3.97 | 3.65 | 3.2 | 3.8 | 4.05 | 3.7 | 4.24 | 3.06 | 3.6 | 4 | 3.56 | 3.73 | 3.29 | 2.65
| PSZ-AC_1:6_UNITARY_PACKAGE_FAN | 3.58 | 3.62 | 3.78 | 3.68 | 3.41 | 3.76 | 3.85 | 3.57 | 4.16 | 3.35 | 3.55 | 4.05 | 3.58 | 3.85 | 3.47 | 3.25
| PSZ-AC_2:7_UNITARY_PACKAGE_FAN | 4.08 | 4.27 | 4.65 | 4.05 | 3.4 | 4.29 | 5.57 | 3.9 | 4.55 | 3.19 | 3.77 | 4.24 | 3.73 | 3.93 | 3.46 | 2.74
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.088873 | 0.11931 | 0.092126 | 0.097936 | 0.12882 | 0.10019 | 0.14963 | 0.078711 | 0.037125 | 0.076011 | 0.087957 | 0.037135 | 0.061432 | 0.077308 | 0.060037 | 0.095433
| Total Cost ($/m2) | 16.32 | 20.75 | 15.57 | 15.14 | 18.2 | 15.41 | 20 | 11.78 | 5.28 | 9.44 | 12.29 | 5.02 | 8.43 | 10.05 | 7.61 | 11.61
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011447 | 0.0081155 | 0.0083732 | 0.010051 | 0.0084706 | 0.0078809 | 0.0084661 | 0.0098064 | 0.0070001 | 0.0083601 | 0.0084418 | 0.0069887 | 0.0079189 | 0.0082211 | 0.0079042 | 0.0041235
| Total Cost ($/m2) | 0.86 | 1.42 | 1.43 | 2.26 | 1.15 | 1.44 | 2.78 | 3.39 | 1.82 | 2.46 | 3.86 | 2.48 | 5 | 4.34 | 5.97 | 5.05
Total Utility Costs
| Cost Intensity ($/m2) | 17.19 | 22.17 | 17 | 17.4 | 19.36 | 16.84 | 22.78 | 15.17 | 7.1 | 11.91 | 16.15 | 7.5 | 13.44 | 14.39 | 13.58 | 16.67
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 466191.6667 | 399852.7778 | 352805.5556 | 272911.1111 | 186305.5556 | 251666.6667 | 118611.1111 | 235661.1111 | 168536.1111 | 73716.6667 | 160944.4444 | 123905.5556 | 140511.1111 | 89833.3333 | 77227.7778 | 46361.1111
| Interior Lighting | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111 | 342536.1111
| Exterior Lighting | 17155.5556 | 17150 | 17147.2222 | 17144.4444 | 17130.5556 | 17127.7778 | 17136.1111 | 17125 | 17133.3333 | 17097.2222 | 17127.7778 | 17119.4444 | 17116.6667 | 17113.8889 | 17102.7778 | 16997.2222
| Interior Equipment | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925 | 348925
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 64550 | 64250 | 77772.2222 | 58283.3333 | 53786.1111 | 74205.5556 | 68850 | 62100 | 77555.5556 | 49330.5556 | 68138.8889 | 73855.5556 | 71794.4444 | 72402.7778 | 62927.7778 | 57608.3333
| Pumps | 22.2222 | 208.3333 | 200 | 302.7778 | 125 | 219.4444 | 469.4444 | 527.7778 | 352.7778 | 422.2222 | 775 | 547.2222 | 1144.4444 | 927.7778 | 1472.2222 | 3019.4444
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 22552.7778 | 22236.1111 | 22030.5556 | 21938.8889 | 22147.2222 | 21822.2222 | 21741.6667 | 21672.2222 | 21652.7778 | 21613.8889 | 21466.6667 | 21447.2222 | 21297.2222 | 21216.6667 | 21027.7778 | 20611.1111
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1261933.3333 | 1195161.1111 | 1161413.8889 | 1062038.8889 | 970958.3333 | 1056502.7778 | 918269.4444 | 1028547.2222 | 976688.8889 | 853644.4444 | 959916.6667 | 928336.1111 | 943322.2222 | 892955.5556 | 871216.6667 | 836058.3333
Gas (MJ)
| Heating | 87300 | 746920 | 730520 | 1069960 | 466100 | 794360 | 1770290 | 1882780 | 1300740 | 1529340 | 2640840 | 1938450 | 3825610 | 3111320 | 4654460 | 7865890
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030 | 361030
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 70280 | 93080 | 82570 | 113380 | 106590 | 97500 | 123770 | 129530 | 126440 | 135330 | 143290 | 142020 | 155530 | 156690 | 173890 | 195620
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 518610 | 1201030 | 1174120 | 1544380 | 933720 | 1252890 | 2255100 | 2373340 | 1788210 | 2025690 | 3145150 | 2441500 | 4342170 | 3629040 | 5189380 | 8422540
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 5061570 | 5503610 | 5355210 | 5367710 | 4429170 | 5056300 | 5560860 | 6076120 | 5304290 | 5098810 | 6600850 | 5783510 | 7738130 | 6843670 | 8325760 | 11432350
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 244.257 | 209.4993 | 184.8494 | 142.9894 | 97.6132 | 131.8585 | 62.1452 | 123.4726 | 88.303 | 38.6232 | 84.3254 | 64.9192 | 73.6196 | 47.0674 | 40.4628 | 24.2905
| Interior Lighting (elec) | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688 | 179.4688
| Exterior Lighting (elec) | 8.9885 | 8.9856 | 8.9841 | 8.9827 | 8.9754 | 8.9739 | 8.9783 | 8.9725 | 8.9769 | 8.9579 | 8.9739 | 8.9696 | 8.9681 | 8.9667 | 8.9608 | 8.9055
| Interior Equipment (elec) | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162 | 182.8162
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 33.8204 | 33.6632 | 40.7481 | 30.537 | 28.1808 | 38.8793 | 36.0734 | 32.5367 | 40.6346 | 25.8463 | 35.7008 | 38.696 | 37.6161 | 37.9348 | 32.9705 | 30.1834
| Pumps (elec) | 0.011643 | 0.10915 | 0.10479 | 0.15864 | 0.065493 | 0.11498 | 0.24596 | 0.27652 | 0.18483 | 0.22122 | 0.40605 | 0.28671 | 0.59962 | 0.4861 | 0.77136 | 1.582
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 11.8163 | 11.6504 | 11.5427 | 11.4947 | 11.6038 | 11.4336 | 11.3914 | 11.355 | 11.3448 | 11.3244 | 11.2473 | 11.2371 | 11.1585 | 11.1163 | 11.0173 | 10.799
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 661.1789 | 626.1941 | 608.5126 | 556.4459 | 508.7251 | 553.5453 | 481.1192 | 538.8983 | 511.7276 | 447.2595 | 502.9399 | 486.3935 | 494.2454 | 467.8562 | 456.4663 | 438.0454
Gas (MJ/m2)
| Heating (gas) | 12.7056 | 108.7062 | 106.3193 | 155.7211 | 67.8358 | 115.6105 | 257.6466 | 274.0183 | 189.3087 | 222.579 | 384.3458 | 282.1205 | 556.7763 | 452.8191 | 677.4065 | 1144.7955
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544 | 52.544
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 10.2285 | 13.5468 | 12.0172 | 16.5012 | 15.513 | 14.1901 | 18.0134 | 18.8517 | 18.402 | 19.6958 | 20.8543 | 20.6695 | 22.6357 | 22.8045 | 25.3078 | 28.4704
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 75.4781 | 174.797 | 170.8805 | 224.7679 | 135.8929 | 182.3446 | 328.2055 | 345.4141 | 260.2547 | 294.8173 | 457.7427 | 355.334 | 631.956 | 528.1677 | 755.2583 | 1225.8099
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 736.657 | 800.9911 | 779.3931 | 781.2123 | 644.618 | 735.89 | 809.3232 | 884.3138 | 771.9822 | 742.0768 | 960.6826 | 841.7276 | 1126.2014 | 996.0224 | 1211.7246 | 1663.8553
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 335.74 | 330.2061 | 265.1299 | 248.0114 | 263.2635 | 249.261 | 219.3016 | 249.4713 | 214.0304 | 178.0604 | 183.2659 | 233.1137 | 186.7305 | 189.4781 | 183.0426 | 185.7113
| Feb | 340.6814 | 307.999 | 274.1515 | 253.2658 | 262.7417 | 251.9428 | 282.0634 | 233.2973 | 250.7224 | 215.1298 | 183.8146 | 205.0625 | 183.2955 | 232.0073 | 182.6597 | 183.065
| Mar | 346.2155 | 322.8817 | 304.7812 | 272.1202 | 257.721 | 260.9987 | 257.9329 | 286.9419 | 252.411 | 232.4652 | 251.3221 | 251.9671 | 222.2543 | 245.3632 | 183.588 | 180.6446
| Apr | 349.9885 | 337.4717 | 323.7684 | 299.0083 | 274.1349 | 304.8086 | 280.5541 | 283.3825 | 270.7258 | 220.5145 | 270.0718 | 266.2398 | 255.7264 | 239.3982 | 213.8116 | 181.2772
| May | 376.6668 | 388.4359 | 367.4316 | 328.1052 | 294.022 | 338.3339 | 298.8348 | 330.7029 | 299.5915 | 264.7162 | 311.405 | 281.6943 | 318.576 | 261.6728 | 251.1472 | 223.9771
| Jun | 394.9729 | 379.5567 | 437.35 | 351.3575 | 283.7893 | 400.7247 | 292.925 | 384.9354 | 329.7882 | 270.5795 | 383.5332 | 314.3234 | 358.2375 | 326.3648 | 307.0822 | 253.6118
| Jul | 302.05 | 347.3009 | 360.7011 | 306.4617 | 214.3641 | 309.3435 | 230.7019 | 332.5144 | 261.4367 | 209.4093 | 294.3366 | 244.8135 | 271.6365 | 225.7869 | 235.408 | 176.5498
| Aug | 313.945 | 318.7035 | 353.1735 | 281.4574 | 231.9299 | 309.4604 | 226.3061 | 328.1944 | 265.3368 | 198.5325 | 287.7651 | 250.8454 | 265.728 | 213.2885 | 225.3007 | 172.9841
| Sep | 375.0463 | 396.2805 | 397.4088 | 341.4258 | 295.534 | 338.1449 | 326.2316 | 335.2152 | 305.4042 | 271.4392 | 320.7189 | 292.4396 | 304.5006 | 277.901 | 292.0925 | 198.5624
| Oct | 371.9178 | 366.4631 | 328.5663 | 301.1044 | 285.2284 | 313.8462 | 290.8839 | 320.7889 | 281.677 | 245.5016 | 298.6304 | 268.9724 | 257.2413 | 254.6827 | 226.4447 | 179.8056
| Nov | 351.8225 | 339.5386 | 296.0903 | 273.6265 | 270.152 | 258.7594 | 252.0245 | 296.0744 | 248.2776 | 220.1329 | 298.09 | 246.6589 | 241.6559 | 201.9834 | 181.7325 | 179.1973
| Dec | 322.8102 | 315.7646 | 281.8396 | 263.683 | 264.3467 | 254.9062 | 222.717 | 213.6454 | 204.4706 | 180.6124 | 182.5472 | 197.9453 | 181.8852 | 186.8923 | 181.0004 | 182.3132
Time of Peak Electrical Demand
| Jan | 06-JAN-11:50 | 03-JAN-11:50 | 27-JAN-14:00 | 23-JAN-12:00 | 26-JAN-12:00 | 18-JAN-14:50 | 06-JAN-15:00 | 09-JAN-11:50 | 25-JAN-14:00 | 27-JAN-11:50 | 25-JAN-11:50 | 27-JAN-11:50 | 05-JAN-11:09 | 05-JAN-08:09 | 09-JAN-11:09 | 13-JAN-10:09
| Feb | 23-FEB-11:50 | 21-FEB-11:39 | 28-FEB-14:00 | 21-FEB-14:09 | 13-FEB-11:50 | 08-FEB-14:00 | 15-FEB-14:00 | 15-FEB-12:00 | 14-FEB-15:20 | 21-FEB-13:00 | 22-FEB-11:50 | 07-FEB-14:00 | 22-FEB-11:50 | 02-FEB-14:00 | 24-FEB-11:50 | 03-FEB-08:09
| Mar | 14-MAR-10:39 | 24-MAR-11:00 | 17-MAR-15:09 | 28-MAR-11:00 | 31-MAR-10:50 | 31-MAR-13:00 | 01-MAR-12:00 | 09-MAR-13:00 | 02-MAR-13:50 | 29-MAR-15:00 | 31-MAR-14:09 | 27-MAR-11:00 | 23-MAR-15:00 | 30-MAR-14:50 | 24-MAR-10:50 | 29-MAR-10:50
| Apr | 03-APR-13:00 | 10-APR-11:00 | 26-APR-13:00 | 13-APR-11:00 | 11-APR-13:00 | 28-APR-13:00 | 28-APR-11:50 | 04-APR-11:00 | 21-APR-13:00 | 14-APR-13:00 | 03-APR-13:00 | 25-APR-13:00 | 27-APR-13:50 | 06-APR-15:00 | 04-APR-14:00 | 19-APR-10:50
| May | 23-MAY-10:50 | 18-MAY-13:00 | 30-MAY-15:09 | 22-MAY-13:00 | 30-MAY-10:50 | 31-MAY-15:00 | 25-MAY-11:00 | 16-MAY-10:39 | 30-MAY-13:00 | 05-MAY-13:00 | 30-MAY-13:00 | 23-MAY-11:00 | 31-MAY-11:00 | 17-MAY-10:39 | 31-MAY-11:00 | 30-MAY-11:00
| Jun | 26-JUN-10:50 | 13-JUN-13:00 | 28-JUN-15:00 | 19-JUN-10:50 | 23-JUN-10:50 | 27-JUN-15:00 | 16-JUN-10:50 | 30-JUN-13:00 | 29-JUN-13:00 | 28-JUN-11:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-11:00 | 30-JUN-12:00 | 14-JUN-13:00 | 21-JUN-13:00
| Jul | 13-JUL-11:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-11:00 | 24-JUL-10:39 | 24-JUL-15:00 | 03-JUL-11:00 | 25-JUL-11:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-10:50 | 18-JUL-13:00 | 13-JUL-15:00 | 21-JUL-15:00 | 07-JUL-10:39 | 11-JUL-11:00
| Aug | 21-AUG-13:00 | 31-AUG-10:00 | 01-AUG-15:00 | 17-AUG-11:00 | 08-AUG-10:39 | 03-AUG-11:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-11:00 | 15-AUG-13:00
| Sep | 18-SEP-11:00 | 15-SEP-13:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-11:00 | 21-SEP-13:00 | 28-SEP-15:09 | 05-SEP-10:39 | 05-SEP-11:39 | 13-SEP-11:00 | 06-SEP-10:50 | 05-SEP-13:00 | 22-SEP-13:09 | 12-SEP-13:00 | 08-SEP-11:30 | 07-SEP-15:00
| Oct | 06-OCT-10:39 | 30-OCT-12:00 | 03-OCT-09:30 | 02-OCT-11:00 | 05-OCT-10:50 | 06-OCT-13:09 | 17-OCT-11:50 | 03-OCT-10:39 | 03-OCT-11:00 | 17-OCT-12:00 | 31-OCT-11:50 | 05-OCT-13:00 | 06-OCT-13:50 | 06-OCT-13:30 | 27-OCT-11:00 | 12-OCT-10:50
| Nov | 01-NOV-11:50 | 27-NOV-12:00 | 13-NOV-14:00 | 22-NOV-11:50 | 07-NOV-12:00 | 10-NOV-12:39 | 06-NOV-12:00 | 03-NOV-11:50 | 08-NOV-14:50 | 03-NOV-12:00 | 02-NOV-11:50 | 10-NOV-13:39 | 02-NOV-14:00 | 21-NOV-11:50 | 09-NOV-11:00 | 14-NOV-11:50
| Dec | 15-DEC-11:50 | 20-DEC-11:50 | 13-DEC-12:00 | 26-DEC-11:50 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 08-DEC-10:00 | 08-DEC-14:00 | 13-DEC-11:50 | 13-DEC-11:50 | 21-DEC-14:00 | 26-DEC-11:50 | 11-DEC-11:09 | 27-DEC-11:50 | 29-DEC-11:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12
| Total Building | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12 | 921.12
Emissions
| Carbon Equivalent (kg) | 355437.0694 | 420316.5563 | 371774.9781 | 354996.1128 | 130309.2239 | 378924.6375 | 147979.7299 | 320357.062 | 431222.2061 | 98703.0896 | 568494.3207 | 423250.4259 | 401193.7168 | 391760.6881 | 391789.6187 | 387137.7284
| CO2 (kg) | 828398.2938 | 1062920 | 885682.7025 | 822954.405 | 351597.1744 | 909251.4093 | 404001.3974 | 746087.2151 | 1022820 | 253232.561 | 1344670 | 1010830 | 970621.5503 | 948049.0399 | 957860.4747 | 1028140
| NOX (kg) | 1437.8461 | 1371.676 | 1449.0935 | 1506.8011 | 303.4222 | 1443.3211 | 351.8548 | 1356.7608 | 1715.6938 | 333.1213 | 2298.9015 | 1665.8419 | 1563.7689 | 1518.9086 | 1500.0081 | 1136.6933
| SO2 (kg) | 5401.7222 | 5701.2353 | 4670.594 | 3728.1694 | 2825.6186 | 5811.9394 | 2672.6555 | 3755.2468 | 4265.4896 | 660.3409 | 6469.9107 | 4054.514 | 2227.5557 | 2385.2704 | 2057.5986 | 4258.1327
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0247 | 0.0161 | 0.0128 | 0.0138 | 0.0014 | 0.011 | 0.0014 | 0.0154 | 0.0168 | 0.0028 | 0.0198 | 0.0161 | 0.0167 | 0.0169 | 0.0156 | 0.0153
| Water for Electricity (m3) | 668.5198 | 1944.67 | 34499.1 | 6630.94 | 17047.8 | 28984.1 | 16122.7 | 233.519 | 4434.95 | 8721.5 | 1489.25 | 4215.39 | 1463.51 | 56563.5 | 1351.64 | 854.1849

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5061.57 | 736.66 | 736.66
Net Site Energy | 5061.57 | 736.66 | 736.66
Total Source Energy | 15635.33 | 2275.55 | 2275.55
Net Source Energy | 15635.33 | 2275.55 | 2275.55
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 87.3 | 0 | 0 | 0 | 0
Cooling | 1678.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 232.38 | 0 | 0 | 0 | 0 | 0
Pumps | 0.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 70.28 | 0 | 0 | 0 | 921.12
Refrigeration | 81.19 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4542.96 | 518.61 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 49 | 49 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 25.2 | 25.2 | 6.49 | 0.441 | 0.44 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 26.6 | 26.6 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 14 | 14 | 6.49 | 0.25 | 0.25 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 11.2 | 11.2 | 6.49 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 21 | 21 | 6.49 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 29.4 | 29.4 | 6.49 | 0.441 | 0.44 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 26.6 | 26.6 | 6.49 | 0.441 | 0.44 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 6.49 | 0.321 | 0.322
North Total or Average |  |  | 324.79 | 6.49 | 0.441 | 0.44
Non-North Total or Average |  |  | 567.77 | 6.49 | 0.253 | 0.255
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1165497.59 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 260697.74 | 208207.62 | 52490.12 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 211310.5 | 168764.25 | 42546.26 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 209104.31 | 167002.26 | 42102.05 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 298674.24 | 238537.75 | 60136.49 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 75149.17 | 54315.02 | 20834.15 | 0.72 | 3.75
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 88868.17 | 60082.28 | 28785.89 | 0.68 | 3.53
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 101416.42 | 68565.94 | 32850.48 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 41464.77 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 91359.55 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 87515.05 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 15.75 | 35936.97 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 12.77 | 29316.91 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 12.63 | 29010.83 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.04 | 41172 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.6 | 6871.81 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.58 | 6826.16 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.08 | 7661.62 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6476.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 66693.6206 | 114.6459 | 426.1213 | 0 | 0.0019 | 52736.1272 | 28504.3214
February | 61105.6473 | 105.7001 | 395.6126 | 0 | 0.0018 | 48960.9302 | 26182.1919
March | 70487.1099 | 122.0238 | 457.1033 | 0 | 0.0021 | 56571.0802 | 30211.4909
April | 66385.619 | 115.4016 | 434.2682 | 0 | 0.002 | 53745.3722 | 28501.4523
May | 77739.8347 | 135.386 | 510.4857 | 0 | 0.0023 | 63178.302 | 33400.9104
June | 78555.0662 | 136.9722 | 517.1491 | 0 | 0.0024 | 64003.0992 | 33767.8533
July | 61384.8546 | 106.6949 | 401.4484 | 0 | 0.0018 | 49683.5588 | 26353.106
August | 64901.4748 | 112.6479 | 423.1923 | 0 | 0.0019 | 52374.4824 | 27846.8568
September | 74037.3263 | 129.032 | 486.9129 | 0 | 0.0022 | 60260.9744 | 31819.5495
October | 73668.1063 | 128.1839 | 482.8738 | 0 | 0.0022 | 59760.9425 | 31640.3601
November | 69388.8613 | 120.5232 | 453.1347 | 0 | 0.0021 | 56080.2375 | 29780.9165
December | 64050.7728 | 110.6345 | 413.42 | 0 | 0.0019 | 51164.6447 | 27428.0605
Annual Sum or Average | 828398.2938 | 1437.8461 | 5401.7222 | 0 | 0.0247 | 668519.7512 | 355437.0694
Minimum of Months | 61105.6473 | 105.7001 | 395.6126 | 0 | 0.0018 | 48960.9302 | 26182.1919
Maximum of Months | 78555.0662 | 136.9722 | 517.1491 | 0 | 0.0024 | 64003.0992 | 33767.8533
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 358371000000 | 335739.96 | 06-JAN-11:50 | 80532.756 | 81262.495 | 20235.845 | 0 | 149866.21 | 0 | 1.355 | 0 | 0 | 0 | 0 | 0 | 3841.3 | 0 | 0
February | 332717000000 | 340681.375 | 23-FEB-11:50 | 80532.756 | 81262.495 | 21156.942 | 0 | 153887.938 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 3841.24 | 0 | 0
March | 384432000000 | 346215.461 | 14-MAR-10:39 | 80532.756 | 81262.495 | 21480.462 | 0 | 159098.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.247 | 0 | 0
April | 365230000000 | 349988.539 | 03-APR-13:00 | 80532.756 | 77263.149 | 22476.153 | 0 | 167149.2 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2567.275 | 0 | 0
May | 429332000000 | 376666.766 | 23-MAY-10:50 | 80532.756 | 81262.495 | 24705.561 | 0 | 186325.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3840.841 | 0 | 0
June | 434937000000 | 394972.905 | 26-JUN-10:50 | 80532.756 | 81262.495 | 25979.945 | 0 | 203356.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3840.896 | 0 | 0
July | 337627000000 | 302050.017 | 13-JUL-11:00 | 44740.42 | 47274.638 | 22371.734 | 0 | 185222.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2440.464 | 0 | 0
August | 355914000000 | 313944.992 | 21-AUG-13:00 | 44740.42 | 43275.293 | 23369.254 | 0 | 200119.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2440.588 | 0 | 0
September | 409507000000 | 375046.336 | 18-SEP-11:00 | 80532.756 | 80410.298 | 24155.495 | 0 | 187376.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2570.963 | 0 | 0
October | 406109000000 | 371917.796 | 06-OCT-10:39 | 80532.756 | 80410.298 | 24384.088 | 0 | 182749.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.001 | 0 | 0
November | 381096000000 | 351822.547 | 01-NOV-11:50 | 80532.756 | 80410.298 | 22257.387 | 0 | 164781.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.078 | 0 | 0
December | 347692000000 | 322810.237 | 15-DEC-11:50 | 80532.756 | 80410.298 | 19400.056 | 0 | 138624.508 | 0 | 1.232 | 0 | 0 | 0 | 0 | 0 | 3841.387 | 0 | 0
Annual Sum or Average | 4542960000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 332717000000 | 302050.017 |  | 44740.42 | 43275.293 | 19400.056 | 0 | 138624.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2440.464 | 0 | 0
Maximum of Months | 434937000000 | 394972.905 |  | 80532.756 | 81262.495 | 25979.945 | 0 | 203356.813 | 0 | 1.355 | 0 | 0 | 0 | 0 | 0 | 3841.387 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 112151.4 | 5936.53 | 0 | 118087.94
Cost per Total Building Area ($/m2) | 16.32 | 0.86 | 0 | 17.19
Cost per Net Conditioned Building Area ($/m2) | 16.32 | 0.86 | 0 | 17.19

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5503.61 | 800.99 | 800.99
Net Site Energy | 5503.61 | 800.99 | 800.99
Total Source Energy | 1311.53 | 190.88 | 190.88
Net Source Energy | 1311.53 | 190.88 | 190.88
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 746.92 | 0 | 0 | 0 | 0
Cooling | 1439.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 231.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0.75 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 93.08 | 0 | 0 | 0 | 921.12
Refrigeration | 80.05 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4302.58 | 1201.03 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 49 | 49 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 25.2 | 25.2 | 6.49 | 0.61 | 0.61 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 26.6 | 26.6 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 14 | 14 | 6.49 | 0.25 | 0.25 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 11.2 | 11.2 | 6.49 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 21 | 21 | 6.49 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 29.4 | 29.4 | 6.49 | 0.61 | 0.61 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 26.6 | 26.6 | 6.49 | 0.61 | 0.61 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 6.49 | 0.383 | 0.384
North Total or Average |  |  | 324.79 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 567.77 | 6.49 | 0.253 | 0.255
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1344207.63 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 279859.43 | 223511.2 | 56348.22 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 227132.35 | 181400.45 | 45731.9 | 0.8 | 4.59
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 225486.44 | 180085.93 | 45400.51 | 0.8 | 4.58
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 315508.87 | 251982.82 | 63526.05 | 0.8 | 4.54
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 75808.33 | 55418.17 | 20390.16 | 0.73 | 3.8
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 89858.58 | 60751.88 | 29106.7 | 0.68 | 3.53
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 106123.15 | 71748.08 | 34375.07 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 54739.18 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 120607.13 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 115531.87 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.91 | 38578.39 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.72 | 31512.01 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.62 | 31283.66 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.06 | 43261.54 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.74 | 7128.51 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.62 | 6902.24 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.27 | 8017.19 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7469.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 86671.9595 | 108.9843 | 424.777 | 0 | 0.0012 | 144876.3567 | 33903.9696
February | 75221.0927 | 94.8108 | 371.8105 | 0 | 0.0011 | 126812.5226 | 29453.6955
March | 88856.989 | 114.0388 | 467.7954 | 0 | 0.0013 | 159560.0004 | 35056.0596
April | 83757.1962 | 108.7936 | 459.153 | 0 | 0.0013 | 156618.2485 | 33211.6346
May | 99642.0315 | 129.9952 | 554.1948 | 0 | 0.0016 | 189039.7837 | 39583.6095
June | 105080.2093 | 137.3389 | 587.9282 | 0 | 0.0017 | 200547.5887 | 41776.0626
July | 83864.7431 | 109.4232 | 466.6033 | 0 | 0.0013 | 159161.7568 | 33317.4215
August | 87280.8745 | 113.6601 | 482.525 | 0 | 0.0014 | 164591.7955 | 34646.1764
September | 92990.9354 | 121.4276 | 518.7378 | 0 | 0.0015 | 176945.6594 | 36955.5395
October | 91642.3104 | 119.2501 | 505.3816 | 0 | 0.0014 | 172387.9001 | 36365.8976
November | 84655.5505 | 109.106 | 452.1101 | 0 | 0.0013 | 154212.0621 | 33457.7093
December | 83258.772 | 104.8474 | 410.2186 | 0 | 0.0012 | 139911.7798 | 32588.7805
Annual Sum or Average | 1062920 | 1371.676 | 5701.2353 | 0 | 0.0161 | 1944670 | 420316.5563
Minimum of Months | 75221.0927 | 94.8108 | 371.8105 | 0 | 0.0011 | 126812.5226 | 29453.6955
Maximum of Months | 105080.2093 | 137.3389 | 587.9282 | 0 | 0.0017 | 200547.5887 | 41776.0626
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 320539000000 | 330206.105 | 03-JAN-11:50 | 80532.756 | 81262.495 | 19572.984 | 0 | 145008.18 | 0 | 8.213 | 0 | 0 | 0 | 0 | 0 | 3821.477 | 0 | 0
February | 280573000000 | 307998.953 | 21-FEB-11:39 | 80532.756 | 81262.495 | 18410.934 | 0 | 123941.702 | 0 | 9.494 | 0 | 0 | 0 | 0 | 0 | 3841.572 | 0 | 0
March | 353027000000 | 322881.696 | 24-MAR-11:00 | 80532.756 | 81262.495 | 19176.66 | 0 | 139339.182 | 0 | 6.539 | 0 | 0 | 0 | 0 | 0 | 2564.065 | 0 | 0
April | 346518000000 | 337471.686 | 10-APR-11:00 | 80532.756 | 81262.495 | 20310.063 | 0 | 152798.982 | 0 | 2.722 | 0 | 0 | 0 | 0 | 0 | 2564.669 | 0 | 0
May | 418251000000 | 388435.915 | 18-MAY-13:00 | 80532.756 | 77263.149 | 25109.303 | 0 | 202959.791 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2570.911 | 0 | 0
June | 443712000000 | 379556.733 | 13-JUN-13:00 | 80532.756 | 77263.149 | 24337.406 | 0 | 194853.308 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 2570.101 | 0 | 0
July | 352146000000 | 347300.861 | 18-JUL-11:00 | 44740.42 | 47274.638 | 26982.921 | 0 | 225859.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2443.24 | 0 | 0
August | 364160000000 | 318703.538 | 31-AUG-10:00 | 44740.42 | 47274.638 | 23512.808 | 0 | 200735.688 | 0 | 0.593 | 0 | 0 | 0 | 0 | 0 | 2439.392 | 0 | 0
September | 391493000000 | 396280.543 | 15-SEP-13:00 | 80532.756 | 76410.953 | 25735.534 | 0 | 211029.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2572.011 | 0 | 0
October | 381409000000 | 366463.061 | 30-OCT-12:00 | 80532.756 | 80410.298 | 23670.926 | 0 | 179278.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2570.131 | 0 | 0
November | 341194000000 | 339538.629 | 27-NOV-12:00 | 80532.756 | 80410.298 | 20624.986 | 0 | 155403.354 | 0 | 1.361 | 0 | 0 | 0 | 0 | 0 | 2565.874 | 0 | 0
December | 309555000000 | 315764.564 | 20-DEC-11:50 | 80532.756 | 80410.298 | 18663.087 | 0 | 132342.126 | 0 | 11.262 | 0 | 0 | 0 | 0 | 0 | 3805.036 | 0 | 0
Annual Sum or Average | 4302580000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 280573000000 | 307998.953 |  | 44740.42 | 47274.638 | 18410.934 | 0 | 123941.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2439.392 | 0 | 0
Maximum of Months | 443712000000 | 396280.543 |  | 80532.756 | 81262.495 | 26982.921 | 0 | 225859.642 | 0 | 11.262 | 0 | 0 | 0 | 0 | 0 | 3841.572 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 142595.24 | 9746.9 | 0 | 152342.15
Cost per Total Building Area ($/m2) | 20.75 | 1.42 | 0 | 22.17
Cost per Net Conditioned Building Area ($/m2) | 20.75 | 1.42 | 0 | 22.17

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5355.21 | 779.39 | 779.39
Net Site Energy | 5355.21 | 779.39 | 779.39
Total Source Energy | 14506.93 | 2111.33 | 2111.33
Net Source Energy | 14506.93 | 2111.33 | 2111.33
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 730.52 | 0 | 0 | 0 | 0
Cooling | 1270.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 279.98 | 0 | 0 | 0 | 0 | 0
Pumps | 0.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 82.57 | 0 | 0 | 0 | 921.12
Refrigeration | 79.31 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4181.09 | 1174.12 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 49 | 49 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 25.2 | 25.2 | 6.49 | 0.61 | 0.61 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 26.6 | 26.6 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 14 | 14 | 6.49 | 0.25 | 0.25 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 11.2 | 11.2 | 6.49 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 21 | 21 | 6.49 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 29.4 | 29.4 | 6.49 | 0.61 | 0.61 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 29.4 | 29.4 | 6.49 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 26.6 | 26.6 | 6.49 | 0.61 | 0.61 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 6.49 | 0.383 | 0.384
North Total or Average |  |  | 324.79 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 567.77 | 6.49 | 0.253 | 0.255
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1353649.71 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 313638.39 | 250488.95 | 63149.44 | 0.8 | 4.54
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 253006.8 | 202065.21 | 50941.59 | 0.8 | 4.58
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 252808.55 | 201906.88 | 50901.67 | 0.8 | 4.58
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 340470.62 | 271918.65 | 68551.97 | 0.8 | 4.54
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 65876.76 | 52546.72 | 13330.04 | 0.8 | 4.32
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 86139.58 | 60107.32 | 26032.26 | 0.7 | 3.63
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 90447 | 67260.12 | 23186.88 | 0.74 | 3.84
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46183.18 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 101755.65 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 97473.68 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.95 | 43005.07 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 15.28 | 35101.79 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 15.27 | 35074.29 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 20.57 | 46684.22 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 3.97 | 7445.34 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.78 | 7202.59 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.65 | 8716.44 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7521.53 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 66505.1711 | 103.8266 | 314.6519 | 0 | 0.0009 | 2323900 | 27412.2153
February | 60824.784 | 95.6242 | 292.5928 | 0 | 0.0008 | 2161020 | 25138.187
March | 73371.4785 | 119.3768 | 382.0832 | 0 | 0.001 | 2822200 | 30730.8666
April | 68791.3163 | 113.7202 | 371.2204 | 0 | 0.001 | 2742060 | 28994.0744
May | 80446.9523 | 134.0502 | 441.7994 | 0 | 0.0012 | 3263460 | 34014.0521
June | 91391.6303 | 152.9565 | 506.7451 | 0 | 0.0014 | 3743230 | 38709.2609
July | 75128.892 | 125.5166 | 414.9658 | 0 | 0.0011 | 3065260 | 31798.6653
August | 76332.6012 | 127.3544 | 420.3619 | 0 | 0.0011 | 3105110 | 32290.6328
September | 81992.4795 | 137.0189 | 453.1326 | 0 | 0.0012 | 3347190 | 34707.2974
October | 74687.0842 | 123.6501 | 404.363 | 0 | 0.0011 | 2986880 | 31497.567
November | 69080.1977 | 111.8912 | 356.093 | 0 | 0.001 | 2630200 | 28882.5811
December | 67130.1154 | 104.1078 | 312.5848 | 0 | 0.0009 | 2308590 | 27599.5781
Annual Sum or Average | 885682.7025 | 1449.0935 | 4670.594 | 0 | 0.0128 | 34499100 | 371774.9781
Minimum of Months | 60824.784 | 95.6242 | 292.5928 | 0 | 0.0008 | 2161020 | 25138.187
Maximum of Months | 91391.6303 | 152.9565 | 506.7451 | 0 | 0.0014 | 3743230 | 38709.2609
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 281643000000 | 265129.876 | 27-JAN-14:00 | 80532.756 | 77263.149 | 18255.249 | 0 | 86572.242 | 0 | 7.55 | 0 | 0 | 0 | 0 | 0 | 2498.93 | 0 | 0
February | 261903000000 | 274151.492 | 28-FEB-14:00 | 80532.756 | 77263.149 | 18913.951 | 0 | 94935.748 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2500.886 | 0 | 0
March | 342035000000 | 304781.162 | 17-MAR-15:09 | 80532.756 | 75263.477 | 21299.681 | 0 | 125296.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2388.648 | 0 | 0
April | 332322000000 | 323768.428 | 26-APR-13:00 | 80532.756 | 77263.149 | 24263.786 | 0 | 139192.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2515.942 | 0 | 0
May | 395512000000 | 367431.628 | 30-MAY-15:09 | 80532.756 | 75263.477 | 28874.515 | 0 | 180352.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2408.591 | 0 | 0
June | 453657000000 | 437350.008 | 28-JUN-15:00 | 80532.756 | 75263.477 | 31014.343 | 0 | 248119.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2420.119 | 0 | 0
July | 371492000000 | 360701.106 | 11-JUL-15:00 | 44740.42 | 41275.62 | 29201.437 | 0 | 243044.18 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2439.44 | 0 | 0
August | 376321000000 | 353173.531 | 01-AUG-15:00 | 44740.42 | 41275.62 | 29285.695 | 0 | 235435.047 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 2436.738 | 0 | 0
September | 405660000000 | 397408.804 | 08-SEP-13:00 | 80532.756 | 76410.953 | 28859.948 | 0 | 209039.473 | 0 | 0.011 | 0 | 0 | 0 | 0 | 0 | 2565.663 | 0 | 0
October | 361993000000 | 328566.263 | 03-OCT-09:30 | 80532.756 | 80410.298 | 22909.913 | 0 | 142138.08 | 0 | 8.779 | 0 | 0 | 0 | 0 | 0 | 2566.437 | 0 | 0
November | 318765000000 | 296090.29 | 13-NOV-14:00 | 80532.756 | 76410.953 | 20824.897 | 0 | 115811.936 | 0 | 1.838 | 0 | 0 | 0 | 0 | 0 | 2507.91 | 0 | 0
December | 279788000000 | 281839.556 | 13-DEC-12:00 | 80532.756 | 80410.298 | 21464.129 | 0 | 96922.092 | 0 | 27.182 | 0 | 0 | 0 | 0 | 0 | 2483.099 | 0 | 0
Annual Sum or Average | 4181090000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 261903000000 | 265129.876 |  | 44740.42 | 41275.62 | 18255.249 | 0 | 86572.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2388.648 | 0 | 0
Maximum of Months | 453657000000 | 437350.008 |  | 80532.756 | 80410.298 | 31014.343 | 0 | 248119.313 | 0 | 27.182 | 0 | 0 | 0 | 0 | 0 | 2566.437 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 106996.9 | 9831.13 | 0 | 116828.03
Cost per Total Building Area ($/m2) | 15.57 | 1.43 | 0 | 17
Cost per Net Conditioned Building Area ($/m2) | 15.57 | 1.43 | 0 | 17

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5367.71 | 781.21 | 781.21
Net Site Energy | 5367.71 | 781.21 | 781.21
Total Source Energy | 14548.17 | 2117.33 | 2117.33
Net Source Energy | 14548.17 | 2117.33 | 2117.33
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1069.96 | 0 | 0 | 0 | 0
Cooling | 982.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 209.82 | 0 | 0 | 0 | 0 | 0
Pumps | 1.09 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 113.38 | 0 | 0 | 0 | 921.12
Refrigeration | 78.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3823.34 | 1544.38 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 49 | 49 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.402 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 26.6 | 26.6 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 14 | 14 | 3.18 | 0.262 | 0.318 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 11.2 | 11.2 | 3.18 | 0.262 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 21 | 21 | 3.18 | 0.262 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.402 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.402 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.23 | 0.314 | 0.431
North Total or Average |  |  | 324.79 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.26 | 0.264 | 0.322
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1303186.29 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 267151.9 | 213362.27 | 53789.63 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 215889.69 | 172421.44 | 43468.25 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 215745.26 | 172306.09 | 43439.17 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 301948.93 | 241153.1 | 60795.83 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 69085.41 | 51973.82 | 17111.6 | 0.75 | 4.05
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 91323.53 | 61742.31 | 29581.22 | 0.68 | 3.53
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 100542.24 | 67974.92 | 32567.32 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 59049.47 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 130104.02 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 124629.12 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.14 | 36826.67 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.04 | 29952.22 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.03 | 29932.18 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.24 | 41623.41 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.65 | 6957.14 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.68 | 7014.77 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.05 | 7595.58 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7241.13 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 71640.1237 | 121.1408 | 275.3793 | 0 | 0.001 | 489691.8325 | 29976.9729
February | 63135.2309 | 108.3333 | 250.4027 | 0 | 0.0009 | 445295.6641 | 26563.5574
March | 69552.9146 | 126.3351 | 310.1204 | 0 | 0.0011 | 551571.8236 | 29909.2617
April | 65735.1916 | 122.6166 | 308.8631 | 0 | 0.0011 | 549367.9847 | 28564.5642
May | 73789.4693 | 139.4658 | 355.655 | 0 | 0.0013 | 632613.1827 | 32233.0479
June | 77957.6943 | 148.4453 | 381.1444 | 0 | 0.0014 | 677962.1524 | 34155.5482
July | 61632.1944 | 116.5171 | 297.2015 | 0 | 0.0011 | 528640.6895 | 26925.1447
August | 65484.1917 | 123.5722 | 314.6632 | 0 | 0.0012 | 559698.1687 | 28586.9851
September | 73281.9015 | 139.3189 | 357.1913 | 0 | 0.0013 | 635353.4605 | 32086.3628
October | 68392.0526 | 127.589 | 321.4275 | 0 | 0.0012 | 571716.1198 | 29720.5996
November | 65213.4605 | 117.3772 | 285.4982 | 0 | 0.0011 | 507768.5672 | 27943.8501
December | 67139.9798 | 116.0897 | 270.6227 | 0 | 0.001 | 481263.2751 | 28330.2183
Annual Sum or Average | 822954.405 | 1506.8011 | 3728.1694 | 0 | 0.0138 | 6630940 | 354996.1128
Minimum of Months | 61632.1944 | 108.3333 | 250.4027 | 0 | 0.0009 | 445295.6641 | 26563.5574
Maximum of Months | 77957.6943 | 148.4453 | 381.1444 | 0 | 0.0014 | 677962.1524 | 34155.5482
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 282352000000 | 248011.402 | 23-JAN-12:00 | 80532.756 | 81262.495 | 14980.305 | 0 | 68756.124 | 0 | 24.946 | 0 | 0 | 0 | 0 | 0 | 2454.776 | 0 | 0
February | 256753000000 | 253265.822 | 21-FEB-14:09 | 80532.756 | 77263.149 | 14921.178 | 0 | 78013.032 | 0 | 30.745 | 0 | 0 | 0 | 0 | 0 | 2504.962 | 0 | 0
March | 318031000000 | 272120.161 | 28-MAR-11:00 | 80532.756 | 81262.495 | 16431.087 | 0 | 91415.888 | 0 | 13.857 | 0 | 0 | 0 | 0 | 0 | 2464.079 | 0 | 0
April | 316760000000 | 299008.296 | 13-APR-11:00 | 80532.756 | 81262.495 | 17819.665 | 0 | 116910.143 | 0 | 5.168 | 0 | 0 | 0 | 0 | 0 | 2478.069 | 0 | 0
May | 364759000000 | 328105.194 | 22-MAY-13:00 | 80532.756 | 77263.149 | 20656.848 | 0 | 147087.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2565.333 | 0 | 0
June | 390907000000 | 351357.514 | 19-JUN-10:50 | 80532.756 | 81262.495 | 23094.723 | 0 | 162626.371 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 3841.157 | 0 | 0
July | 304809000000 | 306461.699 | 03-JUL-11:00 | 44740.42 | 47274.638 | 23228.272 | 0 | 188779.241 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2439.122 | 0 | 0
August | 322717000000 | 281457.363 | 17-AUG-11:00 | 44740.42 | 47274.638 | 20446.708 | 0 | 166622.769 | 0 | 1.464 | 0 | 0 | 0 | 0 | 0 | 2371.364 | 0 | 0
September | 366339000000 | 341425.799 | 11-SEP-13:00 | 80532.756 | 76410.953 | 22028.859 | 0 | 159885.622 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2567.607 | 0 | 0
October | 329646000000 | 301104.395 | 02-OCT-11:00 | 80532.756 | 80410.298 | 18339.608 | 0 | 119256.897 | 0 | 2.289 | 0 | 0 | 0 | 0 | 0 | 2562.548 | 0 | 0
November | 292775000000 | 273626.467 | 22-NOV-11:50 | 80532.756 | 80410.298 | 16263.798 | 0 | 92664.24 | 0 | 19.317 | 0 | 0 | 0 | 0 | 0 | 3736.058 | 0 | 0
December | 277492000000 | 263683.027 | 26-DEC-11:50 | 80532.756 | 80410.298 | 14984.994 | 0 | 83970.806 | 0 | 62.481 | 0 | 0 | 0 | 0 | 0 | 3721.692 | 0 | 0
Annual Sum or Average | 3823340000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 256753000000 | 248011.402 |  | 44740.42 | 47274.638 | 14921.178 | 0 | 68756.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2371.364 | 0 | 0
Maximum of Months | 390907000000 | 351357.514 |  | 80532.756 | 81262.495 | 23228.272 | 0 | 188779.241 | 0 | 62.481 | 0 | 0 | 0 | 0 | 0 | 3841.157 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 104011.35 | 15522.54 | 0 | 119533.88
Cost per Total Building Area ($/m2) | 15.14 | 2.26 | 0 | 17.4
Cost per Net Conditioned Building Area ($/m2) | 15.14 | 2.26 | 0 | 17.4

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4429.17 | 644.62 | 644.62
Net Site Energy | 4429.17 | 644.62 | 644.62
Total Source Energy | 11838.03 | 1722.9 | 1722.9
Net Source Energy | 11838.03 | 1722.9 | 1722.9
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 466.1 | 0 | 0 | 0 | 0
Cooling | 670.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 193.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0.45 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 106.59 | 0 | 0 | 0 | 921.12
Refrigeration | 79.73 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3495.45 | 933.72 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 49 | 49 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.402 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 26.6 | 26.6 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 14 | 14 | 3.18 | 0.262 | 0.318 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 11.2 | 11.2 | 3.18 | 0.262 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 21 | 21 | 3.18 | 0.262 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.402 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.402 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.23 | 0.314 | 0.431
North Total or Average |  |  | 324.79 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.26 | 0.264 | 0.322
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1086550.11 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 239791.01 | 191510.35 | 48280.66 | 0.8 | 4.59
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 190974.31 | 152522.63 | 38451.67 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 194575.86 | 155399.03 | 39176.83 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 268244.54 | 214234.91 | 54009.63 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52906.1 | 42253.73 | 10652.36 | 0.8 | 3.47
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 56446.26 | 45081.1 | 11365.16 | 0.8 | 3.47
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 56331.82 | 44989.71 | 11342.12 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 43125.13 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 95017.83 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 91019.4 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 14.49 | 33268.25 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 11.54 | 26495.5 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 11.75 | 26995.17 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.2 | 36977.29 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.2 | 3495.29 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.41 | 3729.18 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.4 | 3721.62 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6037.4 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29806.6469 | 25.8244 | 221.3269 | 0 | 0.0001 | 1335260 | 10991.3904
February | 26268.639 | 22.7452 | 197.5407 | 0 | 0.0001 | 1191770 | 9694.309
March | 30942.2521 | 26.76 | 238.4064 | 0 | 0.0001 | 1438340 | 11436.5341
April | 28485.4636 | 24.582 | 229.0009 | 0 | 0.0001 | 1381630 | 10557.5397
May | 31483.6832 | 27.1274 | 260.6244 | 0 | 0.0001 | 1572460 | 11691.7106
June | 31373.5686 | 27.0075 | 264.1907 | 0 | 0.0001 | 1593990 | 11664.4801
July | 24947.7199 | 21.5163 | 202.8422 | 0 | 0.0001 | 1223820 | 9253.3114
August | 27412.832 | 23.629 | 225.2861 | 0 | 0.0001 | 1359240 | 10174.9661
September | 30257.8392 | 26.0118 | 261.0965 | 0 | 0.0001 | 1575350 | 11268.8842
October | 30988.0772 | 26.6704 | 261.8707 | 0 | 0.0001 | 1580000 | 11523.9828
November | 30315.2087 | 26.1805 | 240.2363 | 0 | 0.0001 | 1449410 | 11225.0963
December | 29315.244 | 25.3678 | 223.1966 | 0 | 0.0001 | 1346570 | 10827.0192
Annual Sum or Average | 351597.1744 | 303.4222 | 2825.6186 | 0 | 0.0014 | 17047800 | 130309.2239
Minimum of Months | 24947.7199 | 21.5163 | 197.5407 | 0 | 0.0001 | 1191770 | 9253.3114
Maximum of Months | 31483.6832 | 27.1274 | 264.1907 | 0 | 0.0001 | 1593990 | 11691.7106
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 273779000000 | 263263.473 | 26-JAN-12:00 | 80532.756 | 81262.495 | 14459.375 | 0 | 84546.89 | 0 | 4.872 | 0 | 0 | 0 | 0 | 0 | 2457.086 | 0 | 0
February | 244358000000 | 262741.748 | 13-FEB-11:50 | 80532.756 | 81262.495 | 14403.541 | 0 | 82695.781 | 0 | 5.509 | 0 | 0 | 0 | 0 | 0 | 3841.666 | 0 | 0
March | 294914000000 | 257721.007 | 31-MAR-10:50 | 80532.756 | 81262.495 | 14490.651 | 0 | 77691.104 | 0 | 7.351 | 0 | 0 | 0 | 0 | 0 | 3736.65 | 0 | 0
April | 283287000000 | 274134.853 | 11-APR-13:00 | 80532.756 | 77263.149 | 14250.015 | 0 | 99524.02 | 0 | 1.986 | 0 | 0 | 0 | 0 | 0 | 2562.926 | 0 | 0
May | 322413000000 | 294021.953 | 30-MAY-10:50 | 80532.756 | 81262.495 | 15913.142 | 0 | 112469.73 | 0 | 2.106 | 0 | 0 | 0 | 0 | 0 | 3841.724 | 0 | 0
June | 326828000000 | 283789.263 | 23-JUN-10:50 | 80532.756 | 81262.495 | 15188.836 | 0 | 102953.731 | 0 | 9.558 | 0 | 0 | 0 | 0 | 0 | 3841.887 | 0 | 0
July | 250929000000 | 214364.102 | 24-JUL-10:39 | 44740.42 | 47274.638 | 14621.27 | 0 | 103980.423 | 0 | 1.826 | 0 | 0 | 0 | 0 | 0 | 3745.526 | 0 | 0
August | 278695000000 | 231929.856 | 08-AUG-10:39 | 44740.42 | 47274.638 | 15129.672 | 0 | 121037.492 | 0 | 2.559 | 0 | 0 | 0 | 0 | 0 | 3745.075 | 0 | 0
September | 323005000000 | 295534.05 | 25-SEP-11:00 | 80532.756 | 80410.298 | 16932.043 | 0 | 115094.871 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2564.073 | 0 | 0
October | 323959000000 | 285228.416 | 05-OCT-10:50 | 80532.756 | 80410.298 | 15312.253 | 0 | 105194.18 | 0 | 2.85 | 0 | 0 | 0 | 0 | 0 | 3776.079 | 0 | 0
November | 297183000000 | 270152.032 | 07-NOV-12:00 | 80532.756 | 80410.298 | 15557.078 | 0 | 91084.113 | 0 | 4.759 | 0 | 0 | 0 | 0 | 0 | 2563.028 | 0 | 0
December | 276097000000 | 264346.679 | 19-DEC-12:00 | 80532.756 | 80410.298 | 14532.141 | 0 | 86409.625 | 0 | 4.834 | 0 | 0 | 0 | 0 | 0 | 2457.025 | 0 | 0
Annual Sum or Average | 3495450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 244358000000 | 214364.102 |  | 44740.42 | 47274.638 | 14250.015 | 0 | 77691.104 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2457.025 | 0 | 0
Maximum of Months | 326828000000 | 295534.05 |  | 80532.756 | 81262.495 | 16932.043 | 0 | 121037.492 | 0 | 9.558 | 0 | 0 | 0 | 0 | 0 | 3841.887 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 125082.09 | 7909.2 | 0 | 132991.29
Cost per Total Building Area ($/m2) | 18.2 | 1.15 | 0 | 19.36
Cost per Net Conditioned Building Area ($/m2) | 18.2 | 1.15 | 0 | 19.36

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5056.3 | 735.89 | 735.89
Net Site Energy | 5056.3 | 735.89 | 735.89
Total Source Energy | 14972.94 | 2179.15 | 2179.15
Net Source Energy | 14972.94 | 2179.15 | 2179.15
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 794.36 | 0 | 0 | 0 | 0
Cooling | 906 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 267.14 | 0 | 0 | 0 | 0 | 0
Pumps | 0.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 97.5 | 0 | 0 | 0 | 921.12
Refrigeration | 78.56 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3803.41 | 1252.89 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 49 | 49 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.402 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 26.6 | 26.6 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 14 | 14 | 3.18 | 0.262 | 0.318 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 11.2 | 11.2 | 3.18 | 0.262 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 21 | 21 | 3.18 | 0.262 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.402 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 29.4 | 29.4 | 3.18 | 0.262 | 0.318 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.402 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.23 | 0.314 | 0.431
North Total or Average |  |  | 324.79 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.26 | 0.264 | 0.322
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1269129.42 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 291415.69 | 232740.68 | 58675.02 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 234063.5 | 186936.05 | 47127.46 | 0.8 | 4.59
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 234774.76 | 187504.09 | 47270.66 | 0.8 | 4.58
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 318290.61 | 254204.47 | 64086.14 | 0.8 | 4.54
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 62853.13 | 50197.98 | 12655.15 | 0.8 | 4.37
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 72060.04 | 53922.91 | 18137.13 | 0.75 | 3.9
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 73242.49 | 57663.93 | 15578.56 | 0.79 | 4.11
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 49925.23 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 110000.52 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 105371.6 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.6 | 40171.42 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 14.14 | 32473.63 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 14.18 | 32572.31 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.23 | 43642.97 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.8 | 7242.43 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.76 | 7166.2 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.29 | 8044.13 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7051.9 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 72046.0747 | 108.4869 | 405.2784 | 0 | 0.0008 | 2020900 | 29413.8842
February | 62524.6595 | 97.046 | 378.9427 | 0 | 0.0007 | 1889700 | 25827.6768
March | 74122.0435 | 115.6255 | 454.6719 | 0 | 0.0009 | 2267370 | 30678.4902
April | 72124.9185 | 115.6367 | 471.8086 | 0 | 0.0009 | 2352950 | 30176.8627
May | 82695.1109 | 133.699 | 551.4375 | 0 | 0.001 | 2750100 | 34715.3278
June | 93128.4324 | 151.2802 | 627.7109 | 0 | 0.0012 | 3130520 | 39169.3221
July | 75048.758 | 121.7283 | 504.1304 | 0 | 0.0009 | 2514190 | 31546.1029
August | 78994.2889 | 127.8325 | 527.8578 | 0 | 0.001 | 2632510 | 33173.8743
September | 82792.7647 | 134.29 | 556.1592 | 0 | 0.001 | 2773670 | 34801.3349
October | 77440.4662 | 124.4738 | 509.5397 | 0 | 0.001 | 2541130 | 32433.5952
November | 69305.8292 | 108.1778 | 425.7418 | 0 | 0.0008 | 2123100 | 28691.8789
December | 69028.0628 | 105.0445 | 398.6604 | 0 | 0.0008 | 1987940 | 28296.2875
Annual Sum or Average | 909251.4093 | 1443.3211 | 5811.9394 | 0 | 0.011 | 28984100 | 378924.6375
Minimum of Months | 62524.6595 | 97.046 | 378.9427 | 0 | 0.0007 | 1889700 | 25827.6768
Maximum of Months | 93128.4324 | 151.2802 | 627.7109 | 0 | 0.0012 | 3130520 | 39169.3221
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 265190000000 | 249261.039 | 18-JAN-14:50 | 80532.756 | 77263.149 | 29340.707 | 0 | 59610.621 | 0 | 14.226 | 0 | 0 | 0 | 0 | 0 | 2499.58 | 0 | 0
February | 247974000000 | 251942.838 | 08-FEB-14:00 | 80532.756 | 77263.149 | 22267.13 | 0 | 69374.067 | 0 | 7.105 | 0 | 0 | 0 | 0 | 0 | 2498.631 | 0 | 0
March | 297533000000 | 260998.745 | 31-MAR-13:00 | 80532.756 | 77263.149 | 18271.437 | 0 | 82426.907 | 0 | 4.239 | 0 | 0 | 0 | 0 | 0 | 2500.256 | 0 | 0
April | 308763000000 | 304808.575 | 28-APR-13:00 | 80532.756 | 77263.149 | 23387.967 | 0 | 121105.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2519.67 | 0 | 0
May | 360880000000 | 338333.878 | 31-MAY-15:00 | 80532.756 | 75263.477 | 26785.596 | 0 | 153359.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2392.329 | 0 | 0
June | 410799000000 | 400724.673 | 27-JUN-15:00 | 80532.756 | 75263.477 | 29876.585 | 0 | 212656.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2394.88 | 0 | 0
July | 329922000000 | 309343.525 | 24-JUL-15:00 | 44740.42 | 41275.62 | 27170.889 | 0 | 193723.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2432.765 | 0 | 0
August | 345449000000 | 309460.393 | 03-AUG-11:00 | 44740.42 | 47274.638 | 27465.847 | 0 | 187610.002 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2369.479 | 0 | 0
September | 363972000000 | 338144.903 | 21-SEP-13:00 | 80532.756 | 76410.953 | 26673.976 | 0 | 152013.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2513.616 | 0 | 0
October | 333457000000 | 313846.166 | 06-OCT-13:09 | 80532.756 | 76410.953 | 23145.654 | 0 | 131215.702 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2541.099 | 0 | 0
November | 278602000000 | 258759.403 | 10-NOV-12:39 | 80532.756 | 80410.298 | 23326.571 | 0 | 72027.022 | 0 | 11.662 | 0 | 0 | 0 | 0 | 0 | 2451.094 | 0 | 0
December | 260866000000 | 254906.184 | 05-DEC-12:00 | 80532.756 | 80410.298 | 21719.111 | 0 | 69771.619 | 0 | 22.464 | 0 | 0 | 0 | 0 | 0 | 2449.935 | 0 | 0
Annual Sum or Average | 3803410000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 247974000000 | 249261.039 |  | 44740.42 | 41275.62 | 18271.437 | 0 | 59610.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2369.479 | 0 | 0
Maximum of Months | 410799000000 | 400724.673 |  | 80532.756 | 80410.298 | 29876.585 | 0 | 212656.975 | 0 | 22.464 | 0 | 0 | 0 | 0 | 0 | 2541.099 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 105847.83 | 9873.89 | 0 | 115721.72
Cost per Total Building Area ($/m2) | 15.41 | 1.44 | 0 | 16.84
Cost per Net Conditioned Building Area ($/m2) | 15.41 | 1.44 | 0 | 16.84

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5560.86 | 809.32 | 809.32
Net Site Energy | 5560.86 | 809.32 | 809.32
Total Source Energy | 12693.91 | 1847.46 | 1847.46
Net Source Energy | 12693.91 | 1847.46 | 1847.46
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1770.29 | 0 | 0 | 0 | 0
Cooling | 427 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 247.86 | 0 | 0 | 0 | 0 | 0
Pumps | 1.69 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 123.77 | 0 | 0 | 0 | 921.12
Refrigeration | 78.27 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3305.77 | 2255.1 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 12.6 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 4.2 | 4.2 | 6.49 | 0.34 | 0.34 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 12.6 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 12.6 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 4.2 | 4.2 | 6.49 | 0.34 | 0.34 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 12.6 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 12.6 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 4.2 | 4.2 | 6.49 | 0.34 | 0.34 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 12.6 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 49 | 49 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 25.2 | 25.2 | 6.49 | 0.61 | 0.61 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 12.6 | 12.6 | 6.49 | 0.34 | 0.34 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 26.6 | 26.6 | 6.49 | 0.34 | 0.34 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_WEST | 14 | 14 | 6.49 | 0.34 | 0.34 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 29.4 | 29.4 | 6.49 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 29.4 | 29.4 | 6.49 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 23.8 | 23.8 | 6.49 | 0.34 | 0.34 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 11.2 | 11.2 | 6.49 | 0.34 | 0.34 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 21 | 21 | 6.49 | 0.34 | 0.34 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 29.4 | 29.4 | 6.49 | 0.61 | 0.61 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34_EAST | 29.4 | 29.4 | 6.49 | 0.34 | 0.34 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 26.6 | 26.6 | 6.49 | 0.61 | 0.61 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 6.49 | 0.442 | 0.445
North Total or Average |  |  | 324.79 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 567.77 | 6.49 | 0.347 | 0.35
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1402444.15 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 327864.06 | 261850.36 | 66013.7 | 0.8 | 4.54
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 260928.42 | 208391.86 | 52536.57 | 0.8 | 4.56
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 265600.11 | 212122.93 | 53477.19 | 0.8 | 4.56
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 302792.91 | 241827.15 | 60965.76 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67021.53 | 53527.1 | 13494.43 | 0.8 | 4.32
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 63784.4 | 50941.75 | 12842.65 | 0.8 | 4.36
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 92277.07 | 73697.57 | 18579.5 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 47667.53 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 105026.11 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 100606.52 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.81 | 44955.65 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 15.76 | 35968.77 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.04 | 36612.76 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.29 | 41739.76 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.05 | 7595.45 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.85 | 7349.74 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.57 | 10457.63 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7792.66 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37128.223 | 32.5363 | 209.7555 | 0 | 0.0001 | 1265180 | 13490.0963
February | 30569.5578 | 26.6465 | 198.1684 | 0 | 0.0001 | 1195430 | 11184.7794
March | 35676.2669 | 31.1424 | 223.2933 | 0 | 0.0001 | 1346950 | 13028.8752
April | 31646.7462 | 27.5211 | 216.6679 | 0 | 0.0001 | 1307080 | 11614.0374
May | 34771.49 | 30.1606 | 251.9885 | 0 | 0.0001 | 1520220 | 12803.2781
June | 34419.4833 | 29.8494 | 250.491 | 0 | 0.0001 | 1511190 | 12676.8792
July | 29592.2272 | 25.8277 | 185.9081 | 0 | 0.0001 | 1121440 | 10809.118
August | 33475.3983 | 29.2473 | 204.8606 | 0 | 0.0001 | 1235740 | 12210.9133
September | 33527.8715 | 29.0145 | 255.044 | 0 | 0.0001 | 1538700 | 12382.1819
October | 34287.4038 | 29.7273 | 250.8869 | 0 | 0.0001 | 1513580 | 12632.3741
November | 34102.6372 | 29.7197 | 222.2251 | 0 | 0.0001 | 1340550 | 12480.9801
December | 34804.092 | 30.462 | 203.3661 | 0 | 0.0001 | 1226680 | 12666.2168
Annual Sum or Average | 404001.3974 | 351.8548 | 2672.6555 | 0 | 0.0014 | 16122700 | 147979.7299
Minimum of Months | 29592.2272 | 25.8277 | 185.9081 | 0 | 0.0001 | 1121440 | 10809.118
Maximum of Months | 37128.223 | 32.5363 | 255.044 | 0 | 0.0001 | 1538700 | 13490.0963
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 259409000000 | 219301.625 | 06-JAN-15:00 | 80532.756 | 75263.477 | 17022.573 | 0 | 43959.04 | 0 | 33.987 | 0 | 0 | 0 | 0 | 0 | 2489.793 | 0 | 0
February | 245108000000 | 282063.435 | 15-FEB-14:00 | 80532.756 | 77263.149 | 32797.843 | 0 | 88914.941 | 0 | 5.879 | 0 | 0 | 0 | 0 | 0 | 2548.866 | 0 | 0
March | 276176000000 | 257932.894 | 01-MAR-12:00 | 80532.756 | 81262.495 | 22328.67 | 0 | 71282.509 | 0 | 28.348 | 0 | 0 | 0 | 0 | 0 | 2498.118 | 0 | 0
April | 268000000000 | 280554.102 | 28-APR-11:50 | 80532.756 | 81262.495 | 29380.917 | 0 | 86857.846 | 0 | 18.409 | 0 | 0 | 0 | 0 | 0 | 2501.679 | 0 | 0
May | 311702000000 | 298834.841 | 25-MAY-11:00 | 80532.756 | 81262.495 | 27422.649 | 0 | 107079.382 | 0 | 13.732 | 0 | 0 | 0 | 0 | 0 | 2523.827 | 0 | 0
June | 309850000000 | 292924.951 | 16-JUN-10:50 | 80532.756 | 81262.495 | 20999.894 | 0 | 106327.83 | 0 | 41.57 | 0 | 0 | 0 | 0 | 0 | 3760.407 | 0 | 0
July | 229937000000 | 230701.883 | 03-JUL-11:00 | 44740.42 | 47274.638 | 19969.057 | 0 | 116267.156 | 0 | 18.101 | 0 | 0 | 0 | 0 | 0 | 2432.511 | 0 | 0
August | 253373000000 | 226306.079 | 15-AUG-11:00 | 44740.42 | 47274.638 | 18626.03 | 0 | 113300.799 | 0 | 56.841 | 0 | 0 | 0 | 0 | 0 | 2307.351 | 0 | 0
September | 315492000000 | 326231.616 | 28-SEP-15:09 | 80532.756 | 75197.923 | 24745.086 | 0 | 143347.097 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2408.75 | 0 | 0
October | 310341000000 | 290883.909 | 17-OCT-11:50 | 80532.756 | 80410.298 | 28640.649 | 0 | 98768.097 | 0 | 13.807 | 0 | 0 | 0 | 0 | 0 | 2518.303 | 0 | 0
November | 274864000000 | 252024.538 | 06-NOV-12:00 | 80532.756 | 80410.298 | 21305.454 | 0 | 67224.788 | 0 | 59.623 | 0 | 0 | 0 | 0 | 0 | 2491.62 | 0 | 0
December | 251515000000 | 222716.953 | 07-DEC-14:00 | 80532.756 | 76410.953 | 18534.801 | 0 | 44684.567 | 0 | 31.658 | 0 | 0 | 0 | 0 | 0 | 2522.218 | 0 | 0
Annual Sum or Average | 3305770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 229937000000 | 219301.625 |  | 44740.42 | 47274.638 | 17022.573 | 0 | 43959.04 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2307.351 | 0 | 0
Maximum of Months | 315492000000 | 326231.616 |  | 80532.756 | 81262.495 | 32797.843 | 0 | 143347.097 | 0 | 59.623 | 0 | 0 | 0 | 0 | 0 | 3760.407 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 137396.67 | 19091.93 | 0 | 156488.6
Cost per Total Building Area ($/m2) | 20 | 2.78 | 0 | 22.78
Cost per Net Conditioned Building Area ($/m2) | 20 | 2.78 | 0 | 22.78

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6076.12 | 884.31 | 884.31
Net Site Energy | 6076.12 | 884.31 | 884.31
Total Source Energy | 15832.8 | 2304.29 | 2304.29
Net Source Energy | 15832.8 | 2304.29 | 2304.29
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1882.78 | 0 | 0 | 0 | 0
Cooling | 848.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.65 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 223.56 | 0 | 0 | 0 | 0 | 0
Pumps | 1.9 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 129.53 | 0 | 0 | 0 | 921.12
Refrigeration | 78.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3702.77 | 2373.34 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 49 | 49 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.501 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 26.6 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 14 | 3.18 | 0.402 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 11.2 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 21 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.439 | 0.543
North Total or Average |  |  | 324.79 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.404 | 0.498
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1409547.19 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 277376.07 | 221527.85 | 55848.21 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 219767.68 | 175518.61 | 44249.07 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 223803.2 | 178741.6 | 45061.6 | 0.8 | 4.59
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 303197.39 | 242150.19 | 61047.2 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 69992.38 | 52658.16 | 17334.22 | 0.75 | 4.05
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 88714.08 | 59978.1 | 28735.98 | 0.68 | 3.52
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 96782.21 | 65432.83 | 31349.38 | 0.68 | 3.53
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 65732.64 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 144829.08 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 138734.54 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.76 | 38236.06 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.28 | 30490.25 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.52 | 31050.13 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.32 | 41795.51 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.7 | 7049.11 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.57 | 6814.33 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.9 | 7434.06 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7832.13 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 75313.6063 | 119.1504 | 280.7471 | 0 | 0.0012 | 17451.9273 | 30710.1028
February | 61234.0525 | 101.0397 | 251.2543 | 0 | 0.0011 | 15620.5593 | 25349.7237
March | 62680.4899 | 111.289 | 300.6032 | 0 | 0.0012 | 18691.9814 | 26667.4545
April | 55562.5195 | 103.4555 | 292.9948 | 0 | 0.0012 | 18220.651 | 24078.4127
May | 62569.4221 | 119.779 | 348.0376 | 0 | 0.0014 | 21644.7286 | 27414.5344
June | 68282.6466 | 133.8068 | 396.8824 | 0 | 0.0016 | 24683.4076 | 30200.3637
July | 54538.9133 | 106.0629 | 312.5178 | 0 | 0.0013 | 19436.2509 | 24047.5121
August | 58792.2551 | 114.0399 | 335.2634 | 0 | 0.0014 | 20850.7676 | 25895.973
September | 60552.4589 | 117.6814 | 346.5554 | 0 | 0.0014 | 21553.1117 | 26692.0555
October | 60515.781 | 113.979 | 326.2965 | 0 | 0.0013 | 20292.0413 | 26343.8767
November | 60129.6359 | 107.8369 | 294.3162 | 0 | 0.0012 | 18301.441 | 25680.6637
December | 65915.4341 | 108.6403 | 269.7783 | 0 | 0.0011 | 16772.1471 | 27276.3894
Annual Sum or Average | 746087.2151 | 1356.7608 | 3755.2468 | 0 | 0.0154 | 233519.0149 | 320357.062
Minimum of Months | 54538.9133 | 101.0397 | 251.2543 | 0 | 0.0011 | 15620.5593 | 24047.5121
Maximum of Months | 75313.6063 | 133.8068 | 396.8824 | 0 | 0.0016 | 24683.4076 | 30710.1028
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 276725000000 | 249471.267 | 09-JAN-11:50 | 80532.756 | 81262.495 | 15013.16 | 0 | 68854.533 | 0 | 72.122 | 0 | 0 | 0 | 0 | 0 | 3736.202 | 0 | 0
February | 247686000000 | 233297.26 | 15-FEB-12:00 | 80532.756 | 81262.495 | 14555.04 | 0 | 54437.433 | 0 | 59.106 | 0 | 0 | 0 | 0 | 0 | 2450.43 | 0 | 0
March | 296388000000 | 286941.886 | 09-MAR-13:00 | 80532.756 | 77263.149 | 16429.575 | 0 | 110196.565 | 0 | 16.167 | 0 | 0 | 0 | 0 | 0 | 2503.673 | 0 | 0
April | 288914000000 | 283382.529 | 04-APR-11:00 | 80532.756 | 81262.495 | 16868.672 | 0 | 102233.16 | 0 | 17.088 | 0 | 0 | 0 | 0 | 0 | 2468.359 | 0 | 0
May | 343208000000 | 330702.874 | 16-MAY-10:39 | 80532.756 | 81262.495 | 20084.638 | 0 | 144976.688 | 0 | 4.884 | 0 | 0 | 0 | 0 | 0 | 3841.413 | 0 | 0
June | 391390000000 | 384935.448 | 30-JUN-13:00 | 80532.756 | 77263.149 | 24996.928 | 0 | 199571.707 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2570.902 | 0 | 0
July | 308189000000 | 332514.413 | 25-JUL-11:00 | 44740.42 | 47274.638 | 25444.347 | 0 | 212612.607 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2442.399 | 0 | 0
August | 330618000000 | 328194.364 | 09-AUG-14:00 | 44740.42 | 41275.62 | 25450.715 | 0 | 214284.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2443.198 | 0 | 0
September | 341755000000 | 335215.183 | 05-SEP-10:39 | 80532.756 | 80410.298 | 21225.036 | 0 | 149200.844 | 0 | 4.864 | 0 | 0 | 0 | 0 | 0 | 3841.386 | 0 | 0
October | 321759000000 | 320788.929 | 03-OCT-10:39 | 80532.756 | 80410.298 | 19488.012 | 0 | 136511.488 | 0 | 4.898 | 0 | 0 | 0 | 0 | 0 | 3841.478 | 0 | 0
November | 290195000000 | 296074.355 | 03-NOV-11:50 | 80532.756 | 80410.298 | 17426.672 | 0 | 113937.189 | 0 | 15.11 | 0 | 0 | 0 | 0 | 0 | 3752.33 | 0 | 0
December | 265946000000 | 213645.388 | 08-DEC-10:00 | 80532.756 | 80410.298 | 14161.951 | 0 | 35983.067 | 0 | 82.763 | 0 | 0 | 0 | 0 | 0 | 2474.553 | 0 | 0
Annual Sum or Average | 3702770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 247686000000 | 213645.388 |  | 44740.42 | 41275.62 | 14161.951 | 0 | 35983.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2442.399 | 0 | 0
Maximum of Months | 391390000000 | 384935.448 |  | 80532.756 | 81262.495 | 25450.715 | 0 | 214284.41 | 0 | 82.763 | 0 | 0 | 0 | 0 | 0 | 3841.478 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 80957.72 | 23273.96 | 0 | 104231.68
Cost per Total Building Area ($/m2) | 11.78 | 3.39 | 0 | 15.17
Cost per Net Conditioned Building Area ($/m2) | 11.78 | 3.39 | 0 | 15.17

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5304.29 | 771.98 | 771.98
Net Site Energy | 5304.29 | 771.98 | 771.98
Total Source Energy | 13619.09 | 1982.11 | 1982.11
Net Source Energy | 13619.09 | 1982.11 | 1982.11
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1300.74 | 0 | 0 | 0 | 0
Cooling | 606.73 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.68 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 279.2 | 0 | 0 | 0 | 0 | 0
Pumps | 1.27 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 126.44 | 0 | 0 | 0 | 921.12
Refrigeration | 77.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3516.08 | 1788.21 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 49 | 49 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.501 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 26.6 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 14 | 3.18 | 0.402 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 11.2 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 21 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.439 | 0.543
North Total or Average |  |  | 324.79 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.404 | 0.498
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1259583.49 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 313344.21 | 250254 | 63090.21 | 0.8 | 4.54
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 247690.59 | 197819.39 | 49871.2 | 0.8 | 4.58
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 251865.21 | 201153.47 | 50711.74 | 0.8 | 4.59
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 341001.23 | 272342.42 | 68658.8 | 0.8 | 4.54
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70249.6 | 56105.21 | 14144.39 | 0.8 | 4.32
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68859.31 | 54994.85 | 13864.46 | 0.8 | 4.32
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 75352.51 | 60180.68 | 15171.83 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 52228.2 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 115074.66 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 110232.22 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.93 | 42964.73 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 14.96 | 34364.23 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 15.22 | 34943.41 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 20.6 | 46756.97 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.24 | 7961.29 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.16 | 7803.73 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.55 | 8539.59 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6998.85 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 88636.1489 | 140.7855 | 326.9135 | 0 | 0.0013 | 339846.5854 | 36594.8158
February | 75389.9412 | 122.4074 | 292.4636 | 0 | 0.0012 | 304054.7175 | 31386.9814
March | 85145.7413 | 140.7126 | 343.6525 | 0 | 0.0014 | 357290.8075 | 35690.4071
April | 77260.2323 | 130.719 | 328.2695 | 0 | 0.0013 | 341319.1139 | 32683.0482
May | 93581.1398 | 161.3924 | 414.1754 | 0 | 0.0016 | 430660.8482 | 39887.3258
June | 99650.294 | 172.804 | 446.1487 | 0 | 0.0017 | 463913.0179 | 42566.8442
July | 78513.9327 | 135.6479 | 348.7936 | 0 | 0.0014 | 362678.2551 | 33488.8116
August | 82542.5755 | 142.0554 | 363.6984 | 0 | 0.0014 | 378172.7799 | 35152.9352
September | 90661.1108 | 156.8678 | 404.0192 | 0 | 0.0016 | 420103.7796 | 38692.8676
October | 82959.6124 | 140.7087 | 354.3622 | 0 | 0.0014 | 368451.4643 | 35128.043
November | 81047.1073 | 133.1213 | 322.6834 | 0 | 0.0013 | 335483.6537 | 33892.1634
December | 87430.5333 | 138.472 | 320.3096 | 0 | 0.0013 | 332978.2936 | 36057.9629
Annual Sum or Average | 1022820 | 1715.6938 | 4265.4896 | 0 | 0.0168 | 4434950 | 431222.2061
Minimum of Months | 75389.9412 | 122.4074 | 292.4636 | 0 | 0.0012 | 304054.7175 | 31386.9814
Maximum of Months | 99650.294 | 172.804 | 446.1487 | 0 | 0.0017 | 463913.0179 | 42566.8442
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 269434000000 | 214030.376 | 25-JAN-14:00 | 80532.756 | 77263.149 | 20396.597 | 0 | 33327.592 | 0 | 11.175 | 0 | 0 | 0 | 0 | 0 | 2499.106 | 0 | 0
February | 241058000000 | 250722.44 | 14-FEB-15:20 | 80532.756 | 75263.477 | 29702.823 | 0 | 62732.268 | 0 | 5.585 | 0 | 0 | 0 | 0 | 0 | 2485.532 | 0 | 0
March | 283264000000 | 252411.036 | 02-MAR-13:50 | 80532.756 | 77263.149 | 24526.023 | 0 | 67594.764 | 0 | 8.07 | 0 | 0 | 0 | 0 | 0 | 2486.274 | 0 | 0
April | 270602000000 | 270725.775 | 21-APR-13:00 | 80532.756 | 77263.149 | 21240.715 | 0 | 89188.554 | 0 | 1.368 | 0 | 0 | 0 | 0 | 0 | 2499.233 | 0 | 0
May | 341433000000 | 299591.51 | 30-MAY-13:00 | 80532.756 | 77263.149 | 24485.594 | 0 | 114789.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2520.078 | 0 | 0
June | 367796000000 | 329788.175 | 29-JUN-13:00 | 80532.756 | 77263.149 | 27680.955 | 0 | 141778.003 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2533.309 | 0 | 0
July | 287536000000 | 261436.681 | 31-JUL-14:00 | 44740.42 | 41275.62 | 28121.573 | 0 | 144868.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2430.772 | 0 | 0
August | 299820000000 | 265336.776 | 01-AUG-13:00 | 44740.42 | 43275.293 | 25251.307 | 0 | 149685.418 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2384.333 | 0 | 0
September | 333063000000 | 305404.248 | 05-SEP-11:39 | 80532.756 | 80410.298 | 21857.715 | 0 | 120035.943 | 0 | 2.984 | 0 | 0 | 0 | 0 | 0 | 2564.552 | 0 | 0
October | 292113000000 | 281676.969 | 03-OCT-11:00 | 80532.756 | 80410.298 | 20829.055 | 0 | 97426.657 | 0 | 3.89 | 0 | 0 | 0 | 0 | 0 | 2474.312 | 0 | 0
November | 265975000000 | 248277.627 | 08-NOV-14:50 | 80532.756 | 76410.953 | 31722.427 | 0 | 57106.444 | 0 | 5.855 | 0 | 0 | 0 | 0 | 0 | 2499.192 | 0 | 0
December | 263989000000 | 204470.603 | 08-DEC-14:00 | 80532.756 | 76410.953 | 19227.535 | 0 | 25784.031 | 0 | 16.33 | 0 | 0 | 0 | 0 | 0 | 2498.999 | 0 | 0
Annual Sum or Average | 3516080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 241058000000 | 204470.603 |  | 44740.42 | 41275.62 | 19227.535 | 0 | 25784.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2384.333 | 0 | 0
Maximum of Months | 367796000000 | 329788.175 |  | 80532.756 | 80410.298 | 31722.427 | 0 | 149685.418 | 0 | 16.33 | 0 | 0 | 0 | 0 | 0 | 2564.552 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 36259.57 | 12517.69 | 0 | 48777.26
Cost per Total Building Area ($/m2) | 5.28 | 1.82 | 0 | 7.1
Cost per Net Conditioned Building Area ($/m2) | 5.28 | 1.82 | 0 | 7.1

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5098.81 | 742.08 | 742.08
Net Site Energy | 5098.81 | 742.08 | 742.08
Total Source Energy | 7565.42 | 1101.07 | 1101.07
Net Source Energy | 7565.42 | 1101.07 | 1101.07
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1529.34 | 0 | 0 | 0 | 0
Cooling | 265.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.55 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 177.59 | 0 | 0 | 0 | 0 | 0
Pumps | 1.52 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 135.33 | 0 | 0 | 0 | 921.12
Refrigeration | 77.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3073.12 | 2025.69 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 49 | 49 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.501 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 26.6 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 14 | 3.18 | 0.402 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 11.2 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 21 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.439 | 0.543
North Total or Average |  |  | 324.79 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.404 | 0.498
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1205949.06 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 251577.74 | 200923.88 | 50653.85 | 0.8 | 4.59
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 193958.49 | 154905.97 | 39052.52 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 204050.43 | 162965.95 | 41084.48 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 256397.81 | 204773.46 | 51624.35 | 0.8 | 4.59
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 50594.07 | 40407.22 | 10186.85 | 0.8 | 3.47
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 55373.03 | 44223.96 | 11149.07 | 0.8 | 3.47
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52812.05 | 42178.62 | 10633.43 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 56846.24 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 125249.63 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 119979.01 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 15.2 | 34903.53 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 11.72 | 26909.52 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 12.33 | 28309.66 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 15.49 | 35572.26 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.06 | 3342.55 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.35 | 3658.27 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.19 | 3489.08 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6700.84 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 28162.2029 | 34.1075 | 54.671 | 0 | 0.0002 | 721581.64 | 10662.0652
February | 21418.1703 | 27.1164 | 49.0917 | 0 | 0.0002 | 648206.572 | 8234.8321
March | 24193.0173 | 30.8794 | 57.0469 | 0 | 0.0002 | 753294.1479 | 9328.4581
April | 19192.2885 | 25.6197 | 52.4265 | 0 | 0.0002 | 692488.6198 | 7520.5452
May | 18938.3467 | 26.5848 | 60.0594 | 0 | 0.0002 | 793517.4547 | 7560.7101
June | 18549.1694 | 26.7281 | 63.2279 | 0 | 0.0003 | 835475.2564 | 7479.1925
July | 15719.2444 | 21.8583 | 48.5246 | 0 | 0.0002 | 641088.9078 | 6253.3128
August | 17582.7847 | 24.1389 | 52.2932 | 0 | 0.0002 | 690834.5939 | 6961.3714
September | 18251.3285 | 25.8959 | 59.6394 | 0 | 0.0002 | 788006.3317 | 7315.9356
October | 20078.5343 | 27.0672 | 56.5358 | 0 | 0.0002 | 746810.2806 | 7896.1454
November | 23809.9207 | 29.9608 | 53.4005 | 0 | 0.0002 | 705064.4672 | 9134.7284
December | 27337.5532 | 33.1642 | 53.424 | 0 | 0.0002 | 705134.9382 | 10355.7927
Annual Sum or Average | 253232.561 | 333.1213 | 660.3409 | 0 | 0.0028 | 8721500 | 98703.0896
Minimum of Months | 15719.2444 | 21.8583 | 48.5246 | 0 | 0.0002 | 641088.9078 | 6253.3128
Maximum of Months | 28162.2029 | 34.1075 | 63.2279 | 0 | 0.0003 | 835475.2564 | 10662.0652
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 254257000000 | 178060.354 | 27-JAN-11:50 | 80532.756 | 81262.495 | 12437.005 | 0 | 0 | 0 | 90.987 | 0 | 0 | 0 | 0 | 0 | 3737.112 | 0 | 0
February | 228403000000 | 215129.823 | 21-FEB-13:00 | 80532.756 | 77263.149 | 14527.694 | 0 | 40295.334 | 0 | 15.824 | 0 | 0 | 0 | 0 | 0 | 2495.065 | 0 | 0
March | 265431000000 | 232465.236 | 29-MAR-15:00 | 80532.756 | 75263.477 | 18470.312 | 0 | 55801.331 | 0 | 1.867 | 0 | 0 | 0 | 0 | 0 | 2395.492 | 0 | 0
April | 244006000000 | 220514.49 | 14-APR-13:00 | 80532.756 | 77263.149 | 15995.177 | 0 | 44206.037 | 0 | 4.539 | 0 | 0 | 0 | 0 | 0 | 2512.831 | 0 | 0
May | 279604000000 | 264716.246 | 05-MAY-13:00 | 80532.756 | 77263.149 | 14061.297 | 0 | 90328.708 | 0 | 2.125 | 0 | 0 | 0 | 0 | 0 | 2528.21 | 0 | 0
June | 294389000000 | 270579.504 | 28-JUN-11:00 | 80532.756 | 81262.495 | 14781.504 | 0 | 91520.099 | 0 | 1.063 | 0 | 0 | 0 | 0 | 0 | 2481.587 | 0 | 0
July | 225895000000 | 209409.339 | 24-JUL-14:00 | 44740.42 | 41275.62 | 14198.351 | 0 | 106763.607 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2431.334 | 0 | 0
August | 243423000000 | 198532.474 | 07-AUG-14:00 | 44740.42 | 41275.62 | 13646.83 | 0 | 96439.199 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2430.404 | 0 | 0
September | 277663000000 | 271439.22 | 13-SEP-11:00 | 80532.756 | 80410.298 | 14551.258 | 0 | 93458.417 | 0 | 6.261 | 0 | 0 | 0 | 0 | 0 | 2480.23 | 0 | 0
October | 263147000000 | 245501.584 | 17-OCT-12:00 | 80532.756 | 76410.953 | 15798.6 | 0 | 70261.621 | 0 | 5.151 | 0 | 0 | 0 | 0 | 0 | 2492.504 | 0 | 0
November | 248437000000 | 220132.901 | 03-NOV-12:00 | 80532.756 | 80410.298 | 14174.599 | 0 | 42486.687 | 0 | 34.213 | 0 | 0 | 0 | 0 | 0 | 2494.347 | 0 | 0
December | 248462000000 | 180612.43 | 13-DEC-11:50 | 80532.756 | 80410.298 | 12212.887 | 0 | 3499.351 | 0 | 223.354 | 0 | 0 | 0 | 0 | 0 | 3733.784 | 0 | 0
Annual Sum or Average | 3073120000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 225895000000 | 178060.354 |  | 44740.42 | 41275.62 | 12212.887 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2395.492 | 0 | 0
Maximum of Months | 294389000000 | 271439.22 |  | 80532.756 | 81262.495 | 18470.312 | 0 | 106763.607 | 0 | 223.354 | 0 | 0 | 0 | 0 | 0 | 3737.112 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 64886.06 | 16934.97 | 0 | 81821.03
Cost per Total Building Area ($/m2) | 9.44 | 2.46 | 0 | 11.91
Cost per Net Conditioned Building Area ($/m2) | 9.44 | 2.46 | 0 | 11.91

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6600.85 | 960.68 | 960.68
Net Site Energy | 6600.85 | 960.68 | 960.68
Total Source Energy | 15688.42 | 2283.28 | 2283.28
Net Source Energy | 15688.42 | 2283.28 | 2283.28
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2640.84 | 0 | 0 | 0 | 0
Cooling | 579.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.66 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 245.3 | 0 | 0 | 0 | 0 | 0
Pumps | 2.79 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 143.29 | 0 | 0 | 0 | 921.12
Refrigeration | 77.28 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3455.7 | 3145.15 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 49 | 49 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.501 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 26.6 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 14 | 3.18 | 0.402 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 11.2 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 21 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.439 | 0.543
North Total or Average |  |  | 324.79 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.404 | 0.498
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1449619.76 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 267490.8 | 213632.93 | 53857.87 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 211799.45 | 169154.74 | 42644.7 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 216014.79 | 172521.34 | 43493.44 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 292152.83 | 233329.39 | 58823.43 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68427.32 | 51421.22 | 17006.1 | 0.75 | 4.04
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 88216.34 | 59641.59 | 28574.75 | 0.68 | 3.52
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 93676.8 | 63333.31 | 30343.49 | 0.68 | 3.52
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 76789.29 | 0.78
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 169190.26 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 162070.58 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.16 | 36873.39 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 12.79 | 29384.75 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.05 | 29969.57 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.65 | 40273.03 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.6 | 6872.85 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.55 | 6776.1 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.77 | 7195.53 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8054.79 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 131023.3168 | 203.5943 | 508.0815 | 0 | 0.0016 | 116920.7328 | 53442.1469
February | 108403.9396 | 173.8761 | 452.9172 | 0 | 0.0014 | 104236.1644 | 44735.2215
March | 112887.2073 | 188.1939 | 514.3716 | 0 | 0.0016 | 118391.6582 | 47266.7346
April | 95777.4478 | 166.7441 | 478.8163 | 0 | 0.0015 | 110219.0046 | 40779.077
May | 113075.7811 | 201.2946 | 591.8812 | 0 | 0.0018 | 136251.7896 | 48568.197
June | 130510.7081 | 235.2879 | 700.8634 | 0 | 0.0021 | 161343.6315 | 56339.4668
July | 101873.076 | 183.0188 | 543.2351 | 0 | 0.0016 | 125055.6629 | 43915.8031
August | 107034.9704 | 191.4031 | 565.4301 | 0 | 0.0017 | 130163.8792 | 46055.9911
September | 113435.6305 | 203.2734 | 601.7871 | 0 | 0.0018 | 138533.956 | 48850.7079
October | 105302.6435 | 185.1821 | 537.5557 | 0 | 0.0016 | 123742.9015 | 45011.9729
November | 103725.2912 | 174.927 | 484.6559 | 0 | 0.0015 | 111555.1811 | 43622.4476
December | 121624.7344 | 192.1061 | 490.3155 | 0 | 0.0015 | 112838.1097 | 49906.5543
Annual Sum or Average | 1344670 | 2298.9015 | 6469.9107 | 0 | 0.0198 | 1489250 | 568494.3207
Minimum of Months | 95777.4478 | 166.7441 | 452.9172 | 0 | 0.0014 | 104236.1644 | 40779.077
Maximum of Months | 131023.3168 | 235.2879 | 700.8634 | 0 | 0.0021 | 161343.6315 | 56339.4668
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 271306000000 | 183265.879 | 25-JAN-11:50 | 80532.756 | 81262.495 | 13526.998 | 0 | 3992.815 | 0 | 217.022 | 0 | 0 | 0 | 0 | 0 | 3733.793 | 0 | 0
February | 241872000000 | 183814.567 | 22-FEB-11:50 | 80532.756 | 81262.495 | 13681.234 | 0 | 4421.312 | 0 | 182.969 | 0 | 0 | 0 | 0 | 0 | 3733.801 | 0 | 0
March | 274719000000 | 251322.086 | 31-MAR-14:09 | 80532.756 | 75263.477 | 24349.388 | 0 | 68678.085 | 0 | 11.058 | 0 | 0 | 0 | 0 | 0 | 2487.322 | 0 | 0
April | 255755000000 | 270071.798 | 03-APR-13:00 | 80532.756 | 77263.149 | 21226.96 | 0 | 88464.482 | 0 | 17.019 | 0 | 0 | 0 | 0 | 0 | 2567.432 | 0 | 0
May | 316162000000 | 311405.005 | 30-MAY-13:00 | 80532.756 | 77263.149 | 18430.725 | 0 | 132612.812 | 0 | 2.126 | 0 | 0 | 0 | 0 | 0 | 2563.436 | 0 | 0
June | 374386000000 | 383533.201 | 08-JUN-12:00 | 80532.756 | 77263.149 | 24840.756 | 0 | 198325.544 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2570.989 | 0 | 0
July | 290182000000 | 294336.648 | 14-JUL-10:50 | 44740.42 | 47274.638 | 21686.365 | 0 | 176963.045 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 3672.172 | 0 | 0
August | 302035000000 | 287765.087 | 04-AUG-15:00 | 44740.42 | 41275.62 | 20994.62 | 0 | 178454.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2300.061 | 0 | 0
September | 321458000000 | 320718.949 | 06-SEP-10:50 | 80532.756 | 80410.298 | 20058.835 | 0 | 135873.168 | 0 | 2.428 | 0 | 0 | 0 | 0 | 0 | 3841.464 | 0 | 0
October | 287136000000 | 298630.433 | 31-OCT-11:50 | 80532.756 | 80410.298 | 17822.775 | 0 | 116037.667 | 0 | 7.729 | 0 | 0 | 0 | 0 | 0 | 3819.208 | 0 | 0
November | 258855000000 | 298090.044 | 02-NOV-11:50 | 80532.756 | 80410.298 | 17507.57 | 0 | 115892.647 | 0 | 13.951 | 0 | 0 | 0 | 0 | 0 | 3732.824 | 0 | 0
December | 261832000000 | 182547.198 | 13-DEC-11:50 | 80532.756 | 80410.298 | 13559.16 | 0 | 4074.547 | 0 | 236.647 | 0 | 0 | 0 | 0 | 0 | 3733.79 | 0 | 0
Annual Sum or Average | 3455700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 241872000000 | 182547.198 |  | 44740.42 | 41275.62 | 13526.998 | 0 | 3992.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2300.061 | 0 | 0
Maximum of Months | 374386000000 | 383533.201 |  | 80532.756 | 81262.495 | 24840.756 | 0 | 198325.544 | 0 | 236.647 | 0 | 0 | 0 | 0 | 0 | 3841.464 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 84431.02 | 26550.88 | 0 | 110981.9
Cost per Total Building Area ($/m2) | 12.29 | 3.86 | 0 | 16.15
Cost per Net Conditioned Building Area ($/m2) | 12.29 | 3.86 | 0 | 16.15

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5783.51 | 841.73 | 841.73
Net Site Energy | 5783.51 | 841.73 | 841.73
Total Source Energy | 13754.91 | 2001.88 | 2001.88
Net Source Energy | 13754.91 | 2001.88 | 2001.88
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1938.45 | 0 | 0 | 0 | 0
Cooling | 446.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.63 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 265.88 | 0 | 0 | 0 | 0 | 0
Pumps | 1.97 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 142.02 | 0 | 0 | 0 | 921.12
Refrigeration | 77.21 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3342.01 | 2441.5 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 49 | 49 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.501 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 26.6 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 14 | 3.18 | 0.402 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 11.2 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 21 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.439 | 0.543
North Total or Average |  |  | 324.79 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.404 | 0.498
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1279045.54 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 293626.98 | 234506.73 | 59120.25 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 231702.46 | 185050.39 | 46652.07 | 0.8 | 4.59
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 236796.45 | 189118.73 | 47677.72 | 0.8 | 4.58
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 318051.84 | 254013.78 | 64038.07 | 0.8 | 4.54
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 66286.59 | 52940.13 | 13346.46 | 0.8 | 4.32
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67031.46 | 53535.03 | 13496.43 | 0.8 | 4.32
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70121.09 | 56002.58 | 14118.51 | 0.8 | 4.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 62345.45 | 0.8
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 137366.07 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 131585.58 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.74 | 40476.24 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 14 | 32146.06 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 14.3 | 32852.79 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 19.21 | 43610.23 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4 | 7512.16 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.05 | 7596.58 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 4.24 | 7946.72 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7107 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 96792.276 | 149.0951 | 331.8537 | 0 | 0.0013 | 344945.6875 | 39506.5621
February | 80826.0634 | 127.2529 | 292.0056 | 0 | 0.0012 | 303548.8044 | 33259.7105
March | 87603.6966 | 142.3186 | 340.2796 | 0 | 0.0014 | 353766.3618 | 36479.792
April | 77174.6407 | 129.5853 | 322.5539 | 0 | 0.0013 | 335369.5721 | 32549.8494
May | 84398.5864 | 143.3645 | 361.6735 | 0 | 0.0014 | 376054.844 | 35758.4622
June | 90589.9024 | 155.9087 | 399.1777 | 0 | 0.0016 | 415064.1151 | 38580.4869
July | 74150.8352 | 127.4591 | 325.8888 | 0 | 0.0013 | 338857.385 | 31563.9762
August | 77223.1195 | 132.3723 | 337.4004 | 0 | 0.0013 | 350824.7463 | 32835.6839
September | 82261.0509 | 141.0048 | 359.3939 | 0 | 0.0014 | 373693.2444 | 34977.5115
October | 82371.3218 | 138.8306 | 347.0848 | 0 | 0.0014 | 360878.7304 | 34792.5936
November | 82464.6076 | 133.0433 | 315.3035 | 0 | 0.0013 | 327793.4666 | 34248.9083
December | 94973.7299 | 145.6066 | 321.8987 | 0 | 0.0013 | 334592.138 | 38696.8894
Annual Sum or Average | 1010830 | 1665.8419 | 4054.514 | 0 | 0.0161 | 4215390 | 423250.4259
Minimum of Months | 74150.8352 | 127.2529 | 292.0056 | 0 | 0.0012 | 303548.8044 | 31563.9762
Maximum of Months | 96792.276 | 155.9087 | 399.1777 | 0 | 0.0016 | 415064.1151 | 39506.5621
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 273477000000 | 233113.748 | 27-JAN-11:50 | 80532.756 | 81262.495 | 24210.303 | 0 | 43345.074 | 0 | 29.822 | 0 | 0 | 0 | 0 | 0 | 3733.298 | 0 | 0
February | 240657000000 | 205062.521 | 07-FEB-14:00 | 80532.756 | 77263.149 | 19204.638 | 0 | 25552.211 | 0 | 11.668 | 0 | 0 | 0 | 0 | 0 | 2498.099 | 0 | 0
March | 280470000000 | 251967.06 | 27-MAR-11:00 | 80532.756 | 81262.495 | 23306.038 | 0 | 64404.956 | 0 | 10.566 | 0 | 0 | 0 | 0 | 0 | 2450.248 | 0 | 0
April | 265885000000 | 266239.836 | 25-APR-13:00 | 80532.756 | 77263.149 | 19462.386 | 0 | 86470.526 | 0 | 1.237 | 0 | 0 | 0 | 0 | 0 | 2509.782 | 0 | 0
May | 298141000000 | 281694.3 | 23-MAY-11:00 | 80532.756 | 81262.495 | 21748.718 | 0 | 95681.184 | 0 | 2.827 | 0 | 0 | 0 | 0 | 0 | 2466.322 | 0 | 0
June | 329068000000 | 314323.429 | 28-JUN-11:00 | 80532.756 | 81262.495 | 25999.567 | 0 | 124058.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2470.488 | 0 | 0
July | 268650000000 | 244813.55 | 18-JUL-13:00 | 44740.42 | 43275.293 | 23524.013 | 0 | 130903.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2370.005 | 0 | 0
August | 278138000000 | 250845.416 | 30-AUG-13:00 | 44740.42 | 43275.293 | 24734.748 | 0 | 135728.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2366.13 | 0 | 0
September | 296269000000 | 292439.626 | 05-SEP-13:00 | 80532.756 | 76410.953 | 23343.211 | 0 | 109640.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2512.451 | 0 | 0
October | 286109000000 | 268972.429 | 05-OCT-13:00 | 80532.756 | 76410.953 | 20237.792 | 0 | 89285.514 | 0 | 2.155 | 0 | 0 | 0 | 0 | 0 | 2503.259 | 0 | 0
November | 259879000000 | 246658.904 | 10-NOV-13:39 | 80532.756 | 76410.953 | 23635.062 | 0 | 63584.44 | 0 | 9.989 | 0 | 0 | 0 | 0 | 0 | 2485.704 | 0 | 0
December | 265269000000 | 197945.315 | 21-DEC-14:00 | 80532.756 | 76410.953 | 17364.963 | 0 | 21114.764 | 0 | 21.447 | 0 | 0 | 0 | 0 | 0 | 2500.432 | 0 | 0
Annual Sum or Average | 3342010000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 240657000000 | 197945.315 |  | 44740.42 | 43275.293 | 17364.963 | 0 | 21114.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2366.13 | 0 | 0
Maximum of Months | 329068000000 | 314323.429 |  | 80532.756 | 81262.495 | 25999.567 | 0 | 135728.825 | 0 | 29.822 | 0 | 0 | 0 | 0 | 0 | 3733.298 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34473.98 | 17063.03 | 0 | 51537.01
Cost per Total Building Area ($/m2) | 5.02 | 2.48 | 0 | 7.5
Cost per Net Conditioned Building Area ($/m2) | 5.02 | 2.48 | 0 | 7.5

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7738.13 | 1126.2 | 1126.2
Net Site Energy | 7738.13 | 1126.2 | 1126.2
Total Source Energy | 16413.56 | 2388.82 | 2388.82
Net Source Energy | 16413.56 | 2388.82 | 2388.82
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3825.61 | 0 | 0 | 0 | 0
Cooling | 505.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.62 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 258.46 | 0 | 0 | 0 | 0 | 0
Pumps | 4.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 155.53 | 0 | 0 | 0 | 921.12
Refrigeration | 76.67 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3395.96 | 4342.17 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 49 | 49 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.501 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 26.6 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 14 | 3.18 | 0.402 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 11.2 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 21 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.439 | 0.543
North Total or Average |  |  | 324.79 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.404 | 0.498
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1492694.12 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 268077.16 | 214101.23 | 53975.93 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 211281.48 | 168741.06 | 42540.41 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 216651.86 | 173030.15 | 43621.71 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 289162.64 | 230941.26 | 58221.38 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 63806.18 | 49196.91 | 14609.27 | 0.77 | 4.16
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 88795.51 | 60033.15 | 28762.36 | 0.68 | 3.53
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 89501.53 | 61254.77 | 28246.76 | 0.68 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 82986.65 | 0.78
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 182844.93 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 175150.65 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.19 | 36954.22 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 12.76 | 29312.88 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.09 | 30057.96 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.47 | 39860.83 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.56 | 6799.95 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.58 | 6820.58 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.73 | 7108.08 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8294.13 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 119686.059 | 164.8266 | 183.5054 | 0 | 0.0015 | 120428.8306 | 46794.2681
February | 93129.5635 | 134.2616 | 162.3496 | 0 | 0.0013 | 106588.197 | 36985.5735
March | 83555.9643 | 131.1545 | 180.4844 | 0 | 0.0014 | 118561.9586 | 34205.7872
April | 64817.4513 | 109.9657 | 166.7882 | 0 | 0.0012 | 109606.783 | 27320.8311
May | 73838.0589 | 130.0645 | 205.6132 | 0 | 0.0015 | 135141.6307 | 31581.3903
June | 81502.0423 | 146.226 | 235.621 | 0 | 0.0017 | 154875.165 | 35113.7697
July | 64236.4103 | 114.4995 | 183.2658 | 0 | 0.0013 | 120458.865 | 27603.5198
August | 69108.962 | 122.8597 | 196.1087 | 0 | 0.0014 | 128899.1578 | 29666.2717
September | 69081.9064 | 121.8196 | 192.8019 | 0 | 0.0014 | 126721.8138 | 29559.839
October | 67492.126 | 114.1836 | 172.6292 | 0 | 0.0013 | 113443.8858 | 28417.6445
November | 78511.0147 | 123.4154 | 170.1725 | 0 | 0.0013 | 111788.9111 | 32157.693
December | 105661.9916 | 150.4922 | 178.2157 | 0 | 0.0014 | 116993.1604 | 41787.1289
Annual Sum or Average | 970621.5503 | 1563.7689 | 2227.5557 | 0 | 0.0167 | 1463510 | 401193.7168
Minimum of Months | 64236.4103 | 109.9657 | 162.3496 | 0 | 0.0012 | 106588.197 | 27320.8311
Maximum of Months | 119686.059 | 164.8266 | 235.621 | 0 | 0.0017 | 154875.165 | 46794.2681
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 279446000000 | 186730.539 | 05-JAN-11:09 | 80532.756 | 81262.495 | 20234.352 | 0 | 0 | 0 | 1216.431 | 0 | 0 | 0 | 0 | 0 | 3484.505 | 0 | 0
February | 247330000000 | 183295.488 | 22-FEB-11:50 | 80532.756 | 81262.495 | 13519.392 | 0 | 4013.366 | 0 | 233.691 | 0 | 0 | 0 | 0 | 0 | 3733.789 | 0 | 0
March | 275114000000 | 222254.281 | 23-MAR-15:00 | 80532.756 | 75263.477 | 17782.875 | 0 | 46263.813 | 0 | 22.6 | 0 | 0 | 0 | 0 | 0 | 2388.76 | 0 | 0
April | 254334000000 | 255726.386 | 27-APR-13:50 | 80532.756 | 77263.149 | 22795.268 | 0 | 72592.377 | 0 | 12.674 | 0 | 0 | 0 | 0 | 0 | 2530.161 | 0 | 0
May | 313586000000 | 318576.022 | 31-MAY-11:00 | 80532.756 | 81262.495 | 19777.106 | 0 | 134438.147 | 0 | 1.517 | 0 | 0 | 0 | 0 | 0 | 2564.002 | 0 | 0
June | 359376000000 | 358237.498 | 29-JUN-11:00 | 80532.756 | 81262.495 | 23702.247 | 0 | 170169.518 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2570.478 | 0 | 0
July | 279516000000 | 271636.46 | 13-JUL-15:00 | 44740.42 | 41275.62 | 19070.412 | 0 | 164271.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2278.084 | 0 | 0
August | 299101000000 | 265727.973 | 25-AUG-15:00 | 44740.42 | 41275.62 | 18981.082 | 0 | 158456.941 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2273.908 | 0 | 0
September | 294048000000 | 304500.619 | 22-SEP-13:09 | 80532.756 | 76410.953 | 19680.084 | 0 | 125304.603 | 0 | 9.138 | 0 | 0 | 0 | 0 | 0 | 2563.086 | 0 | 0
October | 263238000000 | 257241.325 | 06-OCT-13:50 | 80532.756 | 76410.953 | 21203.997 | 0 | 76584.634 | 0 | 7.134 | 0 | 0 | 0 | 0 | 0 | 2501.851 | 0 | 0
November | 259398000000 | 241655.859 | 02-NOV-14:00 | 80532.756 | 76410.953 | 23212.756 | 0 | 58963.423 | 0 | 7.859 | 0 | 0 | 0 | 0 | 0 | 2528.111 | 0 | 0
December | 271474000000 | 181885.217 | 26-DEC-11:50 | 80532.756 | 80410.298 | 13367.175 | 0 | 3613.61 | 0 | 227.589 | 0 | 0 | 0 | 0 | 0 | 3733.789 | 0 | 0
Annual Sum or Average | 3395960000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 247330000000 | 181885.217 |  | 44740.42 | 41275.62 | 13367.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2273.908 | 0 | 0
Maximum of Months | 359376000000 | 358237.498 |  | 80532.756 | 81262.495 | 23702.247 | 0 | 170169.518 | 0 | 1216.431 | 0 | 0 | 0 | 0 | 0 | 3733.789 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 57950.4 | 34385.38 | 0 | 92335.78
Cost per Total Building Area ($/m2) | 8.43 | 5 | 0 | 13.44
Cost per Net Conditioned Building Area ($/m2) | 8.43 | 5 | 0 | 13.44

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6843.67 | 996.02 | 996.02
Net Site Energy | 6843.67 | 996.02 | 996.02
Total Source Energy | 15136.99 | 2203.03 | 2203.03
Net Source Energy | 15136.99 | 2203.03 | 2203.03
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3111.32 | 0 | 0 | 0 | 0
Cooling | 323.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.61 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 260.65 | 0 | 0 | 0 | 0 | 0
Pumps | 3.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 156.69 | 0 | 0 | 0 | 921.12
Refrigeration | 76.38 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3214.64 | 3629.04 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 49 | 49 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 25.2 | 25.2 | 3.18 | 0.501 | 0.622 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 26.6 | 26.6 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 14 | 14 | 3.18 | 0.402 | 0.495 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 11.2 | 11.2 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 21 | 21 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 29.4 | 29.4 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 29.4 | 29.4 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 26.6 | 26.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.439 | 0.543
North Total or Average |  |  | 324.79 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.404 | 0.498
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1390071.69 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 283066.37 | 226072.45 | 56993.93 | 0.8 | 4.56
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 221532.55 | 176928.14 | 44604.41 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 228720.82 | 182669.09 | 46051.73 | 0.8 | 4.59
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 300310.93 | 239844.91 | 60466.03 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61666.97 | 49250.65 | 12416.32 | 0.8 | 4.37
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 63685.48 | 50862.74 | 12822.74 | 0.8 | 4.37
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 64985.94 | 51901.36 | 13084.58 | 0.8 | 4.37
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 75620.95 | 0.78
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 166616.05 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 159604.69 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 17.1 | 39020.47 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.38 | 30735.1 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.82 | 31732.39 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 18.14 | 41397.62 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.73 | 7105.76 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.85 | 7338.34 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.93 | 7488.19 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7723.91 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 107105.27 | 153.6162 | 204.444 | 0 | 0.0015 | 4844960 | 42520.7581
February | 88148.1198 | 130.1117 | 181.5846 | 0 | 0.0013 | 4304080 | 35350.9679
March | 83848.6816 | 133.2432 | 207.004 | 0 | 0.0015 | 4908630 | 34542.8719
April | 68353.8211 | 112.7301 | 183.6132 | 0 | 0.0013 | 4354710 | 28556.7584
May | 73544.7305 | 125.1977 | 211.6857 | 0 | 0.0015 | 5021140 | 31103.0453
June | 78366.1155 | 135.3236 | 232.5007 | 0 | 0.0016 | 5515160 | 33327.5034
July | 62086.5839 | 107.2488 | 184.335 | 0 | 0.0013 | 4372630 | 26407.7144
August | 63953.5161 | 108.7482 | 183.6374 | 0 | 0.0013 | 4355820 | 27034.9901
September | 71016.7528 | 121.6029 | 206.9722 | 0 | 0.0014 | 4909440 | 30102.4325
October | 72637.2073 | 120.7317 | 198.5093 | 0 | 0.0014 | 4708150 | 30436.8751
November | 79636.1643 | 125.417 | 192.51 | 0 | 0.0014 | 4564740 | 32698.0207
December | 99352.0771 | 144.9377 | 198.4744 | 0 | 0.0015 | 4704050 | 39678.7502
Annual Sum or Average | 948049.0399 | 1518.9086 | 2385.2704 | 0 | 0.0169 | 56563500 | 391760.6881
Minimum of Months | 62086.5839 | 107.2488 | 181.5846 | 0 | 0.0013 | 4304080 | 26407.7144
Maximum of Months | 107105.27 | 153.6162 | 232.5007 | 0 | 0.0016 | 5515160 | 42520.7581
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 275350000000 | 189478.067 | 05-JAN-08:09 | 80532.756 | 77263.149 | 23666.825 | 0 | 0 | 3925 | 1806.242 | 0 | 0 | 0 | 0 | 0 | 2284.095 | 0 | 0
February | 244611000000 | 232007.278 | 02-FEB-14:00 | 80532.756 | 77263.149 | 21081.015 | 0 | 50594.923 | 0 | 20.868 | 0 | 0 | 0 | 0 | 0 | 2514.567 | 0 | 0
March | 278969000000 | 245363.237 | 30-MAR-14:50 | 80532.756 | 75263.477 | 26742.694 | 0 | 60331.992 | 0 | 5.309 | 0 | 0 | 0 | 0 | 0 | 2487.009 | 0 | 0
April | 247488000000 | 239398.206 | 06-APR-15:00 | 80532.756 | 75263.477 | 29089.485 | 0 | 52117.128 | 0 | 7.472 | 0 | 0 | 0 | 0 | 0 | 2387.888 | 0 | 0
May | 285363000000 | 261672.836 | 17-MAY-10:39 | 80532.756 | 81262.495 | 24103.711 | 0 | 72017.002 | 0 | 13.675 | 0 | 0 | 0 | 0 | 0 | 3743.198 | 0 | 0
June | 313440000000 | 326364.755 | 30-JUN-12:00 | 80532.756 | 77263.149 | 25136.5 | 0 | 140881.869 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2550.471 | 0 | 0
July | 248507000000 | 225786.889 | 21-JUL-15:00 | 44740.42 | 41275.62 | 21576.45 | 0 | 115947.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2246.447 | 0 | 0
August | 247552000000 | 213288.476 | 09-AUG-15:00 | 44740.42 | 41275.62 | 19009.882 | 0 | 106017.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2245.537 | 0 | 0
September | 279015000000 | 277901.013 | 12-SEP-13:00 | 80532.756 | 76410.953 | 19141.375 | 0 | 99252.045 | 0 | 1.43 | 0 | 0 | 0 | 0 | 0 | 2562.455 | 0 | 0
October | 267575000000 | 254682.694 | 06-OCT-13:30 | 80532.756 | 76410.953 | 22976.012 | 0 | 72248.839 | 0 | 5.784 | 0 | 0 | 0 | 0 | 0 | 2508.351 | 0 | 0
November | 259425000000 | 201983.372 | 21-NOV-11:50 | 80532.756 | 80410.298 | 17803.102 | 0 | 19454.078 | 0 | 49.728 | 0 | 0 | 0 | 0 | 0 | 3733.411 | 0 | 0
December | 267343000000 | 186892.32 | 11-DEC-11:09 | 80532.756 | 80410.298 | 21540.7 | 0 | 0 | 0 | 930.222 | 0 | 0 | 0 | 0 | 0 | 3478.345 | 0 | 0
Annual Sum or Average | 3214640000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 244611000000 | 186892.32 |  | 44740.42 | 41275.62 | 17803.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2245.537 | 0 | 0
Maximum of Months | 313440000000 | 326364.755 |  | 80532.756 | 81262.495 | 29089.485 | 0 | 140881.869 | 3925 | 1806.242 | 0 | 0 | 0 | 0 | 0 | 3743.198 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 69033.04 | 29834.64 | 0 | 98867.68
Cost per Total Building Area ($/m2) | 10.05 | 4.34 | 0 | 14.39
Cost per Net Conditioned Building Area ($/m2) | 10.05 | 4.34 | 0 | 14.39

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8325.76 | 1211.72 | 1211.72
Net Site Energy | 8325.76 | 1211.72 | 1211.72
Total Source Energy | 16446.53 | 2393.62 | 2393.62
Net Source Energy | 16446.53 | 2393.62 | 2393.62
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4654.46 | 0 | 0 | 0 | 0
Cooling | 278.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 226.54 | 0 | 0 | 0 | 0 | 0
Pumps | 5.3 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 173.89 | 0 | 0 | 0 | 921.12
Refrigeration | 75.7 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3136.38 | 5189.38 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 4.2 | 4.2 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 4.2 | 4.2 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 4.2 | 4.2 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 49 | 49 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 25.2 | 25.2 | 3.18 | 0.651 | 0.64 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 26.6 | 26.6 | 3.18 | 0.501 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 14 | 14 | 3.18 | 0.501 | 0.49 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 29.4 | 29.4 | 3.18 | 0.501 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 29.4 | 29.4 | 3.18 | 0.501 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 23.8 | 23.8 | 3.18 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 11.2 | 11.2 | 3.18 | 0.501 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 21 | 21 | 3.18 | 0.501 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 29.4 | 29.4 | 3.18 | 0.651 | 0.64 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 29.4 | 29.4 | 3.18 | 0.501 | 0.49 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 26.6 | 26.6 | 3.18 | 0.651 | 0.64 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 3.19 | 0.556 | 0.544
North Total or Average |  |  | 324.79 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 567.77 | 3.19 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1431393.05 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 254561.53 | 203306.9 | 51254.62 | 0.8 | 4.59
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 197852.19 | 158015.69 | 39836.5 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 205907.17 | 164448.84 | 41458.33 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 265656.6 | 212168.04 | 53488.56 | 0.8 | 4.56
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 54393.06 | 43441.3 | 10951.76 | 0.8 | 3.47
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 73439.21 | 52773.9 | 20665.31 | 0.72 | 3.2
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68756.75 | 50677.84 | 18078.91 | 0.74 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 84943.16 | 0.78
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 187155.71 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 179280.03 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 15.38 | 35317.49 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 11.95 | 27449.72 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 12.44 | 28567.26 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 16.05 | 36620.55 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.29 | 3593.53 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.47 | 3795.46 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.46 | 3781.45 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7953.51 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 118300.8106 | 162.7509 | 180.8346 | 0 | 0.0014 | 118674.8747 | 46236.6164
February | 99558.365 | 139.7407 | 161.219 | 0 | 0.0013 | 105821.9069 | 39176.5315
March | 92037.7335 | 138.7665 | 180.2405 | 0 | 0.0014 | 118372.6363 | 37133.0348
April | 66699.3488 | 109.7133 | 160.4129 | 0 | 0.0012 | 105402.4461 | 27784.7548
May | 66263.4987 | 113.7937 | 174.9854 | 0 | 0.0013 | 114999.5931 | 28061.7503
June | 70586.7563 | 124.9888 | 198.6804 | 0 | 0.0015 | 130587.5293 | 30253.0314
July | 59239.75 | 104.1358 | 164.2651 | 0 | 0.0012 | 107964.3002 | 25317.0681
August | 58326.6168 | 100.3333 | 154.5783 | 0 | 0.0011 | 101588.7937 | 24716.7901
September | 62973.209 | 109.0221 | 169.1582 | 0 | 0.0012 | 111173.6268 | 26752.3583
October | 67450.8443 | 112.6157 | 167.6459 | 0 | 0.0012 | 110162.6576 | 28257.0756
November | 85486.8661 | 129.3198 | 168.8122 | 0 | 0.0013 | 110869.5118 | 34531.1686
December | 110936.6756 | 154.8274 | 176.7661 | 0 | 0.0014 | 116020.773 | 43569.4387
Annual Sum or Average | 957860.4747 | 1500.0081 | 2057.5986 | 0 | 0.0156 | 1351640 | 391789.6187
Minimum of Months | 58326.6168 | 100.3333 | 154.5783 | 0 | 0.0011 | 101588.7937 | 24716.7901
Maximum of Months | 118300.8106 | 162.7509 | 198.6804 | 0 | 0.0015 | 130587.5293 | 46236.6164
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 275376000000 | 183042.641 | 09-JAN-11:09 | 80532.756 | 81262.495 | 16032.982 | 0 | 0 | 0 | 1728.005 | 0 | 0 | 0 | 0 | 0 | 3486.404 | 0 | 0
February | 245552000000 | 182659.67 | 24-FEB-11:50 | 80532.756 | 81262.495 | 12385.972 | 0 | 4568.1 | 0 | 176.57 | 0 | 0 | 0 | 0 | 0 | 3733.778 | 0 | 0
March | 274675000000 | 183588.047 | 24-MAR-10:50 | 80532.756 | 81262.495 | 12567.992 | 0 | 5362.296 | 0 | 128.738 | 0 | 0 | 0 | 0 | 0 | 3733.771 | 0 | 0
April | 244578000000 | 213811.568 | 04-APR-14:00 | 80532.756 | 75263.477 | 14087.825 | 0 | 41435.559 | 0 | 5.576 | 0 | 0 | 0 | 0 | 0 | 2486.375 | 0 | 0
May | 266848000000 | 251147.238 | 31-MAY-11:00 | 80532.756 | 81262.495 | 16649.036 | 0 | 70239.684 | 0 | 4.362 | 0 | 0 | 0 | 0 | 0 | 2458.905 | 0 | 0
June | 303019000000 | 307082.211 | 14-JUN-13:00 | 80532.756 | 77263.149 | 15976.006 | 0 | 130756.67 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2553.627 | 0 | 0
July | 250523000000 | 235407.98 | 07-JUL-10:39 | 44740.42 | 47274.638 | 15189.897 | 0 | 124454.618 | 0 | 3.349 | 0 | 0 | 0 | 0 | 0 | 3745.059 | 0 | 0
August | 235729000000 | 225300.73 | 11-AUG-11:00 | 44740.42 | 47274.638 | 14121.65 | 0 | 116841.993 | 0 | 9.141 | 0 | 0 | 0 | 0 | 0 | 2312.888 | 0 | 0
September | 257970000000 | 292092.496 | 08-SEP-11:30 | 80532.756 | 80410.298 | 15499.505 | 0 | 113085.746 | 0 | 13.977 | 0 | 0 | 0 | 0 | 0 | 2550.215 | 0 | 0
October | 255624000000 | 226444.724 | 27-OCT-11:00 | 80532.756 | 80410.298 | 15788.069 | 0 | 47225.323 | 0 | 18.776 | 0 | 0 | 0 | 0 | 0 | 2469.502 | 0 | 0
November | 257264000000 | 181732.468 | 09-NOV-11:00 | 80532.756 | 80410.298 | 13294.314 | 0 | 4960.501 | 0 | 52.41 | 0 | 0 | 0 | 0 | 0 | 2482.189 | 0 | 0
December | 269217000000 | 181000.369 | 27-DEC-11:50 | 80532.756 | 80410.298 | 12227.795 | 0 | 3865.448 | 0 | 230.295 | 0 | 0 | 0 | 0 | 0 | 3733.777 | 0 | 0
Annual Sum or Average | 3136380000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 235729000000 | 181000.369 |  | 44740.42 | 47274.638 | 12227.795 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2312.888 | 0 | 0
Maximum of Months | 303019000000 | 307082.211 |  | 80532.756 | 81262.495 | 16649.036 | 0 | 130756.67 | 0 | 1728.005 | 0 | 0 | 0 | 0 | 0 | 3745.059 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 52305.62 | 41017.83 | 0 | 93323.45
Cost per Total Building Area ($/m2) | 7.61 | 5.97 | 0 | 13.58
Cost per Net Conditioned Building Area ($/m2) | 7.61 | 5.97 | 0 | 13.58

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11432.35 | 1663.86 | 1663.86
Net Site Energy | 11432.35 | 1663.86 | 1663.86
Total Source Energy | 19948.47 | 2903.28 | 2903.28
Net Source Energy | 19948.47 | 2903.28 | 2903.28
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7865.89 | 0 | 0 | 0 | 0
Cooling | 166.9 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.13 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 61.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1256.13 | 361.03 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 207.39 | 0 | 0 | 0 | 0 | 0
Pumps | 10.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 195.62 | 0 | 0 | 0 | 921.12
Refrigeration | 74.2 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3009.81 | 8422.54 | 0 | 0 | 0 | 921.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 14 |  | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 | 100 | 10
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 100 | 4
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1629.354
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 14 | 4.35 | 15
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.023 | 4.89 | 51.7194
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 192 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 192 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 192 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 162 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 546 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 171 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 252 | 90 | 0
BATH_ZN_1_FLR_1_WALL_5 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 190 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 441 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 168 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 315 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 399 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 4.2 | 4.2 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 4.2 | 4.2 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 4.2 | 4.2 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 49 | 49 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 25.2 | 25.2 | 2.58 | 0.654 | 0.64 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 26.6 | 26.6 | 2.58 | 0.504 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 14 | 14 | 2.58 | 0.504 | 0.49 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 29.4 | 29.4 | 2.58 | 0.504 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 29.4 | 29.4 | 2.58 | 0.504 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 23.8 | 23.8 | 2.58 | 0.504 | 0.49 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 11.2 | 11.2 | 2.58 | 0.504 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 21 | 21 | 2.58 | 0.504 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 29.4 | 29.4 | 2.58 | 0.654 | 0.64 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 29.4 | 29.4 | 2.58 | 0.504 | 0.49 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 26.6 | 26.6 | 2.58 | 0.654 | 0.64 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 892.56 | 2.59 | 0.558 | 0.544
North Total or Average |  |  | 324.79 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 567.77 | 2.6 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1477921.2 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 223352.92 | 178381.98 | 44970.93 | 0.8 | 4.58
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 169006.42 | 134977.87 | 34028.55 | 0.8 | 4.86
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 180880.1 | 144460.85 | 36419.26 | 0.8 | 4.86
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 206992.3 | 165315.49 | 41676.81 | 0.8 | 4.86
PSZ-AC_2:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 43795.66 | 34977.63 | 8818.02 | 0.8 | 3.47
PSZ-AC_1:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 53797.96 | 42966.02 | 10831.94 | 0.8 | 3.47
PSZ-AC_2:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 45305.32 | 36183.33 | 9121.99 | 0.8 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_2:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 108210.51 | 0.78
PSZ-AC_1:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 231763.01 | 0.78
PSZ-AC_2:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 222010.22 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.28 | 78.67 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.01 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.26 | 282.55 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 13.49 | 30987.66 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 10.21 | 23447.7 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 10.93 | 25095.04 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1388.3 | 12.5 | 28717.81 | 1 | Fan Energy
PSZ-AC_2:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.65 | 2893.4 | 1 | Unitary Fans
PSZ-AC_1:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.25 | 3554.21 | 1 | Unitary Fans
PSZ-AC_2:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.74 | 2993.14 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8212.04 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 142015.5163 | 147.3079 | 385.1836 | 0 | 0.0015 | 77217.514 | 51981.9072
February | 120852.5113 | 126.2554 | 346.5963 | 0 | 0.0013 | 69489.1015 | 44373.9925
March | 105790.9924 | 114.6787 | 390.3942 | 0 | 0.0014 | 78301.4864 | 39483.6671
April | 69906.8108 | 79.8804 | 343.7622 | 0 | 0.0012 | 68972.5111 | 26721.8814
May | 57095.4496 | 69.3584 | 366.898 | 0 | 0.0013 | 73632.5859 | 22458.3084
June | 59427.4404 | 73.1159 | 401.2288 | 0 | 0.0014 | 80525.5261 | 23517.8849
July | 45089.0844 | 54.8335 | 291.0028 | 0 | 0.001 | 58401.4169 | 17744.8991
August | 46955.7806 | 55.9257 | 278.4087 | 0 | 0.001 | 55869.9533 | 18298.2875
September | 56187.2503 | 66.9844 | 334.477 | 0 | 0.0012 | 67121.7452 | 21905.524
October | 81835.0868 | 91.8587 | 367.8608 | 0 | 0.0013 | 73800.3962 | 31027.2724
November | 113999.8606 | 121.3696 | 374.5005 | 0 | 0.0014 | 75100.7534 | 42207.6815
December | 128980.021 | 135.1246 | 377.8196 | 0 | 0.0014 | 75751.9149 | 47416.4223
Annual Sum or Average | 1028140 | 1136.6933 | 4258.1327 | 0 | 0.0153 | 854184.9049 | 387137.7284
Minimum of Months | 45089.0844 | 54.8335 | 278.4087 | 0 | 0.001 | 55869.9533 | 17744.8991
Maximum of Months | 142015.5163 | 147.3079 | 401.2288 | 0 | 0.0015 | 80525.5261 | 51981.9072
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 272084000000 | 185711.338 | 13-JAN-10:09 | 80532.756 | 81262.495 | 13645.466 | 0 | 0 | 3925 | 4059.072 | 0 | 0 | 0 | 0 | 0 | 2286.55 | 0 | 0
February | 244852000000 | 183065.011 | 03-FEB-08:09 | 80532.756 | 77263.149 | 14635.614 | 0 | 0 | 3925 | 4424.617 | 0 | 0 | 0 | 0 | 0 | 2283.875 | 0 | 0
March | 275904000000 | 180644.555 | 29-MAR-10:50 | 80532.756 | 81262.495 | 10874.395 | 0 | 4037.862 | 0 | 203.271 | 0 | 0 | 0 | 0 | 0 | 3733.777 | 0 | 0
April | 243032000000 | 181277.242 | 19-APR-10:50 | 80532.756 | 81262.495 | 11030.55 | 0 | 4556.314 | 0 | 161.348 | 0 | 0 | 0 | 0 | 0 | 3733.78 | 0 | 0
May | 259452000000 | 223977.15 | 30-MAY-11:00 | 80532.756 | 81262.495 | 15250.07 | 0 | 44474.789 | 0 | 2.776 | 0 | 0 | 0 | 0 | 0 | 2454.265 | 0 | 0
June | 283740000000 | 253611.798 | 21-JUN-13:00 | 80532.756 | 77263.149 | 12615.273 | 0 | 80672.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2527.763 | 0 | 0
July | 205784000000 | 176549.776 | 11-JUL-11:00 | 44740.42 | 47274.638 | 11731.418 | 0 | 70361.88 | 0 | 8.795 | 0 | 0 | 0 | 0 | 0 | 2432.626 | 0 | 0
August | 196864000000 | 172984.084 | 15-AUG-13:00 | 44740.42 | 43275.293 | 11244.857 | 0 | 71363.641 | 0 | 5.934 | 0 | 0 | 0 | 0 | 0 | 2353.94 | 0 | 0
September | 236511000000 | 198562.384 | 07-SEP-15:00 | 80532.756 | 75197.923 | 11752.041 | 0 | 28686.438 | 0 | 5.695 | 0 | 0 | 0 | 0 | 0 | 2387.531 | 0 | 0
October | 260044000000 | 179805.57 | 12-OCT-10:50 | 80532.756 | 80410.298 | 10875.17 | 0 | 4039.936 | 0 | 213.634 | 0 | 0 | 0 | 0 | 0 | 3733.777 | 0 | 0
November | 264626000000 | 179197.283 | 14-NOV-11:50 | 80532.756 | 80410.298 | 10734.497 | 0 | 3562.646 | 0 | 223.303 | 0 | 0 | 0 | 0 | 0 | 3733.783 | 0 | 0
December | 266920000000 | 182313.165 | 29-DEC-11:09 | 80532.756 | 80410.298 | 10797.952 | 0 | 0 | 3925 | 3162.128 | 0 | 0 | 0 | 0 | 0 | 3485.032 | 0 | 0
Annual Sum or Average | 3009810000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 196864000000 | 172984.084 |  | 44740.42 | 43275.293 | 10734.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2283.875 | 0 | 0
Maximum of Months | 283740000000 | 253611.798 |  | 80532.756 | 81262.495 | 15250.07 | 0 | 80672.856 | 3925 | 4424.617 | 0 | 0 | 0 | 0 | 0 | 3733.783 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 79787.8 | 34729.99 | 0 | 114517.79
Cost per Total Building Area ($/m2) | 11.61 | 5.05 | 0 | 16.67
Cost per Net Conditioned Building Area ($/m2) | 11.61 | 5.05 | 0 | 16.67

## Picture
DOE Commercial Building Benchmark - Primary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75 | 1444.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75 | 2395.71
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42 | 2.1 | 109.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720