## BuildingSummary
Building Summary Primary School new construction
|  | Value | Data Source
Program
| Building Name | Benchmark Primary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 6871 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.35
| Total | 0.35
| Skylight/TDD Percentage | 0.19%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Flat built-up | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2512
| Net Dimensions - Total Area (m2) | 1619.42
| Wall to Skin Ratio | 0.27
Roof
| Construction Type | Insulation Entirely Above Deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6871
| Net Dimensions - Total Area (m2) | 6871
| Roof to Skin Ratio | 0.73
Window Dimensions (m2)
| South | 324.79 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| East | 114.8
| North | 324.79
| West | 114.8
| Total Area (m2) | 879.18
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 13.38
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 10 cm concrete slab-on-grade
| Dimensions - Total Area (m2) | 6871
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 2932
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 13742
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.37 | 2003 CBECS
HVAC |  |  | 2003 CBECS
| System Type | CAV, PSZ-AC (gym, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | gas boiler, gas furnace (gym, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | PACU
| Fan Control | Constant
Service Water Heating
| SWH Type | Storage Tank | Standard 90.1-2004
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 589.92

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 15 | 0 | 0 | 8 | 0 | 954 | 0 | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 192 | 768 | 4 | 12 | 4.2 | 10 | 19.2 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 15 | 0 | 0 | 8 | 0 | 198 | 0 | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 140 | 49 | 4 | 78.75 | 15.064 | 8.07 | 0 | 0 | 8 | 0 | 630 | 0 | 0.39302
COMPUTER_CLASS_ZN_1_FLR_1 | Yes | 1 | 162 | 648 | 4 | 72 | 25.2 | 3.33 | 48.6486 | 15.064 | 20 | 0 | 0 | 8 | 0 | 389.1892 | 0 | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 546 | 2184 | 4 | 36 | 12.6 | 0 | 0 | 5.38 | 4 | 0 | 0 | 0 | 0.5 | 273 | 0 | 0.29003
LOBBY_ZN_1_FLR_1 | Yes | 1 | 171 | 684 | 4 | 76 | 26.6 | 0 | 0 | 13.988 | 4 | 0 | 0 | 0 | 0.5 | 85.5 | 0 | 0.39302
MECH_ZN_1_FLR_1 | Yes | 1 | 252 | 1008 | 4 | 0 | 0 | 100 | 2.52 | 16.14 | 4 | 0 | 0 | 0 | 0.25 | 63 | 0 | 0.27209
BATH_ZN_1_FLR_1 | Yes | 1 | 190 | 760 | 4 | 40 | 14 | 10 | 19 | 9.684 | 4 | 0 | 213.9574 | 25 | 0 | 300 | 283.1682 | 0.32937
OFFICES_ZN_1_FLR_1 | Yes | 1 | 441 | 1764 | 4 | 168 | 58.8 | 20 | 22.05 | 11.836 | 10.8 | 0 | 0 | 10 | 0 | 220.5 | 0 | 0.37575
GYM_ZN_1_FLR_1 | Yes | 1 | 357 | 1428 | 4 | 68 | 37.18 | 3.33 | 107.2072 | 15.064 | 5 | 0 | 0 | 10 | 0 | 1072.0721 | 0 | 0.32392
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 168 | 672 | 4 | 32 | 11.2 | 6.67 | 25.1874 | 12.912 | 190.452 | 954.0533 | 378.54 | 8 | 0 | 201.4993 | 1557.4251 | 0.32392
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 315 | 1260 | 4 | 144 | 50.4 | 1.3935 | 226.0419 | 15.064 | 25.3936 | 0 | 0 | 10 | 0 | 2260.419 | 0 | 0.39648
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | Yes | 1 | 399 | 1596 | 4 | 160 | 56 | 4.35 | 91.7241 | 13.988 | 15 | 0 | 0 | 8 | 0 | 733.7931 | 0 | 0.3812
Building Total Conditioned Zones |  |  | 6871 | 27484 |  | 2512 | 892.58 |  | 1423.4793
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 11.3935 | 166.9938 | 29.394 | 168.9694 |  | 79.8242 | 8.5151 | 160.1074 | 5.3818 | 16.7523 | 164.6314 | 40.0073 | 30.0711 | 6.7034 | 4.1682 | 0.59086
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | 5.765 | 5.765 | 5.765 | 2.627 | 2.627 | 2.627 | 5.679 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.561
| SHGC | 0.174 | 0.174 | 0.174 | 0.229 | 0.229 | 0.229 | 0.394 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.777 | 0.767
| Visible transmittance | 0.029 | 0.029 | 0.029 | 0.008 | 0.008 | 0.008 | 0.09 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.855 | 0.855
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade | 10cm slab-on-grade
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:6_COOLC DXCOIL | 16.12 | 16.0258 | 15.3517 | 15.6029 | 13.8115 | 14.3502 | 17.0132 | 15.478 | 14.1036 | 10.9081 | 15.0693 | 13.3535 | 14.7224 | 10.5283 | 13.1024 | 8.7378
| PSZ-AC_2:5_COOLC DXCOIL | 28.6862 | 29.2079 | 28.4112 | 29.0211 | 26.6221 | 26.6221 | 24.5873 | 29.5311 | 26.834 | 23.9709 | 28.3947 | 25.8603 | 27.6883 | 21.0508 | 29.3118 | 17.7466
| PSZ-AC_2:7_COOLC DXCOIL | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 56.2748 | 44.0264 | 56.2748 | 53.2715 | 51.3622 | 56.2748 | 53.9233 | 56.2748 | 46.1168 | 56.2748 | 37.5134
| VAV_OTHER_COOLC DXCOIL | 137.5397 | 140.956 | 135.8066 | 130.4879 | 94.4255 | 106.7417 | 107.2683 | 129.8362 | 82.6682 | 74.79 | 121.1868 | 76.6936 | 116.5712 | 77.3775 | 108.5237 | 77.1957
| VAV_POD_1_COOLC DXCOIL | 131.6266 | 135.8376 | 139.6607 | 123.7109 | 97.6335 | 114.5358 | 132.8225 | 128.5403 | 87.8222 | 85.3488 | 121.1062 | 82.0023 | 117.7206 | 71.9942 | 109.246 | 92.0542
| VAV_POD_2_COOLC DXCOIL | 100.9973 | 103.7388 | 105.603 | 95.8871 | 77.6914 | 90.2973 | 103.0405 | 96.9596 | 68.3563 | 65.7868 | 91.154 | 63.7943 | 88.4423 | 53.1674 | 79.6814 | 65.9258
| VAV_POD_3_COOLC DXCOIL | 104.2298 | 107.6813 | 110.693 | 98.5526 | 78.1513 | 91.2158 | 107.3542 | 102.0202 | 69.7836 | 68.8807 | 96.0089 | 65.1813 | 93.4464 | 57.0975 | 86.9486 | 73.4045
Heating (kW)
| HEATSYS1 BOILER | 294.6393 | 376.0517 | 328.6362 | 365.1189 | 240.6777 | 295.0504 | 449.1851 | 408.8831 | 314.5147 | 307.0735 | 438.4285 | 332.2496 | 456.1561 | 392.5024 | 433.2557 | 637.0884
| PSZ-AC_1:6_HEATC | 25.1325 | 32.9845 | 26.6583 | 34.6429 | 22.3956 | 26.9383 | 38.9765 | 38.2551 | 30.0155 | 26.132 | 43.5096 | 33.5606 | 45.9388 | 37.8587 | 41.8476 | 51.8432
| PSZ-AC_2:5_HEATC | 43.4171 | 57.179 | 47.8205 | 61.2483 | 43.1683 | 49.9752 | 53.6246 | 68.4771 | 55.0238 | 56.9032 | 78.4709 | 63.5396 | 84.0276 | 75.6966 | 87.3939 | 105.2941
| PSZ-AC_2:7_HEATC | 87.7376 | 115.8256 | 97.7215 | 124.946 | 91.2508 | 105.6395 | 100.8623 | 139.0873 | 110.5125 | 120.2841 | 162.4826 | 131.9201 | 175.596 | 160.0105 | 179.7358 | 222.5747
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:6_COOLC DXCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.85 | 3.65 | 3.71 | 3.74 | 3.65 | 3.7 | 3.65 | 3.84 | 3.65 | 4.04
| PSZ-AC_2:5_COOLC DXCOIL | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 3.66 | 3.44 | 3.52 | 3.51 | 3.44 | 3.49 | 3.44 | 3.61 | 3.44 | 4.01
| PSZ-AC_2:7_COOLC DXCOIL | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.19 | 3.33 | 3.19 | 3.21 | 3.23 | 3.19 | 3.21 | 3.19 | 3.3 | 3.19 | 3.73
| VAV_OTHER_COOLC DXCOIL | 3.49 | 3.49 | 3.49 | 3.49 | 3.66 | 3.59 | 4.04 | 3.49 | 4.14 | 3.91 | 3.51 | 4.04 | 3.51 | 4.18 | 3.51 | 4.18
| VAV_POD_1_COOLC DXCOIL | 3.49 | 3.49 | 3.49 | 3.49 | 3.59 | 3.55 | 4.07 | 3.49 | 4.02 | 3.92 | 3.51 | 3.98 | 3.51 | 4.18 | 3.51 | 4.14
| VAV_POD_2_COOLC DXCOIL | 3.51 | 3.51 | 3.51 | 3.51 | 3.13 | 3.51 | 4.03 | 3.51 | 4.08 | 3.33 | 3.51 | 3.34 | 3.51 | 3.45 | 3.11 | 4.32
| VAV_POD_3_COOLC DXCOIL | 3.51 | 3.51 | 3.51 | 3.51 | 3.14 | 3.55 | 4.07 | 3.51 | 4.18 | 4.03 | 3.51 | 4.09 | 3.51 | 3.45 | 3.11 | 4.18
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
| PSZ-AC_1:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_2:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_2:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_2:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
| VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATH_ZN_1_FLR_1 EXHAUST FAN | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| PSZ-AC_1:6_FAN | 0.65 | 0.65 | 0.62 | 0.63 | 0.56 | 0.58 | 0.88 | 0.62 | 0.62 | 0.49 | 0.61 | 0.58 | 0.59 | 0.54 | 0.53 | 0.53
| PSZ-AC_2:5_FAN | 1.16 | 1.18 | 1.14 | 1.17 | 1.07 | 1.07 | 1.33 | 1.19 | 1.22 | 1.07 | 1.14 | 1.13 | 1.12 | 1.07 | 1.18 | 1.07
| PSZ-AC_2:7_FAN | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27
| VAV_OTHER_FAN | 5.54 | 5.68 | 5.47 | 5.25 | 4.32 | 4.63 | 6.19 | 5.23 | 4.9 | 3.99 | 4.88 | 4.36 | 4.69 | 4.67 | 4.4 | 4.66
| VAV_POD_1_FAN | 5.3 | 5.47 | 5.62 | 4.98 | 4.23 | 4.79 | 7.78 | 5.18 | 5.03 | 4.56 | 4.88 | 4.52 | 4.74 | 4.35 | 4.4 | 5.56
| VAV_POD_2_FAN | 4.07 | 4.18 | 4.25 | 3.86 | 3.23 | 3.64 | 5.92 | 3.9 | 3.73 | 3.38 | 3.67 | 3.34 | 3.56 | 3.21 | 3.21 | 3.98
| VAV_POD_3_FAN | 4.2 | 4.34 | 4.46 | 3.97 | 3.38 | 3.8 | 6.29 | 4.11 | 3.98 | 3.67 | 3.87 | 3.57 | 3.76 | 3.45 | 3.5 | 4.43
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.089346 | 0.12126 | 0.094386 | 0.098161 | 0.12877 | 0.10003 | 0.14675 | 0.078276 | 0.037154 | 0.074922 | 0.088758 | 0.037164 | 0.061637 | 0.075715 | 0.060202 | 0.095153
| Total Cost ($/m2) | 14.96 | 18.36 | 14.18 | 13.03 | 15.94 | 13.68 | 17.31 | 10.04 | 4.61 | 8.56 | 10.96 | 4.42 | 7.48 | 8.74 | 6.94 | 10.91
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011449 | 0.008117 | 0.0083899 | 0.0099784 | 0.008479 | 0.0078764 | 0.0085263 | 0.0097604 | 0.0069795 | 0.0083866 | 0.0084195 | 0.0069774 | 0.0079001 | 0.0081909 | 0.007887 | 0.0041219
| Total Cost ($/m2) | 0.55 | 0.82 | 0.71 | 1.46 | 0.62 | 0.81 | 1.3 | 2.27 | 1.18 | 1.7 | 2.52 | 1.61 | 3.25 | 2.73 | 3.81 | 3.57
Total Utility Costs
| Cost Intensity ($/m2) | 15.51 | 19.18 | 14.89 | 14.48 | 16.56 | 14.49 | 18.62 | 12.32 | 5.8 | 10.25 | 13.48 | 6.03 | 10.72 | 11.47 | 10.75 | 14.48
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 357783.3333 | 259311.1111 | 245330.5556 | 139561.1111 | 85777.7778 | 160872.2222 | 42083.3333 | 111983.3333 | 77119.4444 | 25511.1111 | 80919.4444 | 49777.7778 | 65086.1111 | 30955.5556 | 28697.2222 | 14633.3333
| Interior Lighting | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889 | 342513.8889
| Exterior Lighting | 27833.3333 | 27825 | 27819.4444 | 27813.8889 | 27794.4444 | 27786.1111 | 27802.7778 | 27783.3333 | 27794.4444 | 27738.8889 | 27788.8889 | 27772.2222 | 27772.2222 | 27763.8889 | 27747.2222 | 27577.7778
| Interior Equipment | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556 | 341730.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 58786.1111 | 48147.2222 | 53769.4444 | 40016.6667 | 32961.1111 | 46644.4444 | 37205.5556 | 37830.5556 | 44291.6667 | 28252.7778 | 36327.7778 | 35988.8889 | 37005.5556 | 31652.7778 | 32541.6667 | 41452.7778
| Pumps | 2.7778 | 102.7778 | 69.4444 | 177.7778 | 19.4444 | 102.7778 | 144.4444 | 341.6667 | 238.8889 | 222.2222 | 422.2222 | 375 | 769.4444 | 605.5556 | 961.1111 | 2236.1111
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 21788.8889 | 20816.6667 | 20880.5556 | 19919.4444 | 19913.8889 | 20241.6667 | 19072.2222 | 19311.1111 | 19336.1111 | 18688.8889 | 18888.8889 | 18791.6667 | 18652.7778 | 18327.7778 | 18005.5556 | 17550
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1150441.6667 | 1040447.2222 | 1032113.8889 | 911730.5556 | 850708.3333 | 939891.6667 | 810550 | 881497.2222 | 853027.7778 | 784658.3333 | 848591.6667 | 816952.7778 | 833527.7778 | 793550 | 792194.4444 | 787694.4444
Gas (MJ)
| Heating | 23660 | 362710 | 260090 | 651500 | 157770 | 368130 | 687170 | 1231960 | 800090 | 1013030 | 1671080 | 1200940 | 2426930 | 1888600 | 2899970 | 5507660
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340 | 234340
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 72940 | 96330 | 84750 | 117670 | 111470 | 100320 | 129590 | 134590 | 131340 | 141490 | 149140 | 147980 | 161960 | 163520 | 181790 | 205440
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 330940 | 693380 | 579190 | 1003510 | 503580 | 702790 | 1051100 | 1600890 | 1165780 | 1388860 | 2054560 | 1583270 | 2823230 | 2286460 | 3316100 | 5947440
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 4472530 | 4438980 | 4294800 | 4285740 | 3566130 | 4086400 | 3969090 | 4774280 | 4236680 | 4213620 | 5109490 | 4524290 | 5823930 | 5143240 | 6168000 | 8783140
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 187.4574 | 135.8638 | 128.5388 | 73.1218 | 44.9425 | 84.2876 | 22.0492 | 58.6727 | 40.4061 | 13.3663 | 42.397 | 26.0806 | 34.1013 | 16.2189 | 15.0357 | 7.667
| Interior Lighting (elec) | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571 | 179.4571
| Exterior Lighting (elec) | 14.583 | 14.5787 | 14.5758 | 14.5728 | 14.5627 | 14.5583 | 14.567 | 14.5568 | 14.5627 | 14.5335 | 14.5597 | 14.551 | 14.551 | 14.5466 | 14.5379 | 14.4491
| Interior Equipment (elec) | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467 | 179.0467
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 30.8005 | 25.2263 | 28.172 | 20.9664 | 17.2697 | 24.4389 | 19.4935 | 19.821 | 23.2062 | 14.8028 | 19.0336 | 18.8561 | 19.3887 | 16.5842 | 17.0499 | 21.7188
| Pumps (elec) | 0.0014554 | 0.05385 | 0.036385 | 0.093145 | 0.010188 | 0.05385 | 0.07568 | 0.17901 | 0.12516 | 0.11643 | 0.22122 | 0.19648 | 0.40314 | 0.31728 | 0.50357 | 1.1716
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 11.4161 | 10.9067 | 10.9402 | 10.4366 | 10.4337 | 10.6054 | 9.9927 | 10.1179 | 10.131 | 9.7919 | 9.8967 | 9.8457 | 9.773 | 9.6027 | 9.4339 | 9.1952
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 602.7638 | 545.1332 | 540.767 | 477.6932 | 445.7211 | 492.448 | 424.6805 | 461.8527 | 446.9364 | 411.1148 | 444.6121 | 428.0352 | 436.7195 | 415.7735 | 415.0633 | 412.7056
Gas (MJ/m2)
| Heating (gas) | 3.4435 | 52.7885 | 37.8533 | 94.8188 | 22.9617 | 53.5774 | 100.0102 | 179.2985 | 116.4445 | 147.4356 | 243.2077 | 174.7839 | 353.2135 | 274.8654 | 422.0594 | 801.5806
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057 | 34.1057
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 10.6156 | 14.0198 | 12.3344 | 17.1256 | 16.2233 | 14.6005 | 18.8604 | 19.5881 | 19.1151 | 20.5923 | 21.7057 | 21.5369 | 23.5715 | 23.7986 | 26.4576 | 29.8996
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 48.1648 | 100.914 | 84.2949 | 146.0501 | 73.2906 | 102.2835 | 152.9763 | 232.9923 | 169.6667 | 202.1336 | 299.0191 | 230.4279 | 410.8907 | 332.7696 | 482.6226 | 865.5858
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 650.9285 | 646.0457 | 625.0619 | 623.7433 | 519.0118 | 594.7315 | 577.6583 | 694.845 | 616.6031 | 613.247 | 743.6312 | 658.4617 | 847.6102 | 748.5432 | 897.6859 | 1278.2914
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 313.806 | 281.8911 | 225.0692 | 199.0038 | 239.2178 | 196.048 | 182.3658 | 183.6749 | 184.4969 | 169.9422 | 171.3553 | 186.6666 | 172.0306 | 172.4904 | 171.5676 | 180.143
| Feb | 322.8131 | 266.0284 | 245.7417 | 193.5425 | 231.4948 | 205.2655 | 213.1326 | 178.9023 | 203.3871 | 181.6091 | 171.2823 | 180.1116 | 171.3046 | 182.8493 | 171.5114 | 174.9425
| Mar | 322.8246 | 276.7293 | 291.34 | 226.353 | 226.7197 | 226.8996 | 199.6329 | 229.7621 | 208.1128 | 197.3655 | 200.6848 | 210.5012 | 183.085 | 196.2298 | 170.2532 | 174.7923
| Apr | 332.903 | 308.5287 | 302.4538 | 265.6687 | 237.6873 | 286.0947 | 213.3757 | 229.2025 | 237.3572 | 188.8893 | 208.0006 | 226.0187 | 201.2106 | 187.7473 | 187.4502 | 173.7325
| May | 346.1142 | 352.0847 | 342.393 | 312.4684 | 258.0521 | 312.6459 | 229.4869 | 297.8459 | 262.3183 | 226.497 | 274.0165 | 245.4302 | 288.7004 | 219.606 | 220.2917 | 209.9668
| Jun | 352.2021 | 353.3758 | 401.2156 | 330.522 | 253.5622 | 359.5078 | 232.3162 | 347.3054 | 284.7826 | 239.1777 | 334.9034 | 277.6656 | 327.7089 | 265.5745 | 293.4902 | 240.8503
| Jul | 268.8458 | 285.5353 | 316.4495 | 270.1709 | 157.2612 | 277.6633 | 160.3388 | 278.0511 | 213.0282 | 164.9958 | 250.5031 | 202.0429 | 240.497 | 188.6573 | 213.4066 | 140.2347
| Aug | 277.2263 | 279.6503 | 318.3009 | 245.9192 | 188.7915 | 270.0311 | 157.3176 | 274.0571 | 208.0155 | 154.0155 | 255.3842 | 203.0839 | 240.6415 | 167.4293 | 194.1494 | 140.5326
| Sep | 350.8597 | 357.2078 | 368.1094 | 325.9194 | 279.9018 | 316.6583 | 292.5802 | 314.5892 | 258.4193 | 253.5713 | 302.2753 | 260.9526 | 288.8967 | 240.2692 | 268.5642 | 182.4012
| Oct | 346.8556 | 334.9271 | 305.4927 | 273.6136 | 264.9808 | 287.1045 | 232.4554 | 276.655 | 237.698 | 206.552 | 245.0058 | 243.3997 | 213.9203 | 209.0829 | 192.7252 | 172.6055
| Nov | 334.128 | 301.3888 | 273.2035 | 217.4742 | 242.6095 | 213.6177 | 196.666 | 247.9304 | 198.7406 | 181.3573 | 237.996 | 198.6353 | 195.0623 | 175.0236 | 171.097 | 176.4437
| Dec | 303.1985 | 278.9164 | 220.3093 | 197.5392 | 242.6695 | 207.1365 | 185.9067 | 171.7616 | 180.9354 | 169.9416 | 170.7909 | 176.6443 | 170.906 | 172.3127 | 170.4825 | 180.0026
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:39 | 26-JAN-15:00 | 23-JAN-15:00 | 26-JAN-12:00 | 18-JAN-14:00 | 27-JAN-14:00 | 09-JAN-11:50 | 25-JAN-14:00 | 17-JAN-11:20 | 27-JAN-11:09 | 24-JAN-12:00 | 05-JAN-11:09 | 05-JAN-08:09 | 09-JAN-11:09 | 02-JAN-11:09
| Feb | 23-FEB-12:00 | 23-FEB-14:00 | 28-FEB-15:00 | 17-FEB-12:00 | 13-FEB-11:00 | 08-FEB-14:00 | 15-FEB-15:00 | 15-FEB-12:00 | 14-FEB-15:00 | 21-FEB-12:00 | 28-FEB-11:20 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-14:00 | 30-MAR-11:00 | 31-MAR-14:00 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-14:00 | 31-MAR-14:00 | 30-MAR-14:00 | 23-MAR-14:00 | 30-MAR-14:00 | 01-MAR-11:20 | 14-MAR-07:10
| Apr | 03-APR-13:00 | 21-APR-14:00 | 26-APR-14:00 | 21-APR-13:00 | 11-APR-15:00 | 21-APR-14:00 | 14-APR-13:00 | 04-APR-14:00 | 21-APR-14:00 | 18-APR-13:00 | 07-APR-13:00 | 25-APR-14:00 | 14-APR-14:00 | 06-APR-14:00 | 04-APR-14:00 | 24-APR-11:00
| May | 24-MAY-14:00 | 18-MAY-11:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-11:00 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-14:00 | 31-MAY-14:00 | 04-MAY-13:00 | 30-MAY-14:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-14:00 | 31-MAY-13:00 | 24-MAY-14:00
| Jun | 28-JUN-11:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-13:50 | 27-JUN-15:00 | 15-JUN-13:09 | 30-JUN-11:00 | 29-JUN-13:00 | 28-JUN-13:00 | 08-JUN-11:00 | 28-JUN-11:00 | 29-JUN-11:00 | 30-JUN-12:00 | 14-JUN-14:00 | 20-JUN-14:00
| Jul | 13-JUL-15:09 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:50 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-11:00 | 31-JUL-15:20 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-13:00 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-15:09 | 04-AUG-15:00 | 15-AUG-11:00 | 17-AUG-13:00 | 01-AUG-15:20 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-13:00
| Sep | 06-SEP-11:00 | 20-SEP-11:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-14:00 | 08-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 05-SEP-13:00 | 13-SEP-14:00 | 06-SEP-11:00 | 05-SEP-13:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 07-SEP-14:00
| Oct | 06-OCT-11:00 | 30-OCT-10:50 | 02-OCT-14:00 | 12-OCT-15:00 | 19-OCT-11:00 | 03-OCT-14:00 | 31-OCT-12:00 | 03-OCT-11:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-11:00 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 06-OCT-14:00 | 31-OCT-07:10
| Nov | 01-NOV-11:00 | 27-NOV-12:00 | 13-NOV-14:00 | 22-NOV-14:00 | 20-NOV-12:00 | 10-NOV-12:00 | 08-NOV-12:00 | 03-NOV-13:00 | 08-NOV-14:00 | 03-NOV-11:00 | 02-NOV-11:00 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:50 | 09-NOV-11:50 | 30-NOV-10:20
| Dec | 15-DEC-14:00 | 19-DEC-14:00 | 13-DEC-12:00 | 13-DEC-12:00 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 06-DEC-11:20 | 08-DEC-14:00 | 01-DEC-11:09 | 05-DEC-11:20 | 21-DEC-14:00 | 20-DEC-11:09 | 18-DEC-08:09 | 20-DEC-11:09 | 29-DEC-11:09
Source Energy
| Total Source Energy (GJ) | 14099.05 | 14361.21 | 12384.95 | 12137.27 | 10028.5 | 12870.62 | 10178.97 | 13096.2 | 11462.27 | 6437.38 | 13076.37 | 11487.26 | 13396.37 | 12426.98 | 13423.17 | 16623.72
| Total Source Energy (MJ/m2) | 2051.96 | 2090.12 | 1802.5 | 1766.45 | 1459.54 | 1873.18 | 1481.44 | 1906.01 | 1668.21 | 936.89 | 1903.12 | 1671.85 | 1949.7 | 1808.61 | 1953.6 | 2419.4
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
| Total Building | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75 | 971.75
Emissions
| Carbon Equivalent (kg) | 321476.1871 | 359555.8202 | 322014.2009 | 298942.8162 | 108499.5932 | 329675.3022 | 113679.9532 | 266744.9072 | 369482.0851 | 82194.7034 | 489475.7149 | 362274.1167 | 336221.1052 | 331224.0081 | 330961.2228 | 328895.5889
| CO2 (kg) | 747818.7124 | 906978.743 | 762894.0159 | 689692.7565 | 291667.6128 | 787438.7058 | 307664.1459 | 616852.5341 | 872682.5229 | 208117.7818 | 1150910 | 860096.3865 | 804843.54 | 793610.4141 | 797906.0593 | 865091.3892
| NOX (kg) | 1304.1027 | 1177.4545 | 1265.8085 | 1278.304 | 250.9686 | 1264.538 | 266.1441 | 1142.2971 | 1479.731 | 283.8215 | 1997.9599 | 1439.2321 | 1333.8183 | 1305.4261 | 1297.6131 | 976.9108
| SO2 (kg) | 4924.4417 | 4963.1165 | 4150.4923 | 3200.4478 | 2475.5949 | 5170.3454 | 2358.8883 | 3218.2421 | 3725.3123 | 606.8501 | 5719.3849 | 3567.8934 | 1968.0145 | 2119.4862 | 1870.5971 | 4011.2716
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0225 | 0.014 | 0.0113 | 0.0118 | 0.0012 | 0.0098 | 0.0012 | 0.0131 | 0.0146 | 0.0025 | 0.0175 | 0.0141 | 0.0147 | 0.0149 | 0.014 | 0.0142
| Water for Electricity (m3) | 609.456 | 1692.93 | 30658.3 | 5692.49 | 14936.5 | 25785 | 14231.5 | 200.1327 | 3873.43 | 8016.69 | 1316.54 | 3709.62 | 1293.17 | 50266.8 | 1229.04 | 804.7712

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4472.53 | 650.93 | 650.93
Net Site Energy | 4472.53 | 650.93 | 650.93
Total Source Energy | 14099.05 | 2051.96 | 2051.96
Net Source Energy | 14099.05 | 2051.96 | 2051.96
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 23.66 | 0 | 0 | 0 | 0
Cooling | 1288.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 211.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0.01 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 72.94 | 0 | 0 | 0 | 971.75
Refrigeration | 78.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 4141.59 | 330.94 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 5.835 | 0.251 | 0.11 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 5.83 | 0.25 | 0.108
North Total or Average |  |  | 324.79 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 570.4 | 5.83 | 0.249 | 0.107
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 294639.28 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16119.98 | 10898.45 | 5221.53 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28686.23 | 19394.28 | 9291.95 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 137539.69 | 92988.28 | 44551.41 | 0.68 | 3.49
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 131626.61 | 88990.54 | 42636.07 | 0.68 | 3.49
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 100997.27 | 68282.56 | 32714.71 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 104229.8 | 70468.02 | 33761.78 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7577.95 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7073.34 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7383.21 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7310.09 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7317.16 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7496.64 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7501.12 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7565.63 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5799.1 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5773.83 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5826.21 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15328.67 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5062.14 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12422.05 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5868.25 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18493.86 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18051.95 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18147.67 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18558.72 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18579.61 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12647.15 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14631.09 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 25132.51 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 43417.07 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 87737.56 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 16478.83 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 15770.38 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 12100.63 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 12487.93 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.65 | 752.96 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.16 | 1315.99 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.54 | 10390.59 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.3 | 9943.88 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.07 | 7757.83 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.2 | 8006.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1622.41 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 57811.0134 | 100.1361 | 375.3447 | 0 | 0.0017 | 46452.6849 | 24784.051
February | 53245.2256 | 92.652 | 349.0413 | 0 | 0.0016 | 43197.7029 | 22869.1881
March | 62181.2547 | 108.1502 | 407.216 | 0 | 0.0019 | 50397.4223 | 26702.1286
April | 61267.6732 | 106.8845 | 403.7775 | 0 | 0.0018 | 49972.1197 | 26342.2073
May | 72512.8068 | 126.678 | 479.2709 | 0 | 0.0022 | 59315.4311 | 31194.6988
June | 75397.9272 | 131.8067 | 499.0364 | 0 | 0.0023 | 61761.7139 | 32444.7311
July | 53408.4234 | 93.33 | 353.2123 | 0 | 0.0016 | 43714.2109 | 22978.7631
August | 55870.6564 | 97.6089 | 369.3093 | 0 | 0.0017 | 45706.3815 | 24035.7506
September | 69668.5972 | 121.7647 | 460.9082 | 0 | 0.0021 | 57042.8713 | 29976.6826
October | 68371.5948 | 119.3856 | 451.4449 | 0 | 0.0021 | 55871.5892 | 29407.3769
November | 62384.8197 | 108.8022 | 410.8941 | 0 | 0.0019 | 50852.8562 | 26819.3979
December | 55698.7201 | 96.9036 | 364.9859 | 0 | 0.0017 | 45171.0003 | 23921.2112
Annual Sum or Average | 747818.7124 | 1304.1027 | 4924.4417 | 0 | 0.0225 | 609455.9841 | 321476.1871
Minimum of Months | 53245.2256 | 92.652 | 349.0413 | 0 | 0.0016 | 43197.7029 | 22869.1881
Maximum of Months | 75397.9272 | 131.8067 | 499.0364 | 0 | 0.0023 | 61761.7139 | 32444.7311
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 315672000000 | 313805.995 | 06-JAN-12:00 | 80527.626 | 79091.122 | 19530.817 | 0 | 132042.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2613.732 | 0 | 0
February | 293552000000 | 322813.086 | 23-FEB-12:00 | 80527.626 | 79091.122 | 22436.405 | 0 | 138144.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2613.369 | 0 | 0
March | 342478000000 | 322824.601 | 13-MAR-14:00 | 80527.626 | 73092.045 | 26360.265 | 0 | 140204.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2640.06 | 0 | 0
April | 339588000000 | 332902.969 | 03-APR-13:00 | 80527.626 | 75091.738 | 28786.339 | 0 | 145848.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2648.604 | 0 | 0
May | 403081000000 | 346114.24 | 24-MAY-14:00 | 80527.626 | 73092.045 | 30704.97 | 0 | 159078.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2710.971 | 0 | 0
June | 419705000000 | 352202.076 | 28-JUN-11:00 | 80527.626 | 79091.122 | 29773.513 | 0 | 160113.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2696.014 | 0 | 0
July | 297062000000 | 268845.849 | 13-JUL-15:09 | 44737.57 | 40636.785 | 27816.881 | 0 | 153098.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.595 | 0 | 0
August | 310600000000 | 277226.269 | 21-AUG-13:00 | 44737.57 | 41836.601 | 28328.243 | 0 | 159739.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2583.9 | 0 | 0
September | 387638000000 | 350859.7 | 06-SEP-11:00 | 80527.626 | 79091.122 | 29837.611 | 0 | 158715.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2687.708 | 0 | 0
October | 379678000000 | 346855.554 | 06-OCT-11:00 | 80527.626 | 79091.122 | 29348.728 | 0 | 155223.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2664.25 | 0 | 0
November | 345573000000 | 334127.99 | 01-NOV-11:00 | 80527.626 | 79091.122 | 25416.22 | 0 | 146460.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2632.466 | 0 | 0
December | 306962000000 | 303198.499 | 15-DEC-14:00 | 80527.626 | 75091.738 | 21435.873 | 0 | 123546.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2597.186 | 0 | 0
Annual Sum or Average | 4141590000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 293552000000 | 268845.849 |  | 44737.57 | 40636.785 | 19530.817 | 0 | 123546.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.595 | 0 | 0
Maximum of Months | 419705000000 | 352202.076 |  | 80527.626 | 79091.122 | 30704.97 | 0 | 160113.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2710.971 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 102786.88 | 3788.85 | 0 | 106575.74
Cost per Total Building Area ($/m2) | 14.96 | 0.55 | 0 | 15.51
Cost per Net Conditioned Building Area ($/m2) | 14.96 | 0.55 | 0 | 15.51

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4438.98 | 646.05 | 646.05
Net Site Energy | 4438.98 | 646.05 | 646.05
Total Source Energy | 14361.21 | 2090.12 | 2090.12
Net Source Energy | 14361.21 | 2090.12 | 2090.12
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 362.71 | 0 | 0 | 0 | 0
Cooling | 933.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 173.33 | 0 | 0 | 0 | 0 | 0
Pumps | 0.37 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 96.33 | 0 | 0 | 0 | 971.75
Refrigeration | 74.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3745.61 | 693.38 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 5.835 | 0.251 | 0.11 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 5.83 | 0.25 | 0.108
North Total or Average |  |  | 324.79 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 570.4 | 5.83 | 0.249 | 0.107
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 376051.69 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16025.78 | 10834.76 | 5191.02 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29207.89 | 19746.96 | 9460.92 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 140955.96 | 95297.96 | 45658 | 0.68 | 3.49
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 135837.65 | 91837.56 | 44000.1 | 0.68 | 3.49
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 103738.79 | 70136.06 | 33602.74 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 107681.27 | 72801.5 | 34879.77 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7779.82 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7091.27 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7720.55 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7645.9 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7653.15 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7646.33 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7650.97 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7717.74 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5893.2 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5867.4 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5922.08 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15541.18 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5376.84 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12571.67 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5867.13 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19379.89 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18943 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19043.93 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18591.01 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18612.3 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12677.76 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15168.86 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 32984.47 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 57178.95 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 115825.61 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 33360.81 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 32149.43 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 24552.42 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 25485.5 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.65 | 748.56 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.18 | 1339.92 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.68 | 10648.68 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.47 | 10262.01 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.18 | 7968.41 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.34 | 8271.24 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2070.7 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 70295.9564 | 89.426 | 358.9926 | 0 | 0.001 | 122444.8336 | 27631.2844
February | 62399.4586 | 79.2805 | 317.2641 | 0 | 0.0009 | 108211.6232 | 24514.4978
March | 71117.0111 | 92.1182 | 386.2623 | 0 | 0.0011 | 131753.8833 | 28166.4012
April | 71104.269 | 92.7431 | 395.1769 | 0 | 0.0011 | 134797.5667 | 28244.0367
May | 88479.6783 | 115.6656 | 495.3749 | 0 | 0.0014 | 168976.954 | 35179.3099
June | 98892.7428 | 129.4047 | 555.448 | 0 | 0.0016 | 189468.9661 | 39335.8368
July | 71313.4855 | 93.3183 | 400.5736 | 0 | 0.0011 | 136639.7558 | 28366.1083
August | 72555.2869 | 94.9189 | 407.2065 | 0 | 0.0011 | 138902.1833 | 28856.9035
September | 84993.462 | 111.168 | 476.6942 | 0 | 0.0013 | 162605.029 | 33800.9078
October | 80011.5055 | 104.4526 | 445.9631 | 0 | 0.0013 | 152121.5033 | 31793.9714
November | 69528.0935 | 90.2649 | 380.501 | 0 | 0.0011 | 129789.6515 | 27563.5012
December | 66287.7933 | 84.6938 | 343.6594 | 0 | 0.001 | 117216.7589 | 26103.0611
Annual Sum or Average | 906978.743 | 1177.4545 | 4963.1165 | 0 | 0.014 | 1692930 | 359555.8202
Minimum of Months | 62399.4586 | 79.2805 | 317.2641 | 0 | 0.0009 | 108211.6232 | 24514.4978
Maximum of Months | 98892.7428 | 129.4047 | 555.448 | 0 | 0.0016 | 189468.9661 | 39335.8368
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 270909000000 | 281891.094 | 03-JAN-12:39 | 80527.626 | 79091.122 | 13666.134 | 0 | 106007.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2599.163 | 0 | 0
February | 239418000000 | 266028.383 | 23-FEB-14:00 | 80527.626 | 75091.738 | 19481.827 | 0 | 88292.733 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2634.453 | 0 | 0
March | 291506000000 | 276729.261 | 29-MAR-11:00 | 80527.626 | 79091.122 | 14030.124 | 0 | 100467.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2612.687 | 0 | 0
April | 298240000000 | 308528.728 | 21-APR-14:00 | 80527.626 | 73092.045 | 23945.179 | 0 | 128326.038 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2637.837 | 0 | 0
May | 373862000000 | 352084.666 | 18-MAY-11:00 | 80527.626 | 79091.122 | 28718.39 | 0 | 161059.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2687.976 | 0 | 0
June | 419200000000 | 353375.846 | 13-JUN-14:00 | 80527.626 | 73092.045 | 31130.224 | 0 | 165890.434 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2735.516 | 0 | 0
July | 302316000000 | 285535.265 | 18-JUL-11:00 | 44737.57 | 44636.17 | 28105.675 | 0 | 165471.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2584.591 | 0 | 0
August | 307321000000 | 279650.328 | 31-AUG-15:00 | 44737.57 | 40636.785 | 28934.137 | 0 | 162743.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2598.102 | 0 | 0
September | 359764000000 | 357207.798 | 20-SEP-11:00 | 80527.626 | 79091.122 | 30887.483 | 0 | 164004.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2696.892 | 0 | 0
October | 336569000000 | 334927.055 | 30-OCT-10:50 | 80527.626 | 79091.122 | 22906.095 | 0 | 148456.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3945.918 | 0 | 0
November | 287160000000 | 301388.837 | 27-NOV-12:00 | 80527.626 | 79091.122 | 15083.956 | 0 | 124080.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2605.825 | 0 | 0
December | 259342000000 | 278916.394 | 19-DEC-14:00 | 80527.626 | 75091.738 | 17340.215 | 0 | 103347.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2609.763 | 0 | 0
Annual Sum or Average | 3745610000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 239418000000 | 266028.383 |  | 44737.57 | 40636.785 | 13666.134 | 0 | 88292.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2584.591 | 0 | 0
Maximum of Months | 419200000000 | 357207.798 |  | 80527.626 | 79091.122 | 31130.224 | 0 | 165890.434 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 3945.918 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 126163.04 | 5628.16 | 0 | 131791.19
Cost per Total Building Area ($/m2) | 18.36 | 0.82 | 0 | 19.18
Cost per Net Conditioned Building Area ($/m2) | 18.36 | 0.82 | 0 | 19.18

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4294.8 | 625.06 | 625.06
Net Site Energy | 4294.8 | 625.06 | 625.06
Total Source Energy | 12384.95 | 1802.5 | 1802.5
Net Source Energy | 12384.95 | 1802.5 | 1802.5
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 260.09 | 0 | 0 | 0 | 0
Cooling | 883.19 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 193.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0.25 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 84.75 | 0 | 0 | 0 | 971.75
Refrigeration | 75.17 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3715.61 | 579.19 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 5.835 | 0.251 | 0.11 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 1A2AB | 1.78 | 1.78 | 5.765 | 0.174 | 0.029 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 5.83 | 0.25 | 0.108
North Total or Average |  |  | 324.79 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 570.4 | 5.83 | 0.249 | 0.107
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 328636.16 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15351.71 | 10379.03 | 4972.68 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28411.15 | 19208.3 | 9202.85 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 135806.65 | 91816.59 | 43990.05 | 0.68 | 3.49
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 139660.7 | 94422.26 | 45238.44 | 0.68 | 3.49
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 105602.98 | 71396.4 | 34206.58 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 110692.96 | 74837.65 | 35855.31 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7202.65 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6857.18 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7933.9 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7864.1 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7871.62 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7701.1 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7705.54 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7771.67 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5239.43 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5214.11 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5276.47 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15013.55 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5450.04 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10356.26 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4774.84 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19642.16 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19272.05 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19397.02 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17926.26 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17945.61 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12237.1 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14822.62 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 26658.32 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 47820.47 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 97721.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 23683.72 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 24355.84 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 18416.41 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 19304.07 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 717.07 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.14 | 1303.37 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.47 | 10259.66 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.62 | 10550.82 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.25 | 8111.6 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.46 | 8502.57 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1809.61 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 55767.0824 | 90.1209 | 285.9723 | 0 | 0.0008 | 2112260 | 23295.446
February | 50581.4977 | 81.9943 | 261.2139 | 0 | 0.0007 | 1929400 | 21154.9104
March | 61758.3095 | 102.2075 | 334.0906 | 0 | 0.0009 | 2467800 | 26041.3107
April | 60584.4503 | 101.0738 | 333.5926 | 0 | 0.0009 | 2464170 | 25628.1412
May | 71397.9481 | 119.5404 | 396.2179 | 0 | 0.0011 | 2926790 | 30245.5193
June | 85334.5098 | 143.1973 | 475.8959 | 0 | 0.0013 | 3515370 | 36181.9913
July | 62092.8963 | 104.1805 | 346.167 | 0 | 0.0009 | 2557080 | 26325.9054
August | 62789.1563 | 105.298 | 349.682 | 0 | 0.001 | 2583040 | 26615.9774
September | 74930.5672 | 125.6512 | 417.2417 | 0 | 0.0011 | 3082090 | 31761.8488
October | 65170.5251 | 108.8721 | 359.9102 | 0 | 0.001 | 2658580 | 27583.0148
November | 57211.7088 | 94.6381 | 309.1698 | 0 | 0.0008 | 2283720 | 24119.6215
December | 55275.3645 | 89.0343 | 281.3384 | 0 | 0.0008 | 2078020 | 23060.5142
Annual Sum or Average | 762894.0159 | 1265.8085 | 4150.4923 | 0 | 0.0113 | 30658300 | 322014.2009
Minimum of Months | 50581.4977 | 81.9943 | 261.2139 | 0 | 0.0007 | 1929400 | 21154.9104
Maximum of Months | 85334.5098 | 143.1973 | 475.8959 | 0 | 0.0013 | 3515370 | 36181.9913
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 255994000000 | 225069.182 | 26-JAN-15:00 | 80527.626 | 73092.045 | 16120.632 | 0 | 52822.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2506.432 | 0 | 0
February | 233833000000 | 245741.668 | 28-FEB-15:00 | 80527.626 | 73092.045 | 19590.253 | 0 | 69972.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2559.382 | 0 | 0
March | 299084000000 | 291340.04 | 17-MAR-14:00 | 80527.626 | 73092.045 | 25720.3 | 0 | 109334.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2665.43 | 0 | 0
April | 298643000000 | 302453.783 | 26-APR-14:00 | 80527.626 | 73092.045 | 27753.12 | 0 | 118393.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2687.309 | 0 | 0
May | 354709000000 | 342393.045 | 30-MAY-14:00 | 80527.626 | 73092.045 | 30456.649 | 0 | 155591.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2725.123 | 0 | 0
June | 426042000000 | 401215.623 | 28-JUN-15:00 | 80527.626 | 73092.045 | 35307.295 | 0 | 209661.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2627.422 | 0 | 0
July | 309903000000 | 316449.54 | 11-JUL-15:00 | 44737.57 | 40636.785 | 31187.942 | 0 | 197372.991 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2514.246 | 0 | 0
August | 313050000000 | 318300.92 | 01-AUG-15:00 | 44737.57 | 40636.785 | 31577.151 | 0 | 198858.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2491.048 | 0 | 0
September | 373532000000 | 368109.364 | 08-SEP-13:00 | 80527.626 | 75091.738 | 31533.416 | 0 | 178225.061 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2731.518 | 0 | 0
October | 322204000000 | 305492.745 | 02-OCT-14:00 | 80527.626 | 73092.045 | 29136.867 | 0 | 120033.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2702.731 | 0 | 0
November | 276774000000 | 273203.459 | 13-NOV-14:00 | 80527.626 | 75091.738 | 21889.354 | 0 | 93041.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2653.519 | 0 | 0
December | 251844000000 | 220309.327 | 13-DEC-12:00 | 80527.626 | 79091.122 | 13573.531 | 0 | 44621.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2495.146 | 0 | 0
Annual Sum or Average | 3715610000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 233833000000 | 220309.327 |  | 44737.57 | 40636.785 | 13573.531 | 0 | 44621.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2491.048 | 0 | 0
Maximum of Months | 426042000000 | 401215.623 |  | 80527.626 | 79091.122 | 35307.295 | 0 | 209661.235 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2731.518 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 97417.35 | 4859.34 | 0 | 102276.69
Cost per Total Building Area ($/m2) | 14.18 | 0.71 | 0 | 14.89
Cost per Net Conditioned Building Area ($/m2) | 14.18 | 0.71 | 0 | 14.89

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4285.74 | 623.74 | 623.74
Net Site Energy | 4285.74 | 623.74 | 623.74
Total Source Energy | 12137.27 | 1766.45 | 1766.45
Net Source Energy | 12137.27 | 1766.45 | 1766.45
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 651.5 | 0 | 0 | 0 | 0
Cooling | 502.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 144.06 | 0 | 0 | 0 | 0 | 0
Pumps | 0.64 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 117.67 | 0 | 0 | 0 | 971.75
Refrigeration | 71.71 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3282.23 | 1003.51 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.252 | 0.162 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.252 | 0.162 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.252 | 0.159
North Total or Average |  |  | 324.79 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.252 | 0.157
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 365118.85 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15602.93 | 10548.88 | 5054.05 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29021.11 | 19620.69 | 9400.43 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 130487.87 | 88220.66 | 42267.21 | 0.68 | 3.49
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 123710.94 | 83638.89 | 40072.05 | 0.68 | 3.49
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 95887.14 | 64827.69 | 31059.45 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 98552.64 | 66629.79 | 31922.85 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6590.8 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6403.53 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6473.36 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6414.9 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6421.09 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6262.86 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6266.55 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6321.83 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5209.03 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5183.43 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5237.18 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14050.36 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4827.81 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10983.43 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5486.3 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17872.93 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17519.64 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17611.13 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16669.42 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16685.12 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11332.65 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13786.98 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 34642.9 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 61248.27 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 124945.98 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 35795.06 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 33936.03 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 26303.48 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 27034.67 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.63 | 728.8 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.17 | 1331.35 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.25 | 9857.85 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 4.98 | 9345.88 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.86 | 7365.31 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.97 | 7570.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2010.5 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 59041.0992 | 103.1316 | 243.1033 | 0 | 0.0009 | 432335.5698 | 25009.3857
February | 53410.5461 | 93.3947 | 220.4016 | 0 | 0.0008 | 391963.9523 | 22633.41
March | 56811.6275 | 104.6324 | 260.371 | 0 | 0.001 | 463103.4005 | 24563.2593
April | 54241.3674 | 102.1414 | 259.5852 | 0 | 0.001 | 461727.7037 | 23659.0923
May | 62608.1359 | 119.0639 | 305.3479 | 0 | 0.0011 | 543137.3831 | 27416.3143
June | 70870.6202 | 135.271 | 348.067 | 0 | 0.0013 | 619128.4307 | 31080.1109
July | 48913.7961 | 93.3601 | 240.2216 | 0 | 0.0009 | 427297.1536 | 21450.8422
August | 51101.3431 | 97.5066 | 250.8235 | 0 | 0.0009 | 446155.1822 | 22407.5136
September | 65088.6386 | 124.2204 | 319.5988 | 0 | 0.0012 | 568490.2223 | 28543.0997
October | 56355.1423 | 106.1189 | 269.6873 | 0 | 0.001 | 479696.3513 | 24580.8201
November | 54512.6858 | 99.1869 | 243.8961 | 0 | 0.0009 | 433788.7323 | 23457.398
December | 56737.7543 | 100.2761 | 239.3446 | 0 | 0.0009 | 425663.9201 | 24141.57
Annual Sum or Average | 689692.7565 | 1278.304 | 3200.4478 | 0 | 0.0118 | 5692490 | 298942.8162
Minimum of Months | 48913.7961 | 93.3601 | 220.4016 | 0 | 0.0008 | 391963.9523 | 21450.8422
Maximum of Months | 70870.6202 | 135.271 | 348.067 | 0 | 0.0013 | 619128.4307 | 31080.1109
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 249281000000 | 199003.833 | 23-JAN-15:00 | 80527.626 | 73092.045 | 14731.119 | 0 | 28268.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2384.22 | 0 | 0
February | 226003000000 | 193542.508 | 17-FEB-12:00 | 80527.626 | 79091.122 | 9277.952 | 0 | 22218.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2427.395 | 0 | 0
March | 267021000000 | 226353.029 | 28-MAR-14:00 | 80527.626 | 73092.045 | 17782.527 | 0 | 52419.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2530.854 | 0 | 0
April | 266228000000 | 265668.7 | 21-APR-13:00 | 80527.626 | 75091.738 | 18885.479 | 0 | 88573.741 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2590.112 | 0 | 0
May | 313168000000 | 312468.389 | 15-MAY-14:00 | 80527.626 | 73092.045 | 25826.36 | 0 | 130366.561 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2655.79 | 0 | 0
June | 356984000000 | 330522.029 | 19-JUN-14:00 | 80527.626 | 73092.045 | 28855.993 | 0 | 145329.377 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2716.984 | 0 | 0
July | 246375000000 | 270170.852 | 03-JUL-15:00 | 44737.57 | 40636.785 | 27523.59 | 0 | 154668.606 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2604.298 | 0 | 0
August | 257249000000 | 245919.217 | 17-AUG-13:00 | 44737.57 | 41836.601 | 13857.863 | 0 | 142914.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2572.972 | 0 | 0
September | 327786000000 | 325919.404 | 11-SEP-13:00 | 80527.626 | 75091.738 | 28207.914 | 0 | 139433.819 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2658.307 | 0 | 0
October | 276588000000 | 273613.597 | 12-OCT-15:00 | 80527.626 | 73092.045 | 17166.098 | 0 | 100249.928 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2577.891 | 0 | 0
November | 250118000000 | 217474.214 | 22-NOV-14:00 | 80527.626 | 75091.738 | 14635.494 | 0 | 44698.2 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2521.155 | 0 | 0
December | 245434000000 | 197539.178 | 13-DEC-12:00 | 80527.626 | 79091.122 | 9183.427 | 0 | 26284.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2452.569 | 0 | 0
Annual Sum or Average | 3282230000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 226003000000 | 193542.508 |  | 44737.57 | 40636.785 | 9183.427 | 0 | 22218.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2384.22 | 0 | 0
Maximum of Months | 356984000000 | 330522.029 |  | 80527.626 | 79091.122 | 28855.993 | 0 | 154668.606 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2716.984 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 89496.04 | 10013.39 | 0 | 99509.43
Cost per Total Building Area ($/m2) | 13.03 | 1.46 | 0 | 14.48
Cost per Net Conditioned Building Area ($/m2) | 13.03 | 1.46 | 0 | 14.48

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3566.13 | 519.01 | 519.01
Net Site Energy | 3566.13 | 519.01 | 519.01
Total Source Energy | 10028.5 | 1459.54 | 1459.54
Net Source Energy | 10028.5 | 1459.54 | 1459.54
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 157.77 | 0 | 0 | 0 | 0
Cooling | 308.8 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 118.66 | 0 | 0 | 0 | 0 | 0
Pumps | 0.07 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 111.47 | 0 | 0 | 0 | 971.75
Refrigeration | 71.69 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3062.55 | 503.58 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.252 | 0.162 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.252 | 0.162 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.252 | 0.159
North Total or Average |  |  | 324.79 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.252 | 0.157
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 240677.66 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13811.47 | 9337.7 | 4473.77 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 94425.5 | 66994.22 | 27431.29 | 0.71 | 3.66
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 97633.51 | 67805.55 | 29827.95 | 0.69 | 3.59
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 77691.4 | 53170.93 | 24520.47 | 0.68 | 3.13
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 78151.26 | 54245.76 | 23905.49 | 0.69 | 3.14
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5837.39 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5297.94 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5934.08 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5884.64 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5890.24 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5517.5 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5520.59 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5568.29 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4534.37 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4510.3 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4563.71 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11536.32 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4241.12 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9451.35 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4842.49 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16298.97 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15991.54 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16080.97 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13514.63 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13527.86 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9208.29 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11625.38 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 22395.59 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 43168.3 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 91250.81 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 14741.34 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 14421.08 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 11035.44 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 11526.86 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 645.13 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.32 | 8241.76 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.23 | 8062.71 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.23 | 3537.47 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.57 | 622 | 3.38 | 3695 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1325.27 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 25571.522 | 22.0616 | 206.6066 | 0 | 0.0001 | 1246530 | 9480.6954
February | 22887.89 | 19.7435 | 185.4304 | 0 | 0.0001 | 1118760 | 8487.278
March | 26410.2808 | 22.7626 | 217.4376 | 0 | 0.0001 | 1311890 | 9804.0361
April | 24124.8865 | 20.76 | 204.4972 | 0 | 0.0001 | 1233840 | 8973.5766
May | 26118.1794 | 22.4535 | 225.2842 | 0 | 0.0001 | 1359270 | 9726.879
June | 26262.5943 | 22.5653 | 228.7435 | 0 | 0.0001 | 1380150 | 9787.4154
July | 17806.0854 | 15.2956 | 155.7643 | 0 | 0.0001 | 939822.9407 | 6637.9468
August | 19602.3026 | 16.8368 | 171.7869 | 0 | 0.0001 | 1036500 | 7308.5048
September | 26327.3256 | 22.6081 | 231.6044 | 0 | 0.0001 | 1397420 | 9818.5474
October | 26433.2173 | 22.7109 | 230.4113 | 0 | 0.0001 | 1390210 | 9851.5567
November | 25167.2806 | 21.6593 | 212.92 | 0 | 0.0001 | 1284650 | 9360.0486
December | 24956.0482 | 21.5112 | 205.1086 | 0 | 0.0001 | 1237500 | 9263.1084
Annual Sum or Average | 291667.6128 | 250.9686 | 2475.5949 | 0 | 0.0012 | 14936500 | 108499.5932
Minimum of Months | 17806.0854 | 15.2956 | 155.7643 | 0 | 0.0001 | 939822.9407 | 6637.9468
Maximum of Months | 26433.2173 | 22.7626 | 231.6044 | 0 | 0.0001 | 1397420 | 9851.5567
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 255585000000 | 239217.795 | 26-JAN-12:00 | 80527.626 | 79091.122 | 13341.482 | 0 | 63694.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2563.277 | 0 | 0
February | 229389000000 | 231494.763 | 13-FEB-11:00 | 80527.626 | 79091.122 | 12472.717 | 0 | 56380.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3022.479 | 0 | 0
March | 268986000000 | 226719.724 | 30-MAR-11:00 | 80527.626 | 79091.122 | 12581.63 | 0 | 51999.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2520.153 | 0 | 0
April | 252983000000 | 237687.305 | 11-APR-15:00 | 80527.626 | 73092.045 | 12676.226 | 0 | 68879.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2512.379 | 0 | 0
May | 278701000000 | 258052.073 | 30-MAY-11:00 | 80527.626 | 79091.122 | 14026.535 | 0 | 81860.578 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2546.207 | 0 | 0
June | 282982000000 | 253562.242 | 28-JUN-13:50 | 80527.626 | 75091.738 | 16251.511 | 0 | 79134.783 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2556.581 | 0 | 0
July | 192699000000 | 157261.153 | 10-JUL-15:50 | 44737.57 | 40636.785 | 10348.818 | 0 | 59198.5 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2339.476 | 0 | 0
August | 212521000000 | 188791.544 | 08-AUG-15:09 | 44737.57 | 40636.785 | 11223.365 | 0 | 89724.808 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2469.009 | 0 | 0
September | 286523000000 | 279901.842 | 25-SEP-14:00 | 80527.626 | 73092.045 | 20554.229 | 0 | 103111.318 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2616.616 | 0 | 0
October | 285046000000 | 264980.828 | 19-OCT-11:00 | 80527.626 | 79091.122 | 17005.987 | 0 | 85770.974 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 2585.105 | 0 | 0
November | 263402000000 | 242609.517 | 20-NOV-12:00 | 80527.626 | 79091.122 | 14252.001 | 0 | 66148.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2590.367 | 0 | 0
December | 253734000000 | 242669.527 | 19-DEC-12:00 | 80527.626 | 79091.122 | 13664.632 | 0 | 66815.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2570.534 | 0 | 0
Annual Sum or Average | 3062550000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 192699000000 | 157261.153 |  | 44737.57 | 40636.785 | 10348.818 | 0 | 51999.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2339.476 | 0 | 0
Maximum of Months | 286523000000 | 279901.842 |  | 80527.626 | 79091.122 | 20554.229 | 0 | 103111.318 | 0 | 0.013 | 0 | 0 | 0 | 0 | 0 | 3022.479 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 109544.47 | 4269.83 | 0 | 113814.3
Cost per Total Building Area ($/m2) | 15.94 | 0.62 | 0 | 16.56
Cost per Net Conditioned Building Area ($/m2) | 15.94 | 0.62 | 0 | 16.56

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4086.4 | 594.73 | 594.73
Net Site Energy | 4086.4 | 594.73 | 594.73
Total Source Energy | 12870.62 | 1873.18 | 1873.18
Net Source Energy | 12870.62 | 1873.18 | 1873.18
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 368.13 | 0 | 0 | 0 | 0
Cooling | 579.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 167.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0.37 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 100.32 | 0 | 0 | 0 | 971.75
Refrigeration | 72.87 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3383.61 | 702.79 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.252 | 0.162 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.252 | 0.162 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.252 | 0.162 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.252 | 0.162 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 3AB | 1.78 | 1.78 | 2.627 | 0.229 | 0.008 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.252 | 0.162 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.252 | 0.162 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.252 | 0.162 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.252 | 0.162 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.252 | 0.162 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.252 | 0.162 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.252 | 0.159
North Total or Average |  |  | 324.79 | 3.24 | 0.252 | 0.162
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.252 | 0.157
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 295050.36 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14350.19 | 9701.92 | 4648.27 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26622.1 | 17998.76 | 8623.35 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 106741.67 | 74173.72 | 32567.95 | 0.69 | 3.59
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 114535.82 | 78539.56 | 35996.25 | 0.69 | 3.55
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 90297.31 | 61048.49 | 29248.81 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 91215.78 | 62431.33 | 28784.45 | 0.68 | 3.55
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5630.18 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5785.93 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6410.65 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6357.03 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6363.98 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6212.06 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6215.23 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6267.29 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4269.27 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4243.86 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4308.61 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12497.22 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4184.19 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8168.01 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4146.84 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16202.31 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15853.01 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15969.73 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14912.22 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14925.27 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10166.86 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12075.55 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 26938.28 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 49975.2 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 105639.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 24473.39 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 25347.93 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 19227.62 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 20085.14 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 670.29 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.63 | 8828.23 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.79 | 9143.7 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.64 | 6935.94 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.8 | 7245.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1624.67 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 62861.8578 | 97.4143 | 379.5286 | 0 | 0.0007 | 1892610 | 25950.8476
February | 54909.6933 | 86.9667 | 349.146 | 0 | 0.0007 | 1741180 | 22862.9458
March | 63605.6896 | 101.0619 | 407.4699 | 0 | 0.0008 | 2032050 | 26517.2344
April | 61955.2212 | 100.1958 | 413.4048 | 0 | 0.0008 | 2061710 | 26011.6999
May | 72800.0181 | 118.2125 | 490.2622 | 0 | 0.0009 | 2445030 | 30614.5478
June | 85873.099 | 139.8043 | 581.7201 | 0 | 0.0011 | 2901160 | 36149.9695
July | 60954.2668 | 99.2256 | 412.8213 | 0 | 0.0008 | 2058830 | 25658.8574
August | 62958.3766 | 102.4578 | 426.1102 | 0 | 0.0008 | 2125100 | 26499.3496
September | 74516.4704 | 121.238 | 504.062 | 0 | 0.0009 | 2513860 | 31361.1435
October | 66853.1024 | 108.2902 | 447.7161 | 0 | 0.0008 | 2232840 | 28086.0793
November | 59621.7582 | 95.0046 | 384.5113 | 0 | 0.0007 | 1917570 | 24884.6752
December | 60529.1524 | 94.6663 | 373.5928 | 0 | 0.0007 | 1863050 | 25077.9522
Annual Sum or Average | 787438.7058 | 1264.538 | 5170.3454 | 0 | 0.0098 | 25785000 | 329675.3022
Minimum of Months | 54909.6933 | 86.9667 | 349.146 | 0 | 0.0007 | 1741180 | 22862.9458
Maximum of Months | 85873.099 | 139.8043 | 581.7201 | 0 | 0.0011 | 2901160 | 36149.9695
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 248357000000 | 196047.993 | 18-JAN-14:00 | 80527.626 | 75091.738 | 12929.729 | 0 | 25067.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2431.599 | 0 | 0
February | 228485000000 | 205265.5 | 08-FEB-14:00 | 80527.626 | 75091.738 | 14995.916 | 0 | 32180.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2469.353 | 0 | 0
March | 266654000000 | 226899.598 | 31-MAR-14:00 | 80527.626 | 73092.045 | 18750.335 | 0 | 52009.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2520.131 | 0 | 0
April | 270546000000 | 286094.709 | 21-APR-14:00 | 80527.626 | 73092.045 | 26348.009 | 0 | 103431.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2695.052 | 0 | 0
May | 320847000000 | 312645.914 | 31-MAY-15:00 | 80527.626 | 73092.045 | 26945.917 | 0 | 129472.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.038 | 0 | 0
June | 380702000000 | 359507.784 | 27-JUN-15:00 | 80527.626 | 73092.045 | 34282.42 | 0 | 168997.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.25 | 0 | 0
July | 270168000000 | 277663.328 | 24-JUL-15:00 | 44737.57 | 40636.785 | 27731.821 | 0 | 162094.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2462.454 | 0 | 0
August | 278864000000 | 270031.086 | 04-AUG-15:00 | 44737.57 | 40636.785 | 27217.112 | 0 | 154949.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2489.677 | 0 | 0
September | 329879000000 | 316658.315 | 08-SEP-14:00 | 80527.626 | 73092.045 | 28067.007 | 0 | 132259.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.941 | 0 | 0
October | 293002000000 | 287104.498 | 03-OCT-14:00 | 80527.626 | 73092.045 | 26921.928 | 0 | 103880.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2682.684 | 0 | 0
November | 251631000000 | 213617.734 | 10-NOV-12:00 | 80527.626 | 79091.122 | 14643.532 | 0 | 36887.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2468.055 | 0 | 0
December | 244477000000 | 207136.517 | 05-DEC-12:00 | 80527.626 | 79091.122 | 12455.022 | 0 | 32614.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2448.489 | 0 | 0
Annual Sum or Average | 3383610000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 228485000000 | 196047.993 |  | 44737.57 | 40636.785 | 12455.022 | 0 | 25067.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2431.599 | 0 | 0
Maximum of Months | 380702000000 | 359507.784 |  | 80527.626 | 79091.122 | 34282.42 | 0 | 168997.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.941 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 94013.52 | 5535.44 | 0 | 99548.96
Cost per Total Building Area ($/m2) | 13.68 | 0.81 | 0 | 14.49
Cost per Net Conditioned Building Area ($/m2) | 13.68 | 0.81 | 0 | 14.49

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3969.09 | 577.66 | 577.66
Net Site Energy | 3969.09 | 577.66 | 577.66
Total Source Energy | 10178.97 | 1481.44 | 1481.44
Net Source Energy | 10178.97 | 1481.44 | 1481.44
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 687.17 | 0 | 0 | 0 | 0
Cooling | 151.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.09 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 133.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0.52 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 129.59 | 0 | 0 | 0 | 971.75
Refrigeration | 68.66 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2917.98 | 1051.1 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 5.835 | 0.39 | 0.223 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 5.835 | 0.39 | 0.223 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.39 | 0.223 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.39 | 0.223 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.39 | 0.223 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.39 | 0.223 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 3C | 1.78 | 1.78 | 5.679 | 0.394 | 0.09 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 5.835 | 0.39 | 0.223 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.39 | 0.223 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.39 | 0.223 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 5.835 | 0.39 | 0.223 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.39 | 0.223 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 5.835 | 0.39 | 0.223 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.39 | 0.223 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 5.835 | 0.39 | 0.223 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 5.83 | 0.39 | 0.22
North Total or Average |  |  | 324.79 | 5.83 | 0.39 | 0.223
Non-North Total or Average |  |  | 570.4 | 5.83 | 0.39 | 0.219
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 449185.09 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17013.24 | 12662.4 | 4350.84 | 0.74 | 3.85
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24587.33 | 18686.81 | 5900.52 | 0.76 | 3.66
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44026.36 | 32767.37 | 11258.98 | 0.74 | 3.33
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 107268.34 | 83931.58 | 23336.76 | 0.78 | 4.04
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 132822.5 | 104568.56 | 28253.95 | 0.79 | 4.07
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 103040.47 | 80447.46 | 22593.01 | 0.78 | 4.03
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 107354.23 | 84528.28 | 22825.95 | 0.79 | 4.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7163.19 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8922.76 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11065.49 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10981.71 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10991.9 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8338.86 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8343.71 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8423.26 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5814.56 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5777.94 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5882.86 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18204.87 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8696.46 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9874.32 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4940.21 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 37634.74 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 36949.32 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 37134.13 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21541.64 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21561.18 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14677.57 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18179.91 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 38976.54 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 53624.62 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 100862.31 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 27399.23 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 34393.23 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 26191.37 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 27805.99 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.88 | 1015.76 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.33 | 1514.25 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.19 | 11620.57 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.78 | 14586.87 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.92 | 11108.3 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 6.29 | 11793.09 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2473.4 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 30635.014 | 26.6884 | 201.3086 | 0 | 0.0001 | 1214380 | 11217.0146
February | 24816.7957 | 21.4969 | 185.0477 | 0 | 0.0001 | 1116390 | 9153.7081
March | 29298.834 | 25.4215 | 210.9344 | 0 | 0.0001 | 1272540 | 10783.9283
April | 25512.556 | 22.0592 | 197.4683 | 0 | 0.0001 | 1191360 | 9432.4066
May | 26598.9749 | 22.9424 | 215.919 | 0 | 0.0001 | 1302710 | 9864.7104
June | 25945.3026 | 22.3601 | 213.9158 | 0 | 0.0001 | 1290640 | 9632.3614
July | 18209.0989 | 15.7097 | 147.1347 | 0 | 0.0001 | 887712.2922 | 6751.102
August | 19588.0733 | 16.9087 | 156.6087 | 0 | 0.0001 | 944865.696 | 7257.2722
September | 25333.3112 | 21.805 | 213.8242 | 0 | 0.0001 | 1290110 | 9420.2709
October | 26445.1341 | 22.7983 | 216.7088 | 0 | 0.0001 | 1307490 | 9813.8752
November | 26453.1446 | 22.8812 | 203.175 | 0 | 0.0001 | 1225780 | 9775.3567
December | 28827.9066 | 25.0727 | 196.8429 | 0 | 0.0001 | 1187480 | 10577.9469
Annual Sum or Average | 307664.1459 | 266.1441 | 2358.8883 | 0 | 0.0012 | 14231500 | 113679.9532
Minimum of Months | 18209.0989 | 15.7097 | 147.1347 | 0 | 0.0001 | 887712.2922 | 6751.102
Maximum of Months | 30635.014 | 26.6884 | 216.7088 | 0 | 0.0001 | 1307490 | 11217.0146
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 248994000000 | 182365.831 | 27-JAN-14:00 | 80527.626 | 75091.738 | 12173.91 | 0 | 12269.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2302.908 | 0 | 0
February | 228903000000 | 213132.561 | 15-FEB-15:00 | 80527.626 | 73092.045 | 13604.821 | 0 | 43417.603 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2490.459 | 0 | 0
March | 260918000000 | 199632.926 | 01-MAR-12:00 | 80527.626 | 79091.122 | 11521.076 | 0 | 26076.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2416.344 | 0 | 0
April | 244273000000 | 213375.716 | 14-APR-13:00 | 80527.626 | 75091.738 | 13140.011 | 0 | 42106.468 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2509.872 | 0 | 0
May | 267105000000 | 229486.931 | 17-MAY-13:00 | 80527.626 | 75091.738 | 13256.49 | 0 | 58024.427 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2586.646 | 0 | 0
June | 264630000000 | 232316.217 | 15-JUN-13:09 | 80527.626 | 75091.738 | 13012.144 | 0 | 61090.283 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2594.42 | 0 | 0
July | 182014000000 | 160338.798 | 03-JUL-12:00 | 44737.57 | 41836.601 | 9652.075 | 0 | 61598.866 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2513.682 | 0 | 0
August | 193733000000 | 157317.557 | 15-AUG-11:00 | 44737.57 | 44636.17 | 9371.213 | 0 | 56111.796 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 2460.805 | 0 | 0
September | 264520000000 | 292580.216 | 28-SEP-14:00 | 80527.626 | 73092.045 | 24241.283 | 0 | 112008.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2711.154 | 0 | 0
October | 268084000000 | 232455.371 | 31-OCT-12:00 | 80527.626 | 75091.738 | 14594.416 | 0 | 59682.548 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2559.039 | 0 | 0
November | 251331000000 | 196665.995 | 08-NOV-12:00 | 80527.626 | 79091.122 | 11758.757 | 0 | 22890.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2397.897 | 0 | 0
December | 243478000000 | 185906.7 | 07-DEC-14:00 | 80527.626 | 75091.738 | 11372.032 | 0 | 16569.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2346.113 | 0 | 0
Annual Sum or Average | 2917980000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 182014000000 | 157317.557 |  | 44737.57 | 41836.601 | 9371.213 | 0 | 12269.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2302.908 | 0 | 0
Maximum of Months | 268084000000 | 292580.216 |  | 80527.626 | 79091.122 | 24241.283 | 0 | 112008.107 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 2711.154 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 118948.44 | 8962.03 | 0 | 127910.47
Cost per Total Building Area ($/m2) | 17.31 | 1.3 | 0 | 18.62
Cost per Net Conditioned Building Area ($/m2) | 17.31 | 1.3 | 0 | 18.62

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4774.28 | 694.84 | 694.84
Net Site Energy | 4774.28 | 694.84 | 694.84
Total Source Energy | 13096.2 | 1906.01 | 1906.01
Net Source Energy | 13096.2 | 1906.01 | 1906.01
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1231.96 | 0 | 0 | 0 | 0
Cooling | 403.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.02 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 136.19 | 0 | 0 | 0 | 0 | 0
Pumps | 1.23 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 134.59 | 0 | 0 | 0 | 971.75
Refrigeration | 69.52 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3173.39 | 1600.89 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.385 | 0.304
North Total or Average |  |  | 324.79 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 408883.09 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15478.05 | 10464.45 | 5013.6 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29531.09 | 19965.48 | 9565.62 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 129836.23 | 87780.1 | 42056.13 | 0.68 | 3.49
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 128540.31 | 86903.94 | 41636.36 | 0.68 | 3.49
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 96959.6 | 65552.76 | 31406.84 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 102020.19 | 68974.14 | 33046.05 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7274.62 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6449.89 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7542.24 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7455.56 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7464.42 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7237.44 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7242.45 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7322.6 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5467.8 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5425.38 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5499.66 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14178.57 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5153.89 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11200.03 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5342.41 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18799.42 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18290.81 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18406.06 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16677.01 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16698.44 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11451.69 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14217.04 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 38255.12 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 68477.11 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 139087.27 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 41046.32 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 40636.63 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 30652.73 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 32252.58 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 722.97 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.19 | 1354.75 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.23 | 9808.62 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.18 | 9710.72 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.9 | 7447.68 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.11 | 7836.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2251.48 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 61279.0924 | 101.7356 | 254.871 | 0 | 0.0011 | 15845.6785 | 25425.2015
February | 51974.6777 | 88.3885 | 227.7682 | 0 | 0.0009 | 14161.5524 | 21756.752
March | 53627.6668 | 96.2044 | 262.6464 | 0 | 0.0011 | 16332.1332 | 22906.3221
April | 45588.509 | 86.0283 | 246.7162 | 0 | 0.001 | 15343.0792 | 19860.7108
May | 50234.5926 | 97.4987 | 286.7847 | 0 | 0.0012 | 17835.7894 | 22131.9394
June | 60143.4411 | 118.4222 | 352.694 | 0 | 0.0014 | 21935.3637 | 26652.1782
July | 42709.3525 | 84.1942 | 251.0074 | 0 | 0.001 | 15611.1235 | 18935.4928
August | 45288.2133 | 89.2436 | 265.9737 | 0 | 0.0011 | 16541.922 | 20075.7027
September | 50624.6877 | 99.3913 | 295.2811 | 0 | 0.0012 | 18364.5488 | 22407.6245
October | 49878.2335 | 95.1464 | 275.5806 | 0 | 0.0011 | 17138.4657 | 21823.0876
November | 49316.3428 | 90.3111 | 251.6962 | 0 | 0.001 | 15651.882 | 21233.1301
December | 56187.7248 | 95.7328 | 247.2225 | 0 | 0.001 | 15371.2028 | 23536.7654
Annual Sum or Average | 616852.5341 | 1142.2971 | 3218.2421 | 0 | 0.0131 | 200132.7412 | 266744.9072
Minimum of Months | 42709.3525 | 84.1942 | 227.7682 | 0 | 0.0009 | 14161.5524 | 18935.4928
Maximum of Months | 61279.0924 | 118.4222 | 352.694 | 0 | 0.0014 | 21935.3637 | 26652.1782
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 251255000000 | 183674.895 | 09-JAN-11:50 | 80527.626 | 79091.122 | 7689.224 | 0 | 12926.643 | 0 | 0.097 | 0 | 0 | 0 | 0 | 0 | 3440.183 | 0 | 0
February | 224551000000 | 178902.257 | 15-FEB-12:00 | 80527.626 | 79091.122 | 8225.944 | 0 | 8775.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2281.997 | 0 | 0
March | 258969000000 | 229762.068 | 09-MAR-15:00 | 80527.626 | 73092.045 | 12017.308 | 0 | 61546.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2578.227 | 0 | 0
April | 243286000000 | 229202.512 | 04-APR-14:00 | 80527.626 | 73092.045 | 14042.801 | 0 | 58982.021 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 2558.014 | 0 | 0
May | 282811000000 | 297845.918 | 15-MAY-14:00 | 80527.626 | 73092.045 | 19739.538 | 0 | 121884.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2602.371 | 0 | 0
June | 347816000000 | 347305.439 | 30-JUN-11:00 | 80527.626 | 79091.122 | 27511.461 | 0 | 157462.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2712.886 | 0 | 0
July | 247536000000 | 278051.114 | 25-JUL-11:00 | 44737.57 | 44636.17 | 25678.422 | 0 | 160390.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2608.341 | 0 | 0
August | 262295000000 | 274057.081 | 17-AUG-13:00 | 44737.57 | 41836.601 | 27027.761 | 0 | 157855.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2599.775 | 0 | 0
September | 291196000000 | 314589.171 | 08-SEP-14:00 | 80527.626 | 73092.045 | 26438.746 | 0 | 131825.166 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 2705.576 | 0 | 0
October | 271754000000 | 276654.953 | 03-OCT-11:00 | 80527.626 | 79091.122 | 15006.446 | 0 | 99425.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2604.326 | 0 | 0
November | 248183000000 | 247930.437 | 03-NOV-13:00 | 80527.626 | 75091.738 | 15709.206 | 0 | 74040.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2561.097 | 0 | 0
December | 243732000000 | 171761.585 | 06-DEC-11:20 | 80527.626 | 79091.122 | 8601.641 | 0 | 0 | 0 | 60.167 | 0 | 0 | 0 | 0 | 0 | 3481.028 | 0 | 0
Annual Sum or Average | 3173390000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 224551000000 | 171761.585 |  | 44737.57 | 41836.601 | 7689.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2281.997 | 0 | 0
Maximum of Months | 347816000000 | 347305.439 |  | 80527.626 | 79091.122 | 27511.461 | 0 | 160390.611 | 0 | 60.167 | 0 | 0 | 0 | 0 | 0 | 3481.028 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 68999.64 | 15625.25 | 0 | 84624.89
Cost per Total Building Area ($/m2) | 10.04 | 2.27 | 0 | 12.32
Cost per Net Conditioned Building Area ($/m2) | 10.04 | 2.27 | 0 | 12.32

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4236.68 | 616.6 | 616.6
Net Site Energy | 4236.68 | 616.6 | 616.6
Total Source Energy | 11462.27 | 1668.21 | 1668.21
Net Source Energy | 11462.27 | 1668.21 | 1668.21
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 800.09 | 0 | 0 | 0 | 0
Cooling | 277.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 159.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0.86 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 131.34 | 0 | 0 | 0 | 971.75
Refrigeration | 69.61 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3070.9 | 1165.78 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.385 | 0.304
North Total or Average |  |  | 324.79 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 314514.67 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14103.62 | 9824.61 | 4279 | 0.7 | 3.71
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26833.96 | 18972.98 | 7860.98 | 0.71 | 3.52
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53271.5 | 36752.03 | 16519.47 | 0.69 | 3.21
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 82668.23 | 65456.56 | 17211.67 | 0.79 | 4.14
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 87822.17 | 68468.62 | 19353.55 | 0.78 | 4.02
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 68356.3 | 52148.78 | 16207.52 | 0.76 | 4.08
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 69783.62 | 54278.35 | 15505.28 | 0.78 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5928.25 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5293.65 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6371.24 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6283.44 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6293.86 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6177.19 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6182.2 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6265.78 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4191.11 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4147.72 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4236.77 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11503.19 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3560.95 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9393.04 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4117.79 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14553.56 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14065.3 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14193.7 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13236.83 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13257.19 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9175.62 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10963.33 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 30015.53 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 55023.79 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 110512.48 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 30053.16 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 30849.88 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 22859.58 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 24385.47 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 713.93 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.22 | 1386.56 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.9 | 9348.03 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.03 | 9437.67 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.73 | 7110.47 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.98 | 7585.1 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1731.85 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 76731.3708 | 125.1796 | 300.8835 | 0 | 0.0012 | 312812.7187 | 32003.7393
February | 67500.2633 | 111.4696 | 271.9909 | 0 | 0.0011 | 282784.6432 | 28285.9413
March | 76582.9759 | 127.7567 | 315.5609 | 0 | 0.0012 | 328092.9339 | 32218.3867
April | 68997.2128 | 117.707 | 298.4027 | 0 | 0.0012 | 310271.6697 | 29282.5763
May | 79850.5722 | 138.3379 | 356.792 | 0 | 0.0014 | 370997.4893 | 34096.2732
June | 85917.4961 | 149.3488 | 386.6075 | 0 | 0.0015 | 402003.3497 | 36735.9143
July | 59460.4039 | 103.4036 | 267.7993 | 0 | 0.001 | 278464.1425 | 25427.9917
August | 60011.5026 | 104.2956 | 269.9216 | 0 | 0.0011 | 280670.5242 | 25657.1469
September | 76965.5676 | 133.7167 | 345.9411 | 0 | 0.0013 | 359717.0309 | 32901.3443
October | 73147.9654 | 125.1286 | 318.1973 | 0 | 0.0012 | 330855.8286 | 31077.5684
November | 72082.7665 | 120.5417 | 298.5998 | 0 | 0.0012 | 310460.2683 | 30353.8233
December | 75434.4259 | 122.8454 | 294.6159 | 0 | 0.0012 | 306295.0201 | 31441.3792
Annual Sum or Average | 872682.5229 | 1479.731 | 3725.3123 | 0 | 0.0146 | 3873430 | 369482.0851
Minimum of Months | 59460.4039 | 103.4036 | 267.7993 | 0 | 0.001 | 278464.1425 | 25427.9917
Maximum of Months | 85917.4961 | 149.3488 | 386.6075 | 0 | 0.0015 | 402003.3497 | 36735.9143
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 248002000000 | 184496.948 | 25-JAN-14:00 | 80527.626 | 75091.738 | 14448.491 | 0 | 12118.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2310.622 | 0 | 0
February | 224195000000 | 203387.131 | 14-FEB-15:00 | 80527.626 | 73092.045 | 18960.253 | 0 | 28365.917 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2441.289 | 0 | 0
March | 260116000000 | 208112.843 | 02-MAR-14:00 | 80527.626 | 75091.738 | 18611.749 | 0 | 31397.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2483.801 | 0 | 0
April | 245987000000 | 237357.224 | 21-APR-14:00 | 80527.626 | 73092.045 | 24740.044 | 0 | 56430.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2567.506 | 0 | 0
May | 294131000000 | 262318.335 | 31-MAY-14:00 | 80527.626 | 73092.045 | 26708.536 | 0 | 79323.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2666.77 | 0 | 0
June | 318713000000 | 284782.589 | 29-JUN-13:00 | 80527.626 | 75091.738 | 28937.366 | 0 | 97499.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2726.245 | 0 | 0
July | 220770000000 | 213028.198 | 31-JUL-15:20 | 44737.57 | 40636.785 | 28286.891 | 0 | 96909.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2457.411 | 0 | 0
August | 222519000000 | 208015.479 | 01-AUG-15:20 | 44737.57 | 40636.785 | 25571.015 | 0 | 94555.226 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2514.881 | 0 | 0
September | 285188000000 | 258419.261 | 05-SEP-13:00 | 80527.626 | 75091.738 | 24857.454 | 0 | 75380.465 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2561.977 | 0 | 0
October | 262306000000 | 237697.959 | 13-OCT-14:00 | 80527.626 | 73092.045 | 25677.608 | 0 | 55842.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2557.72 | 0 | 0
November | 246137000000 | 198740.565 | 08-NOV-14:00 | 80527.626 | 75091.738 | 17908.399 | 0 | 22785.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2426.836 | 0 | 0
December | 242834000000 | 180935.365 | 08-DEC-14:00 | 80527.626 | 75091.738 | 13618.218 | 0 | 9409.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2287.948 | 0 | 0
Annual Sum or Average | 3070900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 220770000000 | 180935.365 |  | 44737.57 | 40636.785 | 13618.218 | 0 | 9409.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2287.948 | 0 | 0
Maximum of Months | 318713000000 | 284782.589 |  | 80527.626 | 75091.738 | 28937.366 | 0 | 97499.614 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2726.245 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 31692.98 | 8136.53 | 0 | 39829.51
Cost per Total Building Area ($/m2) | 4.61 | 1.18 | 0 | 5.8
Cost per Net Conditioned Building Area ($/m2) | 4.61 | 1.18 | 0 | 5.8

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4213.62 | 613.25 | 613.25
Net Site Energy | 4213.62 | 613.25 | 613.25
Total Source Energy | 6437.38 | 936.89 | 936.89
Net Source Energy | 6437.38 | 936.89 | 936.89
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1013.03 | 0 | 0 | 0 | 0
Cooling | 91.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 99.86 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 101.71 | 0 | 0 | 0 | 0 | 0
Pumps | 0.8 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 141.49 | 0 | 0 | 0 | 971.75
Refrigeration | 67.28 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2824.77 | 1388.86 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.385 | 0.304
North Total or Average |  |  | 324.79 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 307073.54 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10908.09 | 7697.74 | 3210.36 | 0.71 | 3.74
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23970.87 | 16856.07 | 7114.79 | 0.7 | 3.51
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 51362.23 | 35929.14 | 15433.1 | 0.7 | 3.23
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 74789.95 | 56501.4 | 18288.55 | 0.76 | 3.91
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 85348.79 | 64533.4 | 20815.39 | 0.76 | 3.92
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 65786.84 | 48951.77 | 16835.07 | 0.74 | 3.33
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 68880.69 | 52047.81 | 16832.88 | 0.76 | 4.03
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5746.35 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4708.25 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6849 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6773.07 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6782.44 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5902.22 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5906.27 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5979.54 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3885.26 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3844.23 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3930.76 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10266.59 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5495.66 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6686.46 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3456.15 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20094.58 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19525.03 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19685.4 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11652.69 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11667.86 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8068.88 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11877.64 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 26131.99 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 56903.15 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 120284.05 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 25209.4 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 28825.75 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 21397.61 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 23228.66 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 571.06 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.99 | 7605.57 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.56 | 8696.6 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.38 | 3701.3 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.67 | 7007.99 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1690.88 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 23451.0137 | 29.5405 | 52.796 | 0 | 0.0002 | 697089.6707 | 9000.3961
February | 19034.0824 | 24.7262 | 47.6375 | 0 | 0.0002 | 629123.603 | 7385.4693
March | 21436.1636 | 28.0466 | 54.9267 | 0 | 0.0002 | 725423.8478 | 8338.9362
April | 17307.8617 | 23.6106 | 50.5123 | 0 | 0.0002 | 667286.0043 | 6836.3669
May | 16142.1351 | 23.3259 | 55.4459 | 0 | 0.0002 | 732654.3401 | 6515.746
June | 15189.7212 | 22.5819 | 56.211 | 0 | 0.0002 | 742844.1982 | 6199.0151
July | 10087.2289 | 15.1388 | 38.2391 | 0 | 0.0002 | 505357.3301 | 4131.9284
August | 10637.0032 | 15.952 | 40.2474 | 0 | 0.0002 | 531897.0956 | 4355.8553
September | 14699.6364 | 21.7467 | 53.7171 | 0 | 0.0002 | 709874.5666 | 5987.5977
October | 16673.8801 | 23.5101 | 53.5425 | 0 | 0.0002 | 707429.0193 | 6667.8179
November | 20546.7685 | 26.7556 | 51.8347 | 0 | 0.0002 | 684565.1006 | 7979.3108
December | 22912.287 | 28.8865 | 51.7399 | 0 | 0.0002 | 683149.6201 | 8796.2637
Annual Sum or Average | 208117.7818 | 283.8215 | 606.8501 | 0 | 0.0025 | 8016690 | 82194.7034
Minimum of Months | 10087.2289 | 15.1388 | 38.2391 | 0 | 0.0002 | 505357.3301 | 4131.9284
Maximum of Months | 23451.0137 | 29.5405 | 56.211 | 0 | 0.0002 | 742844.1982 | 9000.3961
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 245627000000 | 169942.154 | 17-JAN-11:20 | 80527.626 | 79091.122 | 6780.616 | 0 | 0 | 0 | 43.907 | 0 | 0 | 0 | 0 | 0 | 3498.883 | 0 | 0
February | 221679000000 | 181609.089 | 21-FEB-12:00 | 80527.626 | 79091.122 | 8493.815 | 0 | 11162.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2334.475 | 0 | 0
March | 255611000000 | 197365.478 | 29-MAR-14:00 | 80527.626 | 73092.045 | 15306.986 | 0 | 26026.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2412.008 | 0 | 0
April | 235125000000 | 188889.284 | 18-APR-13:00 | 80527.626 | 75091.738 | 12795.079 | 0 | 18107.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2367.269 | 0 | 0
May | 258159000000 | 226497.003 | 04-MAY-13:00 | 80527.626 | 75091.738 | 17803.585 | 0 | 50524.849 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2549.197 | 0 | 0
June | 261749000000 | 239177.654 | 28-JUN-13:00 | 80527.626 | 75091.738 | 17327.523 | 0 | 63643.079 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2587.685 | 0 | 0
July | 178068000000 | 164995.801 | 24-JUL-14:00 | 44737.57 | 40636.785 | 10464.492 | 0 | 66655.352 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2501.598 | 0 | 0
August | 187420000000 | 154015.494 | 07-AUG-14:00 | 44737.57 | 40636.785 | 10080.96 | 0 | 56101.844 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2458.33 | 0 | 0
September | 250132000000 | 253571.253 | 13-SEP-14:00 | 80527.626 | 73092.045 | 21530.692 | 0 | 75798.664 | 0 | 0.008 | 0 | 0 | 0 | 0 | 0 | 2622.218 | 0 | 0
October | 249270000000 | 206551.991 | 17-OCT-14:00 | 80527.626 | 73092.045 | 16656.479 | 0 | 33812.263 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2463.576 | 0 | 0
November | 241214000000 | 181357.283 | 03-NOV-11:00 | 80527.626 | 79091.122 | 7752.564 | 0 | 11636.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2349.478 | 0 | 0
December | 240715000000 | 169941.581 | 01-DEC-11:09 | 80527.626 | 79091.122 | 6700.9 | 0 | 0 | 0 | 147.732 | 0 | 0 | 0 | 0 | 0 | 3474.2 | 0 | 0
Annual Sum or Average | 2824770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 178068000000 | 154015.494 |  | 44737.57 | 40636.785 | 6700.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2334.475 | 0 | 0
Maximum of Months | 261749000000 | 253571.253 |  | 80527.626 | 79091.122 | 21530.692 | 0 | 75798.664 | 0 | 147.732 | 0 | 0 | 0 | 0 | 0 | 3498.883 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 58788.29 | 11647.86 | 0 | 70436.15
Cost per Total Building Area ($/m2) | 8.56 | 1.7 | 0 | 10.25
Cost per Net Conditioned Building Area ($/m2) | 8.56 | 1.7 | 0 | 10.25

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5109.49 | 743.63 | 743.63
Net Site Energy | 5109.49 | 743.63 | 743.63
Total Source Energy | 13076.37 | 1903.12 | 1903.12
Net Source Energy | 13076.37 | 1903.12 | 1903.12
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1671.08 | 0 | 0 | 0 | 0
Cooling | 291.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 100.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 130.78 | 0 | 0 | 0 | 0 | 0
Pumps | 1.52 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 149.14 | 0 | 0 | 0 | 971.75
Refrigeration | 68 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3054.93 | 2054.56 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.385 | 0.304
North Total or Average |  |  | 324.79 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 438428.51 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15069.27 | 10188.08 | 4881.19 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28394.7 | 19197.18 | 9197.52 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 121186.82 | 81932.38 | 39254.45 | 0.68 | 3.51
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 121106.2 | 81877.87 | 39228.33 | 0.68 | 3.51
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 91154 | 61627.69 | 29526.31 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 96008.89 | 64910 | 31098.89 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6592.55 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6027.83 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7013.63 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6930.98 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6939.67 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6685.87 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6690.45 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6767.71 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4981.26 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4938.66 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5014.76 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13207.23 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4655.95 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12049.53 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4921.58 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17433.93 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16922.54 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17035.49 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15479.67 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15499.1 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10639.28 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13141.84 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 43509.59 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 78470.91 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 162482.64 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 46820.57 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 46789.42 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 35217.38 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 37093.07 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 703.88 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.14 | 1302.62 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.88 | 9308.63 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.88 | 9302.44 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.67 | 7001.74 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.87 | 7374.66 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2414.17 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 108902.8616 | 176.633 | 466.7311 | 0 | 0.0015 | 107418.6811 | 45128.1858
February | 93974.7767 | 154.9354 | 417.8279 | 0 | 0.0013 | 96167.7367 | 39182.579
March | 102268.5168 | 172.6971 | 479.2094 | 0 | 0.0015 | 110301.8944 | 43031.4861
April | 87448.4816 | 153.8292 | 446.6821 | 0 | 0.0014 | 102824.2639 | 37384.4482
May | 97529.7963 | 174.8393 | 517.8166 | 0 | 0.0016 | 119203.6768 | 42007.4718
June | 114633.7639 | 207.0897 | 618.1504 | 0 | 0.0019 | 142303.095 | 49526.2846
July | 79336.2826 | 143.4294 | 428.4461 | 0 | 0.0013 | 98631.8063 | 34286.493
August | 79201.7244 | 143.0903 | 427.1455 | 0 | 0.0013 | 98332.2586 | 34219.1868
September | 96787.9396 | 174.4777 | 519.6827 | 0 | 0.0016 | 119634.5578 | 41780.5258
October | 93343.3934 | 165.6514 | 485.5004 | 0 | 0.0015 | 111762.0872 | 40043.4134
November | 95078.4827 | 162.3634 | 456.3557 | 0 | 0.0014 | 105044.2838 | 40178.9834
December | 102407.0571 | 168.924 | 455.837 | 0 | 0.0014 | 104916.0835 | 42706.657
Annual Sum or Average | 1150910 | 1997.9599 | 5719.3849 | 0 | 0.0175 | 1316540 | 489475.7149
Minimum of Months | 79201.7244 | 143.0903 | 417.8279 | 0 | 0.0013 | 96167.7367 | 34219.1868
Maximum of Months | 114633.7639 | 207.0897 | 618.1504 | 0 | 0.0019 | 142303.095 | 49526.2846
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 249257000000 | 171355.264 | 27-JAN-11:09 | 80527.626 | 79091.122 | 7459.292 | 0 | 0 | 0 | 865.768 | 0 | 0 | 0 | 0 | 0 | 3411.456 | 0 | 0
February | 223150000000 | 171282.29 | 28-FEB-11:20 | 80527.626 | 79091.122 | 8136.307 | 0 | 0 | 0 | 6.724 | 0 | 0 | 0 | 0 | 0 | 3520.51 | 0 | 0
March | 255947000000 | 200684.805 | 31-MAR-14:00 | 80527.626 | 73092.045 | 11684.064 | 0 | 32904.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2476.649 | 0 | 0
April | 238596000000 | 208000.576 | 07-APR-13:00 | 80527.626 | 75091.738 | 13715.961 | 0 | 36147.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2517.264 | 0 | 0
May | 276603000000 | 274016.505 | 30-MAY-14:00 | 80527.626 | 73092.045 | 16767.239 | 0 | 101011.118 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2618.476 | 0 | 0
June | 330204000000 | 334903.429 | 08-JUN-11:00 | 80527.626 | 79091.122 | 28157.229 | 0 | 144448.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2678.842 | 0 | 0
July | 228868000000 | 250503.093 | 13-JUL-14:00 | 44737.57 | 40636.785 | 19255.165 | 0 | 143278.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2595.516 | 0 | 0
August | 228173000000 | 255384.23 | 04-AUG-15:00 | 44737.57 | 40636.785 | 26488.127 | 0 | 140973.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2548.036 | 0 | 0
September | 277603000000 | 302275.257 | 06-SEP-11:00 | 80527.626 | 79091.122 | 20794.406 | 0 | 119214.342 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2647.758 | 0 | 0
October | 259336000000 | 245005.782 | 31-OCT-11:00 | 80527.626 | 79091.122 | 12602.437 | 0 | 70228.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2555.816 | 0 | 0
November | 243747000000 | 237995.972 | 02-NOV-11:00 | 80527.626 | 79091.122 | 10811.585 | 0 | 65001.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2563.873 | 0 | 0
December | 243450000000 | 170790.902 | 05-DEC-11:20 | 80527.626 | 79091.122 | 7596.74 | 0 | 0 | 0 | 123.161 | 0 | 0 | 0 | 0 | 0 | 3452.252 | 0 | 0
Annual Sum or Average | 3054930000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 223150000000 | 170790.902 |  | 44737.57 | 40636.785 | 7459.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2476.649 | 0 | 0
Maximum of Months | 330204000000 | 334903.429 |  | 80527.626 | 79091.122 | 28157.229 | 0 | 144448.61 | 0 | 865.768 | 0 | 0 | 0 | 0 | 0 | 3520.51 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 75319.06 | 17298.37 | 0 | 92617.43
Cost per Total Building Area ($/m2) | 10.96 | 2.52 | 0 | 13.48
Cost per Net Conditioned Building Area ($/m2) | 10.96 | 2.52 | 0 | 13.48

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4524.29 | 658.46 | 658.46
Net Site Energy | 4524.29 | 658.46 | 658.46
Total Source Energy | 11487.26 | 1671.85 | 1671.85
Net Source Energy | 11487.26 | 1671.85 | 1671.85
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1200.94 | 0 | 0 | 0 | 0
Cooling | 179.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 99.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 129.56 | 0 | 0 | 0 | 0 | 0
Pumps | 1.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 147.98 | 0 | 0 | 0 | 971.75
Refrigeration | 67.65 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2941.03 | 1583.27 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.385 | 0.304
North Total or Average |  |  | 324.79 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 332249.59 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13353.52 | 9264.06 | 4089.46 | 0.69 | 3.7
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25860.32 | 18035.33 | 7824.99 | 0.7 | 3.49
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53923.29 | 37032.95 | 16890.34 | 0.69 | 3.21
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 76693.58 | 59565.16 | 17128.42 | 0.78 | 4.04
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 82002.31 | 62861.88 | 19140.44 | 0.77 | 3.98
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 63794.34 | 47811.3 | 15983.04 | 0.75 | 3.34
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 65181.34 | 49848.03 | 15333.32 | 0.76 | 4.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5181.87 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4767.51 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5751.38 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5665.43 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5676.17 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5462.44 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5466.9 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5548.52 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4091.19 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4090.58 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4041.83 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10386.55 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3326.39 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11767.76 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4413.98 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13341.12 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12847.24 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12972.74 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11728.53 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11746.55 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8155.96 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9892.78 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 33560.55 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 63539.58 | 0.8
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 131920.13 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 33745.76 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 35029.7 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 25860.84 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 27692.5 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 668.71 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.13 | 1289.6 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.36 | 8308.65 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.52 | 8624.77 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.34 | 3650.68 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.57 | 6818.26 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 1829.51 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 80344.6175 | 128.6127 | 301.7288 | 0 | 0.0012 | 313673.4222 | 33269.3306
February | 70811.2071 | 114.0775 | 269.854 | 0 | 0.0011 | 280542.3386 | 29392.8808
March | 78558.6421 | 129.1456 | 313.3802 | 0 | 0.0012 | 325812.2114 | 32862.4946
April | 69558.8825 | 117.425 | 294.1194 | 0 | 0.0012 | 305809.6764 | 29399.3023
May | 74522.0514 | 127.2523 | 322.947 | 0 | 0.0013 | 335793.0037 | 31639.1135
June | 77775.8468 | 134.5118 | 346.2674 | 0 | 0.0014 | 360052.4183 | 33187.6347
July | 54795.5802 | 95.1747 | 246.1586 | 0 | 0.001 | 255960.8407 | 23421.6608
August | 56656.1708 | 98.3496 | 254.2095 | 0 | 0.001 | 264332.0181 | 24211.3753
September | 71605.8781 | 123.4158 | 316.4965 | 0 | 0.0012 | 329093.5067 | 30513.1454
October | 72813.9755 | 124.0043 | 313.7517 | 0 | 0.0012 | 326229.664 | 30881.433
November | 73690.1741 | 121.2344 | 294.4588 | 0 | 0.0012 | 306140.8281 | 30834.979
December | 78963.3603 | 126.0284 | 294.5216 | 0 | 0.0012 | 306177.9571 | 32660.7668
Annual Sum or Average | 860096.3865 | 1439.2321 | 3567.8934 | 0 | 0.0141 | 3709620 | 362274.1167
Minimum of Months | 54795.5802 | 95.1747 | 246.1586 | 0 | 0.001 | 255960.8407 | 23421.6608
Maximum of Months | 80344.6175 | 134.5118 | 346.2674 | 0 | 0.0014 | 360052.4183 | 33269.3306
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 248684000000 | 186666.641 | 24-JAN-12:00 | 80527.626 | 79091.122 | 10348.425 | 0 | 14322.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2376.575 | 0 | 0
February | 222417000000 | 180111.585 | 07-FEB-14:00 | 80527.626 | 75091.738 | 12490.892 | 0 | 9710.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2290.789 | 0 | 0
March | 258308000000 | 210501.194 | 30-MAR-14:00 | 80527.626 | 73092.045 | 18776.342 | 0 | 35628.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2476.933 | 0 | 0
April | 242450000000 | 226018.736 | 25-APR-14:00 | 80527.626 | 73092.045 | 20618.782 | 0 | 49231.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2548.801 | 0 | 0
May | 266221000000 | 245430.179 | 23-MAY-15:00 | 80527.626 | 73092.045 | 22064.835 | 0 | 67239.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2505.793 | 0 | 0
June | 285454000000 | 277665.558 | 28-JUN-11:00 | 80527.626 | 79091.122 | 20661.088 | 0 | 94699.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2686.094 | 0 | 0
July | 202929000000 | 202042.878 | 17-JUL-15:30 | 44737.57 | 40636.785 | 21440.952 | 0 | 92773.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2454.134 | 0 | 0
August | 209566000000 | 203083.902 | 30-AUG-13:00 | 44737.57 | 41836.601 | 17970.862 | 0 | 95949.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2589.161 | 0 | 0
September | 260909000000 | 260952.636 | 05-SEP-13:00 | 80527.626 | 75091.738 | 22251.824 | 0 | 80390.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.648 | 0 | 0
October | 258639000000 | 243399.65 | 05-OCT-14:00 | 80527.626 | 73092.045 | 23275.003 | 0 | 63909.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2595.731 | 0 | 0
November | 242712000000 | 198635.304 | 10-NOV-13:00 | 80527.626 | 75091.738 | 13974.213 | 0 | 26577.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2464.343 | 0 | 0
December | 242742000000 | 176644.323 | 21-DEC-14:00 | 80527.626 | 75091.738 | 11179.358 | 0 | 7566.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2278.866 | 0 | 0
Annual Sum or Average | 2941030000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 202929000000 | 176644.323 |  | 44737.57 | 40636.785 | 10348.425 | 0 | 7566.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2278.866 | 0 | 0
Maximum of Months | 285454000000 | 277665.558 |  | 80527.626 | 79091.122 | 23275.003 | 0 | 95949.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2690.648 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 30360.83 | 11047.08 | 0 | 41407.91
Cost per Total Building Area ($/m2) | 4.42 | 1.61 | 0 | 6.03
Cost per Net Conditioned Building Area ($/m2) | 4.42 | 1.61 | 0 | 6.03

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5823.93 | 847.61 | 847.61
Net Site Energy | 5823.93 | 847.61 | 847.61
Total Source Energy | 13396.37 | 1949.7 | 1949.7
Net Source Energy | 13396.37 | 1949.7 | 1949.7
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2426.93 | 0 | 0 | 0 | 0
Cooling | 234.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 99.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 133.22 | 0 | 0 | 0 | 0 | 0
Pumps | 2.77 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 161.96 | 0 | 0 | 0 | 971.75
Refrigeration | 67.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3000.7 | 2823.23 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.385 | 0.304
North Total or Average |  |  | 324.79 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 456156.13 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14722.43 | 9953.59 | 4768.84 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27688.35 | 18719.63 | 8968.72 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 116571.15 | 78811.8 | 37759.35 | 0.68 | 3.51
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 117720.61 | 79588.93 | 38131.68 | 0.68 | 3.51
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 88442.3 | 59794.35 | 28647.94 | 0.68 | 3.51
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 93446.42 | 63177.55 | 30268.86 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6266.74 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5765.23 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6789.51 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6704.87 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6713.83 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6357.86 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6362.53 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6441.72 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4844.36 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4844.66 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4792.81 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12679.87 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4571.09 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12979.04 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5112.4 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17210.4 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16683.91 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16798.69 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14691.08 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14710.93 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10124.39 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12768.2 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 45938.84 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 84027.56 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 175595.96 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 49460.88 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 49948.6 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 37525.87 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 39649.11 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 687.68 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.12 | 1270.21 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.69 | 8954.09 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.74 | 9042.38 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.56 | 6793.45 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.76 | 7177.83 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2511.79 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 90881.5941 | 133.0752 | 165.1206 | 0 | 0.0013 | 108420.4026 | 36289.1939
February | 75386.8134 | 113.6247 | 147.5119 | 0 | 0.0011 | 96877.9578 | 30411.6068
March | 73532.9014 | 118.2295 | 167.9768 | 0 | 0.0013 | 110359.9331 | 30370.9761
April | 58918.4141 | 101.2648 | 155.8648 | 0 | 0.0012 | 102433.9255 | 24959.2983
May | 63926.6747 | 113.5258 | 181.0092 | 0 | 0.0013 | 118974.0145 | 27430.1188
June | 71329.9118 | 128.398 | 207.5883 | 0 | 0.0015 | 136450.7052 | 30771.6369
July | 48453.4983 | 87.3473 | 141.4295 | 0 | 0.001 | 92964.0722 | 20915.0331
August | 51090.9974 | 92.0917 | 149.0948 | 0 | 0.0011 | 98002.5456 | 22052.5378
September | 58893.7836 | 105.2094 | 168.7819 | 0 | 0.0012 | 110939.6589 | 25329.9677
October | 61801.2893 | 106.1788 | 163.358 | 0 | 0.0012 | 107358.3118 | 26176.6458
November | 68893.9732 | 111.358 | 159.2917 | 0 | 0.0012 | 104656.7004 | 28511.1064
December | 81733.6886 | 123.5151 | 160.987 | 0 | 0.0012 | 105729.5449 | 33002.9836
Annual Sum or Average | 804843.54 | 1333.8183 | 1968.0145 | 0 | 0.0147 | 1293170 | 336221.1052
Minimum of Months | 48453.4983 | 87.3473 | 141.4295 | 0 | 0.001 | 92964.0722 | 20915.0331
Maximum of Months | 90881.5941 | 133.0752 | 207.5883 | 0 | 0.0015 | 136450.7052 | 36289.1939
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 251581000000 | 172030.586 | 05-JAN-11:09 | 80527.626 | 79091.122 | 7363.514 | 0 | 0 | 0 | 1641.543 | 0 | 0 | 0 | 0 | 0 | 3406.78 | 0 | 0
February | 224798000000 | 171304.621 | 03-FEB-11:09 | 80527.626 | 79091.122 | 7363.514 | 0 | 0 | 0 | 907.939 | 0 | 0 | 0 | 0 | 0 | 3414.419 | 0 | 0
March | 256082000000 | 183085.034 | 23-MAR-14:00 | 80527.626 | 73092.045 | 11041.007 | 0 | 16104.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2319.48 | 0 | 0
April | 237690000000 | 201210.603 | 14-APR-14:00 | 80527.626 | 73092.045 | 13622.114 | 0 | 31518.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2450.628 | 0 | 0
May | 276070000000 | 288700.416 | 31-MAY-11:00 | 80527.626 | 79091.122 | 17904.817 | 0 | 108529.423 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 2647.424 | 0 | 0
June | 316624000000 | 327708.921 | 29-JUN-11:00 | 80527.626 | 79091.122 | 25392.855 | 0 | 140019.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2677.67 | 0 | 0
July | 215716000000 | 240496.966 | 13-JUL-15:00 | 44737.57 | 40636.785 | 17364.635 | 0 | 135201.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2556.414 | 0 | 0
August | 227408000000 | 240641.516 | 25-AUG-15:00 | 44737.57 | 40636.785 | 19618.98 | 0 | 133103.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2545.152 | 0 | 0
September | 257427000000 | 288896.703 | 14-SEP-14:00 | 80527.626 | 73092.045 | 23686.995 | 0 | 108954.404 | 0 | 0.014 | 0 | 0 | 0 | 0 | 0 | 2635.62 | 0 | 0
October | 249117000000 | 213920.32 | 06-OCT-14:00 | 80527.626 | 73092.045 | 15805.545 | 0 | 41993.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2501.495 | 0 | 0
November | 242848000000 | 195062.291 | 02-NOV-14:00 | 80527.626 | 73092.045 | 14105.779 | 0 | 24961.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2375.537 | 0 | 0
December | 245337000000 | 170906.042 | 20-DEC-11:09 | 80527.626 | 79091.122 | 7363.514 | 0 | 0 | 0 | 512.016 | 0 | 0 | 0 | 0 | 0 | 3411.764 | 0 | 0
Annual Sum or Average | 3000700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 215716000000 | 170906.042 |  | 44737.57 | 40636.785 | 7363.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2319.48 | 0 | 0
Maximum of Months | 316624000000 | 327708.921 |  | 80527.626 | 79091.122 | 25392.855 | 0 | 140019.647 | 0 | 1641.543 | 0 | 0 | 0 | 0 | 0 | 3414.419 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51376.15 | 22303.86 | 0 | 73680.02
Cost per Total Building Area ($/m2) | 7.48 | 3.25 | 0 | 10.72
Cost per Net Conditioned Building Area ($/m2) | 7.48 | 3.25 | 0 | 10.72

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5143.24 | 748.54 | 748.54
Net Site Energy | 5143.24 | 748.54 | 748.54
Total Source Energy | 12426.98 | 1808.61 | 1808.61
Net Source Energy | 12426.98 | 1808.61 | 1808.61
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1888.6 | 0 | 0 | 0 | 0
Cooling | 111.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 99.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 113.95 | 0 | 0 | 0 | 0 | 0
Pumps | 2.18 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 163.52 | 0 | 0 | 0 | 971.75
Refrigeration | 65.98 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2856.78 | 2286.46 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.385 | 0.305 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.385 | 0.305 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.385 | 0.305 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 456 | 1.78 | 1.78 | 2.674 | 0.414 | 0.26 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.385 | 0.304
North Total or Average |  |  | 324.79 | 3.24 | 0.385 | 0.305
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.386 | 0.303
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 392502.43 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10528.3 | 7800.91 | 2727.39 | 0.74 | 3.84
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21050.83 | 15597.54 | 5453.29 | 0.74 | 3.61
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46116.8 | 33668.35 | 12448.44 | 0.73 | 3.3
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 77377.49 | 61797.94 | 15579.55 | 0.8 | 4.18
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 71994.21 | 57498.55 | 14495.66 | 0.8 | 4.18
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 53167.44 | 42462.46 | 10704.99 | 0.8 | 3.45
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 57097.53 | 45601.24 | 11496.29 | 0.8 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5712.88 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4703.89 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5829.31 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5743.43 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5754.2 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5327.22 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5331.73 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5413.6 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5038.89 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5039.07 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4985.81 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10329.23 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4132.52 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13254.44 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5473.78 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14301.41 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13786.11 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13915.29 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11532.13 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11550.26 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8027.91 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10267.47 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 37858.7 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 75696.65 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 160010.48 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 44999.29 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 41868.62 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 30919.81 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 33205.37 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 621.92 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.67 | 8916.05 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.35 | 8295.74 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.21 | 3512.56 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.57 | 622 | 3.45 | 3772.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2161.29 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 83869.3937 | 127.1201 | 184.7919 | 0 | 0.0013 | 4380820 | 33956.341
February | 70958.4666 | 110.2146 | 165.9773 | 0 | 0.0012 | 3935320 | 28986.5325
March | 73260.9039 | 119.0854 | 190.511 | 0 | 0.0013 | 4518010 | 30438.8783
April | 63566.5114 | 105.6043 | 173.5365 | 0 | 0.0012 | 4115850 | 26631.1107
May | 65495.0445 | 112.1466 | 190.8746 | 0 | 0.0013 | 4527600 | 27761.7681
June | 67757.8902 | 117.7954 | 203.8855 | 0 | 0.0014 | 4836490 | 28892.4273
July | 46041.9832 | 80.6618 | 140.7802 | 0 | 0.001 | 3339630 | 19692.4484
August | 46691.2293 | 81.3942 | 141.3006 | 0 | 0.001 | 3351910 | 19930.9857
September | 61817.2033 | 106.8593 | 183.8097 | 0 | 0.0013 | 4360180 | 26300.4745
October | 65105.6228 | 110.0628 | 184.6151 | 0 | 0.0013 | 4378910 | 27459.7269
November | 69532.0829 | 112.5232 | 179.0025 | 0 | 0.0013 | 4245000 | 28841.1767
December | 79514.0824 | 121.9582 | 180.4014 | 0 | 0.0013 | 4277020 | 32332.1381
Annual Sum or Average | 793610.4141 | 1305.4261 | 2119.4862 | 0 | 0.0149 | 50266800 | 331224.0081
Minimum of Months | 46041.9832 | 80.6618 | 140.7802 | 0 | 0.001 | 3339630 | 19692.4484
Maximum of Months | 83869.3937 | 127.1201 | 203.8855 | 0 | 0.0014 | 4836490 | 33956.341
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 248972000000 | 172490.412 | 05-JAN-08:09 | 80527.626 | 75091.738 | 6657.526 | 0 | 0 | 6368 | 1949.722 | 0 | 0 | 0 | 0 | 0 | 1895.8 | 0 | 0
February | 223654000000 | 182849.314 | 02-FEB-14:00 | 80527.626 | 75091.738 | 9267.111 | 0 | 15592.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2369.85 | 0 | 0
March | 256770000000 | 196229.798 | 30-MAR-14:00 | 80527.626 | 73092.045 | 13995.833 | 0 | 26188.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2426.032 | 0 | 0
April | 233913000000 | 187747.318 | 06-APR-14:00 | 80527.626 | 73092.045 | 11597.424 | 0 | 20143.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2387.164 | 0 | 0
May | 257315000000 | 219606.005 | 16-MAY-14:00 | 80527.626 | 73092.045 | 17333.018 | 0 | 46126.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2526.909 | 0 | 0
June | 274870000000 | 265574.532 | 30-JUN-12:00 | 80527.626 | 75091.738 | 21606.642 | 0 | 85617.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2731.059 | 0 | 0
July | 189799000000 | 188657.33 | 21-JUL-15:00 | 44737.57 | 40636.785 | 20687.081 | 0 | 80150.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2445.73 | 0 | 0
August | 190497000000 | 167429.294 | 09-AUG-15:00 | 44737.57 | 40636.785 | 11023.665 | 0 | 68615.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2416.119 | 0 | 0
September | 247799000000 | 240269.161 | 12-SEP-13:00 | 80527.626 | 75091.738 | 18072.855 | 0 | 63979.286 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2597.65 | 0 | 0
October | 248864000000 | 209082.883 | 06-OCT-14:00 | 80527.626 | 73092.045 | 16482.281 | 0 | 36491.049 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2489.88 | 0 | 0
November | 241254000000 | 175023.603 | 21-NOV-11:50 | 80527.626 | 79091.122 | 7275.049 | 0 | 4797.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3332.594 | 0 | 0
December | 243073000000 | 172312.731 | 18-DEC-08:09 | 80527.626 | 75091.738 | 6657.526 | 0 | 0 | 6368 | 1770.225 | 0 | 0 | 0 | 0 | 0 | 1897.616 | 0 | 0
Annual Sum or Average | 2856780000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 189799000000 | 167429.294 |  | 44737.57 | 40636.785 | 6657.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1895.8 | 0 | 0
Maximum of Months | 274870000000 | 265574.532 |  | 80527.626 | 79091.122 | 21606.642 | 0 | 85617.468 | 6368 | 1949.722 | 0 | 0 | 0 | 0 | 0 | 3332.594 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 60083.26 | 18728.1 | 0 | 78811.36
Cost per Total Building Area ($/m2) | 8.74 | 2.73 | 0 | 11.47
Cost per Net Conditioned Building Area ($/m2) | 8.74 | 2.73 | 0 | 11.47

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6168 | 897.69 | 897.69
Net Site Energy | 6168 | 897.69 | 897.69
Total Source Energy | 13423.17 | 1953.6 | 1953.6
Net Source Energy | 13423.17 | 1953.6 | 1953.6
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2899.97 | 0 | 0 | 0 | 0
Cooling | 103.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 99.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 117.15 | 0 | 0 | 0 | 0 | 0
Pumps | 3.46 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 181.79 | 0 | 0 | 0 | 971.75
Refrigeration | 64.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2851.9 | 3316.1 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 3.241 | 0.487 | 0.409 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 3.241 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 3.241 | 0.487 | 0.409 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 3.241 | 0.487 | 0.409 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 3.241 | 0.487 | 0.409 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 7 | 1.78 | 1.78 | 2.674 | 0.777 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 3.241 | 0.487 | 0.409 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 3.241 | 0.487 | 0.409 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 3.241 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 3.241 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 3.241 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 3.23 | 0.493 | 0.417
North Total or Average |  |  | 324.79 | 3.24 | 0.487 | 0.409
Non-North Total or Average |  |  | 570.4 | 3.22 | 0.496 | 0.421
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 433255.69 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13102.37 | 8858.29 | 4244.08 | 0.68 | 3.65
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29311.84 | 19817.24 | 9494.6 | 0.68 | 3.44
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56274.82 | 38046.46 | 18228.36 | 0.68 | 3.19
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 108523.71 | 73536.31 | 34987.4 | 0.68 | 3.51
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 109245.96 | 73859.36 | 35386.6 | 0.68 | 3.51
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 79681.35 | 53871.22 | 25810.13 | 0.68 | 3.11
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 86948.61 | 58784.49 | 28164.11 | 0.68 | 3.11
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5844.62 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4878.28 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6645.08 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6527.89 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6541.4 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6063.51 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6069.52 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6181.72 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5126.51 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5127.32 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5072.23 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10824.92 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4236.62 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13429.08 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5522.36 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16220.47 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15543.27 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15726.72 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11913.08 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11936.84 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8397.76 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11167.1 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 41847.58 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 87393.89 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 179735.84 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 47682.56 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 47703.51 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 34793.78 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 37967.11 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 612 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.18 | 1344.69 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.4 | 8387.74 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.4 | 8391.43 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.57 | 622 | 3.21 | 3509.19 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.57 | 622 | 3.5 | 3829.25 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 2385.69 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 90446.2272 | 132.4672 | 164.4256 | 0 | 0.0013 | 107964.2267 | 36118.169
February | 77604.1826 | 115.6557 | 147.5819 | 0 | 0.0011 | 96916.5267 | 31180.7962
March | 78494.6228 | 122.6029 | 167.5753 | 0 | 0.0013 | 110078.7249 | 32075.7776
April | 61856.4932 | 103.0637 | 153.0521 | 0 | 0.0011 | 100571.8727 | 25893.2063
May | 61973.62 | 107.0608 | 165.7217 | 0 | 0.0012 | 108914.1302 | 26305.6525
June | 62368.5423 | 111.3694 | 178.5857 | 0 | 0.0013 | 117383.496 | 26819.9151
July | 44549.7496 | 79.9909 | 128.9959 | 0 | 0.0009 | 84790.0144 | 19199.4698
August | 44115.1412 | 78.3777 | 125.0256 | 0 | 0.0009 | 82177.1411 | 18932.5597
September | 57460.8357 | 100.6827 | 158.2707 | 0 | 0.0012 | 104023.1195 | 24525.653
October | 63169.135 | 106.7771 | 161.2699 | 0 | 0.0012 | 105978.6614 | 26588.5747
November | 71392.0729 | 113.5905 | 159.1892 | 0 | 0.0012 | 104580.716 | 29372.3546
December | 84475.437 | 125.9744 | 160.9038 | 0 | 0.0012 | 105665.4791 | 33949.0942
Annual Sum or Average | 797906.0593 | 1297.6131 | 1870.5971 | 0 | 0.014 | 1229040 | 330961.2228
Minimum of Months | 44115.1412 | 78.3777 | 125.0256 | 0 | 0.0009 | 82177.1411 | 18932.5597
Maximum of Months | 90446.2272 | 132.4672 | 178.5857 | 0 | 0.0013 | 117383.496 | 36118.169
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 250523000000 | 171567.576 | 09-JAN-11:09 | 80527.626 | 79091.122 | 6727.29 | 0 | 0 | 0 | 1812.411 | 0 | 0 | 0 | 0 | 0 | 3409.127 | 0 | 0
February | 224887000000 | 171511.408 | 01-FEB-11:09 | 80527.626 | 79091.122 | 6727.29 | 0 | 0 | 0 | 1750.402 | 0 | 0 | 0 | 0 | 0 | 3414.968 | 0 | 0
March | 255429000000 | 170253.202 | 01-MAR-11:20 | 80527.626 | 79091.122 | 6979.915 | 0 | 0 | 0 | 210.806 | 0 | 0 | 0 | 0 | 0 | 3443.733 | 0 | 0
April | 233369000000 | 187450.164 | 04-APR-14:00 | 80527.626 | 73092.045 | 12021.117 | 0 | 19478.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2331.161 | 0 | 0
May | 252727000000 | 220291.677 | 31-MAY-13:00 | 80527.626 | 75091.738 | 16295.09 | 0 | 45856.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2521.046 | 0 | 0
June | 272380000000 | 293490.173 | 14-JUN-14:00 | 80527.626 | 73092.045 | 19030.166 | 0 | 118220.607 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 2619.727 | 0 | 0
July | 196749000000 | 213406.63 | 06-JUL-15:00 | 44737.57 | 40636.785 | 12919.927 | 0 | 112672.102 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 2440.24 | 0 | 0
August | 190686000000 | 194149.354 | 11-AUG-15:39 | 44737.57 | 40636.785 | 10097.785 | 0 | 96267.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2409.792 | 0 | 0
September | 241378000000 | 268564.247 | 07-SEP-14:00 | 80527.626 | 73092.045 | 18583.081 | 0 | 93790.079 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 2571.416 | 0 | 0
October | 245915000000 | 192725.214 | 06-OCT-14:00 | 80527.626 | 73092.045 | 13688.759 | 0 | 23064.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2352.228 | 0 | 0
November | 242672000000 | 171097.043 | 09-NOV-11:50 | 80527.626 | 79091.122 | 7047.597 | 0 | 1152.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3278.235 | 0 | 0
December | 245189000000 | 170482.478 | 20-DEC-11:09 | 80527.626 | 79091.122 | 6727.29 | 0 | 0 | 0 | 718.342 | 0 | 0 | 0 | 0 | 0 | 3418.097 | 0 | 0
Annual Sum or Average | 2851900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 190686000000 | 170253.202 |  | 44737.57 | 40636.785 | 6727.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2331.161 | 0 | 0
Maximum of Months | 272380000000 | 293490.173 |  | 80527.626 | 79091.122 | 19030.166 | 0 | 118220.607 | 0 | 1812.411 | 0 | 0 | 0 | 0 | 0 | 3443.733 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 47691.95 | 26154 | 0 | 73845.95
Cost per Total Building Area ($/m2) | 6.94 | 3.81 | 0 | 10.75
Cost per Net Conditioned Building Area ($/m2) | 6.94 | 3.81 | 0 | 10.75

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8783.14 | 1278.29 | 1278.29
Net Site Energy | 8783.14 | 1278.29 | 1278.29
Total Source Energy | 16623.72 | 2419.4 | 2419.4
Net Source Energy | 16623.72 | 2419.4 | 2419.4
Area [m2]
Total Building Area | 6871
Net Conditioned Building Area | 6871
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5507.66 | 0 | 0 | 0 | 0
Cooling | 52.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1233.05 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 99.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1230.23 | 234.34 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 149.23 | 0 | 0 | 0 | 0 | 0
Pumps | 8.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 205.44 | 0 | 0 | 0 | 971.75
Refrigeration | 63.18 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2835.7 | 5947.44 | 0 | 0 | 0 | 971.75
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BATH_ZN_1_FLR_1 | 190 | Yes | 760 | 1 | 40 | 14 | 9.68 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 144 | 50.4 | 15.06 | 1.39 | 25.39
COMPUTER_CLASS_ZN_1_FLR_1 | 162 | Yes | 648 | 1 | 72 | 25.2 | 15.06 | 3.33 | 20
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 15
CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | Yes | 768 | 1 | 12 | 4.2 | 5.38 | 10 | 4
GYM_ZN_1_FLR_1 | 357 | Yes | 1428 | 1 | 68 | 37.18 | 15.06 | 3.33 | 5
KITCHEN_ZN_1_FLR_1 | 168 | Yes | 672 | 1 | 32 | 11.2 | 12.91 | 6.67 | 1147.9524
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | Yes | 1596 | 1 | 160 | 56 | 13.99 | 4.35 | 15
LOBBY_ZN_1_FLR_1 | 171 | Yes | 684 | 1 | 76 | 26.6 | 13.99 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | Yes | 2184 | 1 | 36 | 12.6 | 5.38 | 10 | 4
MECH_ZN_1_FLR_1 | 252 | Yes | 1008 | 1 | 0 | 0 | 16.14 |  | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 15
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | Yes | 1260 | 1 | 140 | 49 | 15.06 | 4 | 15
OFFICES_ZN_1_FLR_1 | 441 | Yes | 1764 | 1 | 168 | 58.8 | 11.84 | 20 | 10.8
Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Conditioned Total | 6871 |  | 27484 |  | 2512 | 892.56 | 13.0221 | 4.65 | 39.7288
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 40 | 270 | 90 | W
BATH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 190 | 270 | 180
BATH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 190 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 60 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
CAFETERIA_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 315 | 90 | 0
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 72 | 0 | 90 | N
COMPUTER_CLASS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 162 | 270 | 180
COMPUTER_CLASS_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 162 | 90 | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 192 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 192 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 12 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 192 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 192 | 90 | 0
GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 68 | 90 | 90 | E
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 357 | 270 | 180
GYM_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 357 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 32 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 168 | 270 | 180
KITCHEN_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 168 | 90 | 0
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 76 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 399 | 270 | 180
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 399 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 76 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 171 | 270 | 180
LOBBY_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 171 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 36 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 546 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 546 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 252 | 270 | 180
MECH_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 252 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 140 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 315 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 315 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 84 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 441 | 270 | 180
OFFICES_ZN_1_FLR_1_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 441 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
BATH_ZN_1_FLR_1_WALL_5_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 14 | 14 | 2.615 | 0.702 | 0.633 | No | BATH_ZN_1_FLR_1_WALL_5 | 270 | W
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 21 | 21 | 2.615 | 0.702 | 0.633 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 2.615 | 0.702 | 0.633 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
COMPUTER_CLASS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 25.2 | 25.2 | 2.615 | 0.702 | 0.633 | No | COMPUTER_CLASS_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 15.4 | 15.4 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 4.2 | 4.2 | 2.615 | 0.702 | 0.633 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_7 | 270 | W
GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 23.8 | 23.8 | 2.615 | 0.702 | 0.633 | No | GYM_ZN_1_FLR_1_WALL_2 | 90 | E
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_1 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_2 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_3 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_4 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_5 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_6 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_7 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_8 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
GYM_ZN_1_FLR_1_CEILING_SKYLIGHT_9 | SKYLIGHT CONS 8 | 1.78 | 1.78 | 2.561 | 0.767 | 0.855 | No | GYM_ZN_1_FLR_1_CEILING | 90
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 11.2 | 11.2 | 2.615 | 0.702 | 0.633 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 2.615 | 0.702 | 0.633 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 2.615 | 0.702 | 0.633 | No | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 26.6 | 26.6 | 2.615 | 0.702 | 0.633 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 12.6 | 12.6 | 2.615 | 0.702 | 0.633 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 74.2 | 74.2 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 49 | 49 | 2.615 | 0.702 | 0.633 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 2.615 | 0.702 | 0.633 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 29.4 | 29.4 | 2.615 | 0.702 | 0.633 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
Total or Average |  |  | 895.19 | 2.61 | 0.703 | 0.637
North Total or Average |  |  | 324.79 | 2.61 | 0.702 | 0.633
Non-North Total or Average |  |  | 570.4 | 2.61 | 0.704 | 0.639
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 637088.38 | 0.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8737.82 | 6978.51 | 1759.31 | 0.8 | 4.04
PSZ-AC_2:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17746.6 | 14173.41 | 3573.18 | 0.8 | 4.01
PSZ-AC_2:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37513.44 | 29960.31 | 7553.13 | 0.8 | 3.73
VAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 77195.66 | 61652.72 | 15542.94 | 0.8 | 4.18
VAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 92054.22 | 73519.58 | 18534.63 | 0.8 | 4.14
VAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 65925.78 | 52651.97 | 13273.81 | 0.8 | 4.32
VAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 73404.5 | 58624.89 | 14779.61 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6312.8 | -
COMPUTER_CLASS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4699.32 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8785.91 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8585.74 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8612.79 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6151.18 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6162.09 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6349.59 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5641.11 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5642.34 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5583.45 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9778.31 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8570.99 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14442.68 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5960.17 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29011.34 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27414.69 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27766.05 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12466.19 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12469.86 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8224.79 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14439.16 | -
PSZ-AC_1:6_HEATC | Coil:Heating:Gas | 51843.23 | 0.8
PSZ-AC_2:5_HEATC | Coil:Heating:Gas | 105294.08 | 0.78
PSZ-AC_2:7_HEATC | Coil:Heating:Gas | 222574.67 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 62830.07 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 74923.54 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 53657.44 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 59744.41 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATH_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.28 | 104.73 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.36 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.2 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 612.26 | 1 | Fan Energy
PSZ-AC_2:5_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.07 | 1221.3 | 1 | Fan Energy
PSZ-AC_2:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2478.36 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.66 | 8895.09 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.56 | 10432.37 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.98 | 7596.49 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.43 | 8458.25 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 3508.08 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 1 | 845000 | 0.8 | 0.68 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 111708.5208 | 118.8647 | 365.6052 | 0 | 0.0014 | 73316.5013 | 41349.2659
February | 95185.2115 | 102.014 | 326.8227 | 0 | 0.0012 | 65544.0878 | 35345.6191
March | 86948.1919 | 96.4815 | 367.4844 | 0 | 0.0013 | 73719.5172 | 32794.045
April | 62910.5605 | 72.9322 | 331.245 | 0 | 0.0012 | 66465.6551 | 24208.5512
May | 55658.5431 | 67.513 | 355.5753 | 0 | 0.0012 | 71359.8909 | 21877.7392
June | 54976.724 | 67.7673 | 373.8426 | 0 | 0.0013 | 75029.5877 | 21776.1417
July | 36432.115 | 44.916 | 247.9021 | 0 | 0.0008 | 49753.5679 | 14431.869
August | 38595.4261 | 46.95 | 249.3766 | 0 | 0.0009 | 50047.4788 | 15191.3922
September | 54210.5786 | 64.8927 | 328.2503 | 0 | 0.0011 | 65873.1457 | 21175.6372
October | 70817.5334 | 81.0375 | 350.6768 | 0 | 0.0012 | 70360.3598 | 27087.9242
November | 93828.8649 | 102.115 | 354.6894 | 0 | 0.0013 | 71142.525 | 35081.1906
December | 103819.1194 | 111.4267 | 359.8012 | 0 | 0.0013 | 72158.9108 | 38576.2136
Annual Sum or Average | 865091.3892 | 976.9108 | 4011.2716 | 0 | 0.0142 | 804771.228 | 328895.5889
Minimum of Months | 36432.115 | 44.916 | 247.9021 | 0 | 0.0008 | 49753.5679 | 14431.869
Maximum of Months | 111708.5208 | 118.8647 | 373.8426 | 0 | 0.0014 | 75029.5877 | 41349.2659
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 258339000000 | 180143.044 | 02-JAN-11:09 | 80527.626 | 79091.122 | 7736.624 | 0 | 0 | 6368 | 3021.879 | 0 | 0 | 0 | 0 | 0 | 3397.792 | 0 | 0
February | 230952000000 | 174942.484 | 03-FEB-09:09 | 80527.626 | 75091.738 | 7736.624 | 0 | 0 | 6368 | 3281.019 | 0 | 0 | 0 | 0 | 0 | 1937.477 | 0 | 0
March | 259759000000 | 174792.252 | 14-MAR-07:10 | 80527.626 | 75091.738 | 7736.624 | 0 | 0 | 6368 | 3167.765 | 0 | 0 | 0 | 0 | 0 | 1900.5 | 0 | 0
April | 234199000000 | 173732.521 | 24-APR-11:00 | 80527.626 | 79091.122 | 11932.899 | 0 | 0 | 0 | 37.763 | 0 | 0 | 0 | 0 | 0 | 2143.111 | 0 | 0
May | 251444000000 | 209966.787 | 24-MAY-14:00 | 80527.626 | 73092.045 | 22535.698 | 0 | 31408.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2403.148 | 0 | 0
June | 264375000000 | 240850.313 | 20-JUN-14:00 | 80527.626 | 73092.045 | 24504.641 | 0 | 60162.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2563.378 | 0 | 0
July | 175312000000 | 140234.705 | 21-JUL-15:00 | 44737.57 | 40636.785 | 10203.223 | 0 | 42343.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2313.875 | 0 | 0
August | 176348000000 | 140532.606 | 15-AUG-13:00 | 44737.57 | 41836.601 | 10793.687 | 0 | 40736.525 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 2428.215 | 0 | 0
September | 232111000000 | 182401.195 | 07-SEP-14:00 | 80527.626 | 73092.045 | 13861.813 | 0 | 12640.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2278.854 | 0 | 0
October | 247922000000 | 172605.454 | 31-OCT-07:10 | 80527.626 | 75091.738 | 7736.624 | 0 | 0 | 6368 | 969.441 | 0 | 0 | 0 | 0 | 0 | 1912.025 | 0 | 0
November | 250678000000 | 176443.742 | 30-NOV-10:20 | 80527.626 | 79091.122 | 7736.624 | 0 | 0 | 6368 | 763.93 | 0 | 0 | 0 | 0 | 0 | 1956.439 | 0 | 0
December | 254260000000 | 180002.562 | 29-DEC-11:09 | 80527.626 | 79091.122 | 7736.624 | 0 | 0 | 6368 | 2877.879 | 0 | 0 | 0 | 0 | 0 | 3401.31 | 0 | 0
Annual Sum or Average | 2835700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 175312000000 | 140234.705 |  | 44737.57 | 40636.785 | 7736.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900.5 | 0 | 0
Maximum of Months | 264375000000 | 240850.313 |  | 80527.626 | 79091.122 | 24504.641 | 0 | 60162.623 | 6368 | 3281.019 | 0 | 0 | 0 | 0 | 0 | 3401.31 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 74951.3 | 24514.52 | 0 | 99465.82
Cost per Total Building Area ($/m2) | 10.91 | 3.57 | 0 | 14.48
Cost per Net Conditioned Building Area ($/m2) | 10.91 | 3.57 | 0 | 14.48

## Picture
DOE Commercial Building Benchmark - Primary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75 | 1444.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.75 | 33.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75 | 2395.71
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 9.75 | 48.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 2607.14
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720