## BuildingSummary
Building Summary - Secondary School new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Secondary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 19592 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.28
| Total | 0.34
| Skylight/TDD Percentage | 1.12%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Flat built-up | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6384
| Net Dimensions - Total Area (m2) | 4088.16
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | Insulation Entirely Above Deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11902
| Net Dimensions - Total Area (m2) | 11768.6976
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| South | 753.18
| East | 291.61
| North | 753.18
| West | 291.2
| Total Area (m2) | 2089.17
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 133.8
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 11902
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 6792
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 39184
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.26 | See Benchmark Technical Report
HVAC
| System Type | MZ VAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | Air cooled chiller, PACU (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Fan Control | Variable, constant (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 815.28

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
First Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.017006
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.017006
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.017006
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.21987
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.12093
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200 | 70 | 0 | 0 | 5.38 | 4 | 0 | 0 | 2.5 | 0.3 | 342 | 0 | 0.047735
LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60 | 21 | 0 | 0 | 13.988 | 4 | 0 | 0 | 2.5 | 0.3 | 63 | 0 | 0.07774
BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116 | 40.6 | 10 | 21 | 9.684 | 4 | 0 | 197.4991 | 0 | 0 | 0 | 0 | 0.1503
OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208 | 72.8 | 20 | 26.6 | 11.836 | 10.8 | 0 | 0 | 2.5 | 0.3 | 226.1 | 0 | 0.10638
GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.28 | 1 | 1976 | 15.064 | 5 | 0 | 717.2337 | 0 | 1.5 | 2964 | 0 | 0.13605
AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608 | 266.35 | 3.33 | 374.7748 | 15.064 | 5 | 0 | 0 | 0 | 1.5 | 1872 | 0 | 0.20232
AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512 | 106.4 | 1 | 988 | 9.684 | 5 | 0 | 0 | 2.5 | 0.3 | 2766.4 | 0 | 0.20655
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6.67 | 32.3838 | 12.912 | 222.194 | 1678.56 | 503.4582 | 0 | 0 | 0 | 2831.682 | 0.045349
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200 | 70 | 1.3935 | 447.7782 | 15.064 | 19.2604 | 0 | 0 | 3.8 | 0.9 | 2263.1573 | 0 | 0.087209
MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.14 | 4 | 0 | 0 | 0 | 0.25439 | 87 | 0 | 0
Total Conditioned Zones |  |  | 11902 | 64456 |  | 3752 | 1374.23 |  | 4829.9568
Second Floor
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 20 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.38 | 4 | 0 | 0 | 0 | 0.3 | 96 | 0 | 0.2891
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80 | 28 | 4 | 24.75 | 15.064 | 10 | 0 | 0 | 5 | 0.6 | 183.15 | 0 | 0.49196
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212 | 74.2 | 4 | 119.25 | 15.064 | 20 | 0 | 0 | 5 | 0.6 | 882.45 | 0 | 0.39302
MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200 | 70 | 0 | 0 | 5.38 | 4 | 0 | 0 | 2.5 | 0.3 | 342 | 0 | 0.31983
LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60 | 21 | 0 | 0 | 13.988 | 4 | 0 | 0 | 2.5 | 0.3 | 63 | 0 | 0.34983
BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116 | 40.6 | 10 | 21 | 9.684 | 4 | 0 | 197.4991 | 0 | 0 | 0 | 0 | 0.42239
OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208 | 72.8 | 20 | 26.6 | 11.836 | 10.8 | 0 | 0 | 2.5 | 0.3 | 226.1 | 0 | 0.37847
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236 | 83.01 | 4.35 | 49.6552 | 13.988 | 10 | 0 | 0 | 5 | 0.6 | 377.8759 | 0 | 0.34854
MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.14 | 4 | 0 | 0 | 0 | 0.5 | 171 | 0 | 0
Total Conditioned Zones |  |  | 7690 | 30760 |  | 2632 | 921.61 |  | 1060.6752
Building Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384 | 2295.84 |  | 5890.632
4088.16
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Weighting Factor
Fabric
Exterior walls
| Construction Type | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed | Steel-framed
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7473 | 2.7473
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 2.8011 | 3.663
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.262 | 0.262 | 0.262 | 0.34 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.402 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.318 | 0.318 | 0.318 | 0.34 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.495 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 6.53 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.82 | 3.23
| SHGC | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.501
| Visible transmittance | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.457 | 0.775 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 1700.3656 | 1702.4569 | 3148.5809 | 1541.8156 | 1545.6702 | 2776.9815 | 1791.8465 | 1605.1873 | 2469.058 | 1072.7817 | 1563.3134 | 2306.7144 | 1475.8496 | 2334.6429 | 1246.1131 | 2145.8262
| PSZ-AC_1:5_COOLC DXCOIL | 622.9717 | 636.1183 | 651.3031 | 640.2282 | 398.4731 | 565.7682 | 676.7436 | 633.8435 | 491.054 | 422.7951 | 627.9709 | 475.4953 | 624.2337 | 445.2451 | 588.1377 | 327.0982
| PSZ-AC_2:6_COOLC DXCOIL | 285.9452 | 291.6386 | 299.9534 | 266.4222 | 226.7103 | 278.836 | 274.6024 | 274.538 | 309.433 | 241.2854 | 269.2249 | 292.7252 | 266.373 | 279.5497 | 250.3524 | 228.757
| PSZ-AC_3:7_COOLC DXCOIL | 346.5705 | 363.1969 | 292.2445 | 348.1772 | 197.2725 | 244.28 | 342.6471 | 332.2696 | 259.9605 | 183.7067 | 314.9542 | 236.935 | 302.9377 | 219.5986 | 232.116 | 150.9721
| PSZ-AC_4:8_COOLC DXCOIL | 116.8991 | 117.6708 | 104.6534 | 120.6452 | 76.126 | 87.869 | 87.1082 | 117.5258 | 91.7876 | 75.8121 | 117.9977 | 91.0281 | 118.896 | 87.5556 | 95.8515 | 75.4829
| PSZ-AC_5:9_COOLC DXCOIL | 142.256 | 146.0546 | 135.6477 | 140.0335 | 82.1201 | 110.3693 | 156.0346 | 137.0341 | 105.8173 | 79.331 | 134.3552 | 100.9781 | 134.1789 | 93.9421 | 116.7635 | 74.1239
Heating (kW)
| HEATSYS1 BOILER | 2197.4471 | 2571.5387 | 2654.4181 | 2498.0069 | 2058.065 | 2481.5912 | 2819.3713 | 2748.0106 | 2470.9858 | 2409.7602 | 2849.6665 | 2526.9926 | 2954.7345 | 2777.1733 | 2900.3098 | 3153.411
| PSZ-AC_1:5_HEATC | 291.3808 | 392.7802 | 339.2973 | 426.4462 | 283.5656 | 365.9706 | 545.8677 | 469.9769 | 433.9852 | 359.2613 | 543.9433 | 501.6394 | 584.3444 | 569.7468 | 567.593 | 582.2214
| PSZ-AC_2:6_HEATC | 162.3044 | 215.6291 | 198.8165 | 226.6878 | 159.1102 | 202.3411 | 194.9628 | 257.9497 | 217.8277 | 212.9751 | 291.6236 | 247.4158 | 314.2777 | 290.7186 | 314.2693 | 376.8084
| PSZ-AC_3:7_HEATC | 162.1005 | 224.261 | 202.4439 | 231.9155 | 143.9586 | 206.371 | 276.3823 | 246.3685 | 229.7487 | 176.7126 | 272.8107 | 249.9623 | 290.8291 | 281.0039 | 273.9937 | 268.7241
| PSZ-AC_4:8_HEATC | 54.6769 | 72.6575 | 62.879 | 80.3599 | 55.5526 | 67.8319 | 70.2623 | 87.142 | 81.1203 | 72.9258 | 102.2087 | 96.0331 | 112.2621 | 112.0383 | 113.9303 | 134.3565
| PSZ-AC_5:9_HEATC | 66.537 | 90.1834 | 79.1263 | 93.2742 | 59.9267 | 80.1777 | 125.8589 | 101.6069 | 93.5196 | 74.3661 | 116.3773 | 106.5302 | 125.6047 | 120.2106 | 121.5215 | 131.9375
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| PSZ-AC_1:5_COOLC DXCOIL | 3.26 | 3.26 | 3.25 | 3.25 | 3.71 | 3.38 | 3.73 | 3.26 | 3.74 | 3.56 | 3.26 | 3.74 | 3.26 | 3.74 | 3.26 | 3.76
| PSZ-AC_2:6_COOLC DXCOIL | 3.54 | 3.61 | 3.76 | 3.7 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.72 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76
| PSZ-AC_3:7_COOLC DXCOIL | 3.26 | 3.26 | 3.57 | 3.26 | 3.95 | 3.76 | 3.76 | 3.26 | 3.76 | 3.95 | 3.27 | 3.76 | 3.29 | 3.94 | 3.48 | 4.14
| PSZ-AC_4:8_COOLC DXCOIL | 3.51 | 3.51 | 3.68 | 3.51 | 4.18 | 3.98 | 4.18 | 3.51 | 4.18 | 4.18 | 3.51 | 4.18 | 3.52 | 4.18 | 3.8 | 4.18
| PSZ-AC_5:9_COOLC DXCOIL | 3.51 | 3.51 | 3.64 | 3.51 | 4.18 | 3.86 | 4.15 | 3.51 | 4.18 | 4.12 | 3.51 | 4.18 | 3.51 | 4.18 | 3.6 | 4.18
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
| PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_4:8_HEATC | 0.8 | 0.78 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_1:5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:6_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_3:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_4:8_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_5:9_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83
| VAV_POD_1_FAN | 23.79 | 25.88 | 30.1 | 24.46 | 21.73 | 27.5 | 32.42 | 25.81 | 29.4 | 23.91 | 24.94 | 27.57 | 25.12 | 26.8 | 24.47 | 23.12
| VAV_POD_2_FAN | 23.75 | 25.84 | 30.06 | 24.36 | 21.61 | 27.4 | 32.26 | 25.64 | 29.22 | 23.67 | 24.75 | 27.36 | 24.92 | 26.56 | 24.22 | 22.77
| VAV_POD_3_FAN | 26.03 | 28.14 | 32.43 | 26.72 | 24.03 | 29.92 | 34.07 | 27.96 | 32.03 | 26.18 | 27.12 | 30.18 | 27.31 | 29.25 | 26.72 | 25.22
| VAV_OTHER_FAN | 35.57 | 38.04 | 42.99 | 36.57 | 32.68 | 40.2 | 40.34 | 37.74 | 43.09 | 33.49 | 36.37 | 40.18 | 36.24 | 38.37 | 34.66 | 29.86
| PSZ-AC_1:5_FAN | 25.09 | 25.62 | 26.23 | 25.78 | 23.47 | 26.17 | 40.88 | 25.52 | 29.66 | 22.56 | 25.29 | 28.72 | 25.14 | 26.9 | 23.85 | 19.76
| PSZ-AC_2:6_FAN | 15 | 16.01 | 18.12 | 15.53 | 13.7 | 16.84 | 16.59 | 16.58 | 18.69 | 14.58 | 15.92 | 17.68 | 16.09 | 16.89 | 15.12 | 13.82
| PSZ-AC_3:7_FAN | 13.96 | 14.63 | 15.65 | 14.02 | 11.92 | 14.76 | 20.7 | 13.38 | 15.7 | 11.1 | 12.68 | 14.31 | 12.51 | 13.27 | 11.52 | 9.12
| PSZ-AC_4:8_FAN | 4.71 | 4.74 | 4.86 | 4.86 | 4.6 | 4.85 | 5.26 | 4.73 | 5.54 | 4.58 | 4.75 | 5.5 | 4.83 | 5.29 | 4.79 | 4.56
| PSZ-AC_5:9_FAN | 5.73 | 5.88 | 6.12 | 5.64 | 4.96 | 5.73 | 9.43 | 5.52 | 6.39 | 4.67 | 5.41 | 6.1 | 5.4 | 5.68 | 5.11 | 4.48
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.089373 | 0.11699 | 0.085969 | 0.10251 | 0.061986 | 0.10209 | 0.15787 | 0.08018 | 0.036993 | 0.072352 | 0.08345 | 0.036997 | 0.064282 | 0.079127 | 0.061481 | 0.095519
| Total Cost ($/m2) | 18.44 | 22.2 | 16.88 | 16.41 | 8.33 | 17.61 | 21.61 | 12.5 | 5.61 | 8.75 | 11.97 | 5.23 | 9.06 | 10.66 | 7.95 | 12.01
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011442 | 0.008087 | 0.0082866 | 0.009714 | 0.0085479 | 0.0077562 | 0.0085347 | 0.0097013 | 0.0069152 | 0.0084118 | 0.0083229 | 0.0069214 | 0.0078854 | 0.0080967 | 0.0078675 | 0.004123
| Total Cost ($/m2) | 0.52 | 1.26 | 1.06 | 2.41 | 0.76 | 1.2 | 2.26 | 4.16 | 1.86 | 3.25 | 5.04 | 2.81 | 6.44 | 5.32 | 7.79 | 6.59
Total Utility Costs
| Cost Intensity ($/m2) | 18.96 | 23.47 | 17.94 | 18.81 | 9.09 | 18.8 | 23.87 | 16.66 | 7.46 | 12 | 17.01 | 8.04 | 15.5 | 15.98 | 15.74 | 18.59
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1767688.8889 | 1428650 | 1520019.4444 | 858222.2222 | 430694.4444 | 1081763.8889 | 255088.8889 | 755136.1111 | 598619.4444 | 161836.1111 | 504152.7778 | 419261.1111 | 426202.7778 | 292652.7778 | 211280.5556 | 146408.3333
| Interior Lighting | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222 | 927397.2222
| Exterior Lighting | 104397.2222 | 104358.3333 | 104338.8889 | 104322.2222 | 104241.6667 | 104219.4444 | 104275 | 104211.1111 | 104250 | 104044.4444 | 104227.7778 | 104166.6667 | 104158.3333 | 104136.1111 | 104075 | 103438.8889
| Interior Equipment | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667 | 673616.6667
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 506619.4444 | 524088.8889 | 562188.8889 | 516130.5556 | 442527.7778 | 537063.8889 | 669752.7778 | 539908.3333 | 611825 | 452388.8889 | 547408.3333 | 594658.3333 | 576650 | 590069.4444 | 565763.8889 | 559122.2222
| Pumps | 16688.8889 | 14711.1111 | 13666.6667 | 10575 | 7644.4444 | 9686.1111 | 6283.3333 | 9963.8889 | 7886.1111 | 4538.8889 | 8258.3333 | 6594.4444 | 8441.6667 | 6352.7778 | 7002.7778 | 9222.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 45730.5556 | 45638.8889 | 45244.4444 | 45472.2222 | 45666.6667 | 45083.3333 | 45502.7778 | 45280.5556 | 45030.5556 | 45305.5556 | 45113.8889 | 44975 | 44872.2222 | 44836.1111 | 44708.3333 | 43961.1111
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4042136.1111 | 3718458.3333 | 3846469.4444 | 3135733.3333 | 2631788.8889 | 3378830.5556 | 2681913.8889 | 3055511.1111 | 2968625 | 2369125 | 2810172.2222 | 2770666.6667 | 2761336.1111 | 2639058.3333 | 2533844.4444 | 2463163.8889
Gas (MJ)
| Heating | 158090 | 2266040 | 1752000 | 4002670 | 912140 | 2214120 | 4296470 | 7493330 | 4372540 | 6658340 | 10933270 | 7011210 | 15018500 | 11896000 | 18358720 | 30200700
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460 | 544460
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 183800 | 250280 | 219890 | 309320 | 289350 | 263240 | 339220 | 356310 | 347290 | 372910 | 396330 | 392600 | 431980 | 435240 | 485210 | 548270
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 886350 | 3060780 | 2516350 | 4856450 | 1745950 | 3021820 | 5180160 | 8394100 | 5264290 | 7575710 | 11874050 | 7948270 | 15994940 | 12875700 | 19388380 | 31293430
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 15438040 | 16447230 | 16363640 | 16145080 | 11220390 | 15185600 | 14835040 | 19393940 | 15951340 | 16104570 | 21990670 | 17922670 | 25935750 | 22376320 | 28510220 | 40160820
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 324.8101 | 262.5122 | 279.3012 | 157.697 | 79.1394 | 198.7725 | 46.8722 | 138.7551 | 109.9954 | 29.7371 | 92.6373 | 77.0386 | 78.3141 | 53.7745 | 38.8225 | 26.9023
| Interior Lighting (elec) | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078 | 170.4078
| Exterior Lighting (elec) | 19.1828 | 19.1757 | 19.1721 | 19.169 | 19.1542 | 19.1502 | 19.1604 | 19.1486 | 19.1558 | 19.118 | 19.1517 | 19.1405 | 19.1389 | 19.1349 | 19.1236 | 19.0067
| Interior Equipment (elec) | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776 | 123.776
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 93.0905 | 96.3005 | 103.3013 | 94.8382 | 81.3138 | 98.6847 | 123.066 | 99.2073 | 112.4219 | 83.1258 | 100.5854 | 109.2676 | 105.9586 | 108.4244 | 103.9582 | 102.7379
| Pumps (elec) | 3.0666 | 2.7031 | 2.5112 | 1.9431 | 1.4047 | 1.7798 | 1.1546 | 1.8308 | 1.4491 | 0.83401 | 1.5175 | 1.2117 | 1.5511 | 1.1673 | 1.2867 | 1.6946
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 8.4029 | 8.3861 | 8.3136 | 8.3555 | 8.3912 | 8.284 | 8.3611 | 8.3202 | 8.2743 | 8.3248 | 8.2896 | 8.2641 | 8.2452 | 8.2386 | 8.2151 | 8.0778
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 742.7363 | 683.261 | 706.7829 | 576.1862 | 483.5872 | 620.8549 | 492.7976 | 561.4455 | 545.4803 | 435.3231 | 516.3648 | 509.1058 | 507.3913 | 484.9229 | 465.59 | 452.6026
Gas (MJ/m2)
| Heating (gas) | 8.0691 | 115.6615 | 89.4243 | 204.3012 | 46.5568 | 113.0114 | 219.2972 | 382.4689 | 223.1799 | 339.8499 | 558.0477 | 357.8609 | 766.5629 | 607.1866 | 937.0519 | 1541.4812
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899 | 27.7899
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 9.3814 | 12.7746 | 11.2235 | 15.7881 | 14.7688 | 13.4361 | 17.3142 | 18.1865 | 17.7261 | 19.0338 | 20.2292 | 20.0388 | 22.0488 | 22.2152 | 24.7657 | 27.9844
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 45.2404 | 156.226 | 128.4376 | 247.8792 | 89.1155 | 154.2374 | 264.4018 | 428.4453 | 268.6959 | 386.6736 | 606.0663 | 405.6896 | 816.4016 | 657.1917 | 989.607 | 1597.2555
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 787.9767 | 839.487 | 835.2205 | 824.0649 | 572.7026 | 775.0919 | 757.1989 | 989.8908 | 814.1762 | 821.9972 | 1122.4311 | 914.7953 | 1323.7929 | 1142.1151 | 1455.197 | 2049.8581
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1070.2352 | 1014.8574 | 892.0745 | 674.6981 | 808.0903 | 704.2982 | 643.9502 | 665.1511 | 622.2885 | 510.3939 | 527.6184 | 659.0176 | 526.0498 | 547.1492 | 518.5895 | 528.6239
| Feb | 1110.7461 | 942.0217 | 968.5222 | 678.6384 | 782.1422 | 748.3446 | 763.3884 | 649.7043 | 746.7558 | 598.5172 | 527.9882 | 597.5871 | 526.3019 | 644.0135 | 518.9531 | 522.3798
| Mar | 1167.183 | 1006.9734 | 1144.5067 | 806.742 | 758.7503 | 878.7367 | 719.958 | 872.4587 | 767.0557 | 628.253 | 718.5545 | 785.7868 | 615.7632 | 720.6105 | 519.4546 | 518.7368
| Apr | 1219.625 | 1100.7576 | 1182.5932 | 952.215 | 858.0094 | 1105.2582 | 783.9193 | 858.9674 | 923.3668 | 603.6514 | 706.002 | 847.0296 | 712.4815 | 680.3309 | 603.7178 | 503.6079
| May | 1359.0103 | 1406.4812 | 1333.6035 | 1120.3087 | 850.625 | 1227.2714 | 901.0018 | 1135.9303 | 1041.1971 | 764.491 | 1086.9045 | 952.0972 | 1027.5711 | 845.7855 | 752.0775 | 645.6364
| Jun | 1478.5067 | 1402.8609 | 1574.6424 | 1244.2859 | 814.2306 | 1414.6002 | 922.6218 | 1436.2547 | 1162.119 | 795.6758 | 1414.1782 | 1092.1068 | 1293.2539 | 1114.0176 | 1036.379 | 823.9348
| Jul | 1210.0203 | 1388.05 | 1340.7515 | 1223.389 | 674.4472 | 1182.0579 | 843.5341 | 1339.8328 | 990.1788 | 702.7617 | 1179.3448 | 929.203 | 1106.5606 | 877.6313 | 875.6745 | 636.8557
| Aug | 1289.5134 | 1274.1686 | 1334.343 | 1124.2252 | 798.7134 | 1150.9429 | 813.2823 | 1341.3397 | 972.9763 | 644.6299 | 1167.1991 | 940.3855 | 1055.4485 | 828.5866 | 832.7423 | 617.5253
| Sep | 1368.166 | 1478.1351 | 1412.4684 | 1176.3756 | 950.5919 | 1231.5437 | 1159.6511 | 1118.6633 | 1010.7753 | 830.6687 | 1052.2833 | 1006.242 | 999.3829 | 884.8318 | 874.2665 | 562.719
| Oct | 1319.1062 | 1217.0068 | 1191.3824 | 1044.1054 | 887.5151 | 1105.8036 | 866.6293 | 982.8334 | 908.0485 | 654.0703 | 837.2427 | 926.0638 | 741.9901 | 781.865 | 621.6146 | 514.9952
| Nov | 1169.0996 | 1087.0012 | 1075.9267 | 732.1759 | 813.7578 | 758.4964 | 736.0094 | 851.3497 | 701.7545 | 591.888 | 839.8771 | 731.9195 | 645.7982 | 576.9583 | 517.8813 | 519.5489
| Dec | 1059.8029 | 990.6717 | 873.6723 | 702.1943 | 819.5694 | 756.5684 | 657.2104 | 586.616 | 599.4241 | 510.6675 | 525.4473 | 576.107 | 525.0814 | 544.9288 | 517.8055 | 526.1588
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:39 | 26-JAN-16:10 | 23-JAN-16:30 | 26-JAN-12:00 | 18-JAN-14:00 | 27-JAN-14:00 | 09-JAN-11:39 | 25-JAN-14:00 | 17-JAN-16:00 | 11-JAN-11:39 | 24-JAN-13:00 | 20-JAN-11:39 | 05-JAN-08:09 | 06-JAN-11:39 | 02-JAN-11:09
| Feb | 23-FEB-11:00 | 23-FEB-16:10 | 28-FEB-16:10 | 21-FEB-13:00 | 13-FEB-11:00 | 08-FEB-16:10 | 14-FEB-12:00 | 15-FEB-14:00 | 14-FEB-16:10 | 21-FEB-13:00 | 10-FEB-11:39 | 07-FEB-14:00 | 28-FEB-11:39 | 02-FEB-14:00 | 27-FEB-11:39 | 03-FEB-08:09
| Mar | 13-MAR-15:09 | 29-MAR-11:00 | 17-MAR-15:00 | 28-MAR-15:20 | 30-MAR-11:00 | 31-MAR-15:00 | 01-MAR-12:00 | 09-MAR-16:10 | 02-MAR-14:00 | 29-MAR-15:00 | 31-MAR-15:09 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 14-MAR-10:39 | 14-MAR-07:10
| Apr | 17-APR-12:00 | 17-APR-15:00 | 26-APR-15:09 | 13-APR-15:09 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-15:09 | 04-APR-15:00 | 21-APR-15:00 | 14-APR-13:00 | 07-APR-14:39 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 19-APR-10:39
| May | 24-MAY-14:00 | 18-MAY-14:09 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-09:09 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-15:00 | 31-MAY-15:00 | 30-MAY-14:00
| Jun | 26-JUN-14:00 | 13-JUN-15:09 | 28-JUN-15:39 | 19-JUN-15:09 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-15:00 | 29-JUN-13:00 | 28-JUN-15:09 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-15:09 | 30-JUN-15:09 | 14-JUN-15:09 | 20-JUN-15:00
| Jul | 10-JUL-12:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-11:00 | 10-JUL-09:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-11:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-12:00 | 18-JUL-13:00 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-14:00 | 21-JUL-16:00
| Aug | 21-AUG-13:00 | 31-AUG-10:00 | 01-AUG-15:00 | 17-AUG-14:00 | 08-AUG-09:00 | 04-AUG-14:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-13:00
| Sep | 26-SEP-15:00 | 15-SEP-14:39 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-11:00 | 20-SEP-15:00 | 28-SEP-15:09 | 08-SEP-15:09 | 21-SEP-13:00 | 13-SEP-15:00 | 06-SEP-10:00 | 05-SEP-13:00 | 14-SEP-15:09 | 07-SEP-15:00 | 07-SEP-15:09 | 07-SEP-15:00
| Oct | 06-OCT-15:09 | 30-OCT-12:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:09 | 30-OCT-12:00 | 03-OCT-11:00 | 11-OCT-15:00 | 17-OCT-15:00 | 31-OCT-12:00 | 05-OCT-15:09 | 06-OCT-15:09 | 06-OCT-15:00 | 27-OCT-11:00 | 20-OCT-07:00
| Nov | 01-NOV-11:39 | 27-NOV-16:00 | 13-NOV-16:10 | 22-NOV-16:10 | 20-NOV-12:00 | 10-NOV-16:10 | 16-NOV-15:00 | 03-NOV-13:00 | 08-NOV-14:00 | 03-NOV-13:00 | 02-NOV-11:00 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:39 | 10-NOV-11:39 | 28-NOV-10:20
| Dec | 15-DEC-16:10 | 19-DEC-14:00 | 11-DEC-16:10 | 26-DEC-13:00 | 19-DEC-12:00 | 05-DEC-14:00 | 07-DEC-14:00 | 08-DEC-10:00 | 05-DEC-13:00 | 13-DEC-11:39 | 21-DEC-11:39 | 21-DEC-14:09 | 04-DEC-11:39 | 22-DEC-08:09 | 04-DEC-11:39 | 29-DEC-11:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86
| Total Building | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86 | 2677.86
Emissions
| Carbon Equivalent (kg) | 1124540 | 1295530 | 1206530 | 1053500 | 339050.3161 | 1194090 | 406836.2648 | 975914.5561 | 1307610 | 309163.817 | 1712360 | 1275140 | 1233620 | 1196590 | 1216940 | 1257410
| CO2 (kg) | 2613100 | 3271820 | 2861790 | 2445270 | 912113.5985 | 2856580 | 1106680 | 2286410 | 3099930 | 804591.3004 | 4075490 | 3051340 | 3012360 | 2913920 | 3009640 | 3366620
| NOX (kg) | 4568.9544 | 4235.6744 | 4734.3257 | 4462.9494 | 785.3025 | 4569.3332 | 961.1245 | 4094.0864 | 5206.7249 | 1016.9292 | 6856.2044 | 5003.078 | 4732.8863 | 4590.7275 | 4565.8063 | 3655.3512
| SO2 (kg) | 17302.1944 | 17737.8685 | 15468.0997 | 11007.7242 | 7658.6591 | 18587.0733 | 7805.4351 | 11156.0854 | 12964.8069 | 1833.175 | 18941.497 | 12101.0788 | 6521.4845 | 7050.0551 | 5985.4742 | 12546.883
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0789 | 0.0502 | 0.0422 | 0.0407 | 0.0036 | 0.0351 | 0.0041 | 0.0458 | 0.051 | 0.0079 | 0.0584 | 0.048 | 0.0493 | 0.0503 | 0.0457 | 0.0458
| Water for Electricity (m3) | 2141.35 | 6050.37 | 114257 | 19578.3 | 46208.3 | 92694.8 | 47088.4 | 693.7158 | 13479.9 | 24204.9 | 4359.81 | 12581 | 4284.05 | 167169 | 3931.11 | 2516.57

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15438.04 | 787.98 | 787.98
Net Site Energy | 15438.04 | 787.98 | 787.98
Total Source Energy | 49235.84 | 2513.06 | 2513.06
Net Source Energy | 49235.84 | 2513.06 | 2513.06
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 158.09 | 0 | 0 | 0 | 0
Cooling | 6363.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1823.83 | 0 | 0 | 0 | 0 | 0
Pumps | 60.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 183.8 | 0 | 0 | 0 | 2677.86
Refrigeration | 164.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14551.69 | 886.35 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 15.4 | 15.4 | 6.49 | 0.441 | 0.44 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 74.2 | 74.2 | 6.49 | 0.441 | 0.44 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 25.2 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 25.2 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 21 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 21 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 21 | 21 | 6.49 | 0.441 | 0.44 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 21 | 21 | 6.49 | 0.441 | 0.44 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 53.2 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 19.6 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 53.2 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 19.6 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 33.6 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 72.8 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 33.6 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 72.8 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 53.2 | 53.2 | 6.49 | 0.441 | 0.44 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 53.2 | 53.2 | 6.49 | 0.441 | 0.44 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 49.41 | 49.41 | 6.49 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 33.6 | 33.6 | 6.49 | 0.441 | 0.44 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 36.4 | 36.4 | 6.49 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.44_VT_0.44 | 33.6 | 33.6 | 6.49 | 0.441 | 0.44 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 6.49 | 0.321 | 0.327
North Total or Average |  |  | 753.18 | 6.49 | 0.441 | 0.44
Non-North Total or Average |  |  | 1469.82 | 6.49 | 0.26 | 0.269
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1700365.6 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2197447.14 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 402838.28 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 402472.18 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 423524 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 471531.14 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 622971.69 | 421180.71 | 201790.98 | 0.68 | 3.26
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 285945.17 | 214508.51 | 71436.66 | 0.75 | 3.54
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 346570.55 | 234310.53 | 112260.02 | 0.68 | 3.26
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 116899.07 | 79033.5 | 37865.57 | 0.68 | 3.51
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 142256.02 | 96176.91 | 46079.11 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 291380.83 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 162304.43 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 162100.49 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 54676.88 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 66537.02 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 23.79 | 53775.26 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 23.75 | 53670.69 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 26.03 | 58828.6 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 35.57 | 80404.82 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 25.09 | 41959.9 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15 | 25243.82 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.96 | 23493.66 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.71 | 8831.27 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.73 | 10746.89 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12210.08 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15581.5 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 192322.1166 | 332.8191 | 1246.2535 | 0 | 0.0057 | 154236.1694 | 82419.2425
February | 176577.8806 | 307.8528 | 1162.1722 | 0 | 0.0053 | 143832.0482 | 75900.4977
March | 205808.2283 | 358.5317 | 1352.333 | 0 | 0.0062 | 167366.3951 | 88436.6147
April | 201834.3497 | 353.1461 | 1338.3197 | 0 | 0.0061 | 165633.2614 | 86883.0455
May | 250715.0248 | 439.3203 | 1667.541 | 0 | 0.0076 | 206378.8772 | 107989.5482
June | 261718.1951 | 458.9429 | 1743.4172 | 0 | 0.0079 | 215769.7507 | 112763.1807
July | 222484.6553 | 390.1756 | 1482.315 | 0 | 0.0068 | 183455.1056 | 95862.2993
August | 231901.3153 | 406.5159 | 1543.6862 | 0 | 0.007 | 191050.4277 | 99902.2567
September | 247565.7474 | 434.0816 | 1648.7963 | 0 | 0.0075 | 204059.192 | 106661.099
October | 232032.8112 | 406.3577 | 1541.5015 | 0 | 0.007 | 190779.757 | 99919.9487
November | 209300.8442 | 366.1193 | 1387.1134 | 0 | 0.0063 | 171672.0043 | 90088.0232
December | 180835.3544 | 315.0915 | 1188.7454 | 0 | 0.0054 | 147120.6364 | 77712.102
Annual Sum or Average | 2613100 | 4568.9544 | 17302.1944 | 0 | 0.0789 | 2141350 | 1124540
Minimum of Months | 176577.8806 | 307.8528 | 1162.1722 | 0 | 0.0053 | 143832.0482 | 75900.4977
Maximum of Months | 261718.1951 | 458.9429 | 1743.4172 | 0 | 0.0079 | 215769.7507 | 112763.1807
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1048120000000 | 1070235.176 | 06-JAN-12:00 | 218037.744 | 161697.68 | 132033.319 | 0 | 548390.502 | 0 | 4851.037 | 0 | 0 | 0 | 0 | 0 | 5224.893 | 0 | 0
February | 977419000000 | 1110746.101 | 23-FEB-11:00 | 218037.744 | 161697.68 | 133025.263 | 0 | 587663.148 | 0 | 5098.558 | 0 | 0 | 0 | 0 | 0 | 5223.708 | 0 | 0
March | 1137350000000 | 1167182.965 | 13-MAR-15:09 | 218037.744 | 142955.664 | 132435.769 | 0 | 663435.382 | 0 | 5094.902 | 0 | 0 | 0 | 0 | 0 | 5223.504 | 0 | 0
April | 1125570000000 | 1219625.018 | 17-APR-12:00 | 218037.744 | 155696.336 | 133903.932 | 0 | 701271.558 | 0 | 5494.189 | 0 | 0 | 0 | 0 | 0 | 5221.26 | 0 | 0
May | 1402460000000 | 1359010.258 | 24-MAY-14:00 | 218037.744 | 147825.664 | 133626.946 | 0 | 848489.014 | 0 | 5807.397 | 0 | 0 | 0 | 0 | 0 | 5223.493 | 0 | 0
June | 1466280000000 | 1478506.699 | 26-JUN-14:00 | 218037.744 | 147825.664 | 133806.669 | 0 | 966699.731 | 0 | 6910.119 | 0 | 0 | 0 | 0 | 0 | 5226.772 | 0 | 0
July | 1246680000000 | 1210020.265 | 10-JUL-12:00 | 121132.08 | 90545.984 | 132033.319 | 0 | 855319.344 | 0 | 6018.085 | 0 | 0 | 0 | 0 | 0 | 4971.453 | 0 | 0
August | 1298290000000 | 1289513.439 | 21-AUG-13:00 | 121132.08 | 90545.984 | 132044.129 | 0 | 934537.401 | 0 | 6280.81 | 0 | 0 | 0 | 0 | 0 | 4973.035 | 0 | 0
September | 1386700000000 | 1368165.964 | 26-SEP-15:00 | 218037.744 | 142877.04 | 133152.856 | 0 | 862881.602 | 0 | 5992.288 | 0 | 0 | 0 | 0 | 0 | 5224.435 | 0 | 0
October | 1296450000000 | 1319106.196 | 06-OCT-15:09 | 218037.744 | 142877.04 | 133968.41 | 0 | 812907.788 | 0 | 6090.443 | 0 | 0 | 0 | 0 | 0 | 5224.77 | 0 | 0
November | 1166610000000 | 1169099.566 | 01-NOV-11:39 | 218037.744 | 160675.568 | 132490.78 | 0 | 644758.562 | 0 | 5368.383 | 0 | 0 | 0 | 0 | 0 | 7768.528 | 0 | 0
December | 999766000000 | 1059802.861 | 15-DEC-16:10 | 218037.744 | 142877.04 | 132054.254 | 0 | 556786.237 | 0 | 4823.714 | 0 | 0 | 0 | 0 | 0 | 5223.872 | 0 | 0
Annual Sum or Average | 14551700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 977419000000 | 1059802.861 |  | 121132.08 | 90545.984 | 132033.319 | 0 | 548390.502 | 0 | 4823.714 | 0 | 0 | 0 | 0 | 0 | 4971.453 | 0 | 0
Maximum of Months | 1466280000000 | 1478506.699 |  | 218037.744 | 161697.68 | 133968.41 | 0 | 966699.731 | 0 | 6910.119 | 0 | 0 | 0 | 0 | 0 | 7768.528 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 361256.59 | 10141.6 | 0 | 371398.19
Cost per Total Building Area ($/m2) | 18.44 | 0.52 | 0 | 18.96
Cost per Net Conditioned Building Area ($/m2) | 18.44 | 0.52 | 0 | 18.96

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16447.23 | 839.49 | 839.49
Net Site Energy | 16447.23 | 839.49 | 839.49
Total Source Energy | 3342.37 | 170.6 | 170.6
Net Source Energy | 3342.37 | 170.6 | 170.6
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2266.04 | 0 | 0 | 0 | 0
Cooling | 5143.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.69 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1886.72 | 0 | 0 | 0 | 0 | 0
Pumps | 52.96 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 250.28 | 0 | 0 | 0 | 2677.86
Refrigeration | 164.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13386.45 | 3060.78 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 25.2 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 25.2 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 21 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 21 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 21 | 21 | 6.49 | 0.61 | 0.61 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 21 | 21 | 6.49 | 0.61 | 0.61 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 53.2 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 19.6 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 53.2 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 19.6 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 33.6 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 72.8 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 33.6 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 72.8 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 53.2 | 53.2 | 6.49 | 0.61 | 0.61 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 53.2 | 53.2 | 6.49 | 0.61 | 0.61 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 49.41 | 49.41 | 6.49 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 33.6 | 33.6 | 6.49 | 0.61 | 0.61 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 36.4 | 36.4 | 6.49 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 33.6 | 33.6 | 6.49 | 0.61 | 0.61 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 6.49 | 0.379 | 0.384
North Total or Average |  |  | 753.18 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 1469.82 | 6.49 | 0.26 | 0.269
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1702456.89 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2571538.71 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 402401.83 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 402093.68 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 422242.48 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 475718.91 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 636118.35 | 430068.94 | 206049.41 | 0.68 | 3.26
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 291638.62 | 223146.27 | 68492.35 | 0.77 | 3.61
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 363196.87 | 245551.31 | 117645.56 | 0.68 | 3.26
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 117670.81 | 79555.26 | 38115.55 | 0.68 | 3.51
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 146054.57 | 98745.04 | 47309.53 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 392780.24 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 215629.08 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 224261.03 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 72657.5 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 90183.45 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 25.88 | 58504.26 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 25.84 | 58402.39 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 28.14 | 63594.5 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 38.04 | 85976.47 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 25.62 | 42845.38 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.01 | 26954.26 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.63 | 24620.74 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.74 | 8889.57 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.88 | 11033.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14288.71 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15600.66 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 249132.373 | 312.0645 | 1204.1401 | 0 | 0.0035 | 410683.4637 | 97299.4587
February | 217857.5412 | 272.3575 | 1045.5276 | 0 | 0.003 | 356584.4451 | 85016.3986
March | 244531.7728 | 315.3832 | 1309.0951 | 0 | 0.0037 | 446525.5695 | 96673.2735
April | 239373.7101 | 312.3688 | 1332.4353 | 0 | 0.0038 | 454503.5215 | 95103.0326
May | 310822.4974 | 406.9409 | 1748.8498 | 0 | 0.0049 | 596551.4554 | 123661.7545
June | 350946.5119 | 459.9687 | 1981.5521 | 0 | 0.0056 | 675930.8934 | 139689.1314
July | 306411.8013 | 401.6686 | 1731.0685 | 0 | 0.0049 | 590488.2833 | 121971.6965
August | 311034.0217 | 407.5116 | 1754.1534 | 0 | 0.0049 | 598361.8796 | 123783.7686
September | 298442.6956 | 390.9985 | 1682.9156 | 0 | 0.0047 | 574061.7769 | 118770.6564
October | 271948.1551 | 355.3242 | 1520.0259 | 0 | 0.0043 | 518494.0353 | 108102.5473
November | 237057.2513 | 307.02 | 1286.9648 | 0 | 0.0036 | 438982.9184 | 93882.8914
December | 234258.1949 | 294.0679 | 1141.1401 | 0 | 0.0033 | 389199.9221 | 91572.1352
Annual Sum or Average | 3271820 | 4235.6744 | 17737.8685 | 0 | 0.0502 | 6050370 | 1295530
Minimum of Months | 217857.5412 | 272.3575 | 1045.5276 | 0 | 0.003 | 356584.4451 | 85016.3986
Maximum of Months | 350946.5119 | 459.9687 | 1981.5521 | 0 | 0.0056 | 675930.8934 | 139689.1314
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 908638000000 | 1014857.412 | 03-JAN-12:39 | 218037.744 | 161697.68 | 137806.039 | 0 | 487350.888 | 0 | 4739.451 | 0 | 0 | 0 | 0 | 0 | 5225.61 | 0 | 0
February | 788944000000 | 942021.696 | 23-FEB-16:10 | 218037.744 | 142955.664 | 137806.039 | 0 | 434522.943 | 0 | 3484.971 | 0 | 0 | 0 | 0 | 0 | 5214.334 | 0 | 0
March | 987939000000 | 1006973.418 | 29-MAR-11:00 | 218037.744 | 161697.68 | 137806.039 | 0 | 479812.496 | 0 | 4396.391 | 0 | 0 | 0 | 0 | 0 | 5223.067 | 0 | 0
April | 1005590000000 | 1100757.586 | 17-APR-15:00 | 218037.744 | 142955.664 | 137833.177 | 0 | 592163.476 | 0 | 4547.413 | 0 | 0 | 0 | 0 | 0 | 5220.112 | 0 | 0
May | 1319870000000 | 1406481.225 | 18-MAY-14:09 | 218037.744 | 147825.664 | 138876.235 | 0 | 890293.889 | 0 | 6222.851 | 0 | 0 | 0 | 0 | 0 | 5224.841 | 0 | 0
June | 1495500000000 | 1402860.864 | 13-JUN-15:09 | 218037.744 | 142955.664 | 138573.766 | 0 | 892531.714 | 0 | 5539.914 | 0 | 0 | 0 | 0 | 0 | 5222.062 | 0 | 0
July | 1306460000000 | 1388049.952 | 18-JUL-11:00 | 121132.08 | 96547.328 | 137806.039 | 0 | 1020712.287 | 0 | 6878.177 | 0 | 0 | 0 | 0 | 0 | 4974.04 | 0 | 0
August | 1323880000000 | 1274168.609 | 31-AUG-10:00 | 121132.08 | 96547.328 | 137806.039 | 0 | 907476.693 | 0 | 6234.121 | 0 | 0 | 0 | 0 | 0 | 4972.347 | 0 | 0
September | 1270110000000 | 1478135.117 | 15-SEP-14:39 | 218037.744 | 146803.552 | 137821.123 | 0 | 963685.099 | 0 | 6560.512 | 0 | 0 | 0 | 0 | 0 | 5227.087 | 0 | 0
October | 1147170000000 | 1217006.758 | 30-OCT-12:00 | 218037.744 | 160675.568 | 137923.119 | 0 | 689275.316 | 0 | 5869.526 | 0 | 0 | 0 | 0 | 0 | 5225.486 | 0 | 0
November | 971251000000 | 1087001.174 | 27-NOV-16:00 | 218037.744 | 142877.04 | 137806.039 | 0 | 577825.432 | 0 | 5229.333 | 0 | 0 | 0 | 0 | 0 | 5225.586 | 0 | 0
December | 861106000000 | 990671.7 | 19-DEC-14:00 | 218037.744 | 154674.224 | 137806.039 | 0 | 470535.873 | 0 | 4395.155 | 0 | 0 | 0 | 0 | 0 | 5222.665 | 0 | 0
Annual Sum or Average | 13386500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 788944000000 | 942021.696 |  | 121132.08 | 96547.328 | 137806.039 | 0 | 434522.943 | 0 | 3484.971 | 0 | 0 | 0 | 0 | 0 | 4972.347 | 0 | 0
Maximum of Months | 1495500000000 | 1478135.117 |  | 218037.744 | 161697.68 | 138876.235 | 0 | 1020712.287 | 0 | 6878.177 | 0 | 0 | 0 | 0 | 0 | 5227.087 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 435007.01 | 24752.68 | 0 | 459759.69
Cost per Total Building Area ($/m2) | 22.2 | 1.26 | 0 | 23.47
Cost per Net Conditioned Building Area ($/m2) | 22.2 | 1.26 | 0 | 23.47

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16363.64 | 835.22 | 835.22
Net Site Energy | 16363.64 | 835.22 | 835.22
Total Source Energy | 46546.84 | 2375.81 | 2375.81
Net Source Energy | 46546.84 | 2375.81 | 2375.81
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1752 | 0 | 0 | 0 | 0
Cooling | 5472.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.62 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2023.88 | 0 | 0 | 0 | 0 | 0
Pumps | 49.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 219.89 | 0 | 0 | 0 | 2677.86
Refrigeration | 162.88 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13847.29 | 2516.35 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 15.4 | 15.4 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 74.2 | 74.2 | 6.49 | 0.25 | 0.25 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 7 | 7 | 6.49 | 0.25 | 0.25 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 25.2 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 25.2 | 25.2 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_WEST | 23.8 | 23.8 | 6.49 | 0.25 | 0.25 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 21 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 21 | 21 | 6.49 | 0.25 | 0.25 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 21 | 21 | 6.49 | 0.61 | 0.61 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 4.2 | 4.2 | 6.49 | 0.25 | 0.25 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 21 | 21 | 6.49 | 0.61 | 0.61 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 53.2 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 19.6 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 53.2 | 53.2 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 19.6 | 19.6 | 6.49 | 0.25 | 0.25 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 33.6 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 72.8 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25 | 33.6 | 33.6 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 72.8 | 72.8 | 6.49 | 0.25 | 0.25 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 53.2 | 53.2 | 6.49 | 0.61 | 0.61 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 53.2 | 53.2 | 6.49 | 0.61 | 0.61 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 12.6 | 12.6 | 6.49 | 0.25 | 0.25 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 49.41 | 49.41 | 6.49 | 0.25 | 0.25 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 33.6 | 33.6 | 6.49 | 0.61 | 0.61 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.25_VT_0.25_EAST | 36.4 | 36.4 | 6.49 | 0.25 | 0.25 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 33.6 | 33.6 | 6.49 | 0.61 | 0.61 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 6.49 | 0.379 | 0.384
North Total or Average |  |  | 753.18 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 1469.82 | 6.49 | 0.26 | 0.269
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3148580.88 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2654418.11 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 700711.68 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 699959.21 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 748594.06 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 939208.42 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 651303.11 | 440335.1 | 210968.01 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 299953.43 | 239559.38 | 60394.05 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 292244.53 | 221197.74 | 71046.79 | 0.76 | 3.57
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 104653.42 | 74687.23 | 29966.2 | 0.71 | 3.68
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 135647.72 | 95689.36 | 39958.36 | 0.71 | 3.64
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 339297.3 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 198816.53 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 202443.87 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 62878.96 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 79126.26 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 30.1 | 68021.34 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 30.06 | 67937.37 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 32.43 | 73289.41 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 42.99 | 96656.06 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 26.23 | 43635.05 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 18.12 | 30502.82 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.65 | 26343.07 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.86 | 9118.43 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.12 | 11474.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14749.23 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28852.39 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 186490.5814 | 293.1373 | 896.7407 | 0 | 0.0025 | 6623110 | 77069.4241
February | 169841.965 | 269.6035 | 835.7511 | 0 | 0.0023 | 6172800 | 70455.696
March | 216760.8503 | 357.2357 | 1161.7857 | 0 | 0.0032 | 8581610 | 91249.2795
April | 214905.3756 | 359.1604 | 1187.8853 | 0 | 0.0032 | 8774650 | 90972.0366
May | 268824.846 | 451.587 | 1502.6619 | 0 | 0.0041 | 11100000 | 114030.7706
June | 322685.8906 | 543.0452 | 1810.8161 | 0 | 0.0049 | 13376300 | 136976.7127
July | 285079.4852 | 479.8705 | 1600.5965 | 0 | 0.0043 | 11823400 | 121024.606
August | 289197.9374 | 486.6504 | 1622.6154 | 0 | 0.0044 | 11986100 | 122757.5709
September | 284696.193 | 478.8603 | 1595.8036 | 0 | 0.0043 | 11788000 | 120824.9716
October | 236505.4886 | 395.7478 | 1310.8111 | 0 | 0.0036 | 9682700 | 100164.9924
November | 197783.2015 | 324.9896 | 1053.0548 | 0 | 0.0029 | 7778410 | 83162.2417
December | 189015.9166 | 294.438 | 889.5775 | 0 | 0.0025 | 6570050 | 77843.1737
Annual Sum or Average | 2861790 | 4734.3257 | 15468.0997 | 0 | 0.0422 | 114257000 | 1206530
Minimum of Months | 169841.965 | 269.6035 | 835.7511 | 0 | 0.0023 | 6172800 | 70455.696
Maximum of Months | 322685.8906 | 543.0452 | 1810.8161 | 0 | 0.0049 | 13376300 | 136976.7127
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 802682000000 | 892074.51 | 26-JAN-16:10 | 218037.744 | 142955.664 | 147930.427 | 0 | 375511.229 | 0 | 2775.095 | 0 | 0 | 0 | 0 | 0 | 4864.351 | 0 | 0
February | 748108000000 | 968522.192 | 28-FEB-16:10 | 218037.744 | 142955.664 | 147930.427 | 0 | 451380.95 | 0 | 3012.979 | 0 | 0 | 0 | 0 | 0 | 5204.428 | 0 | 0
March | 1040040000000 | 1144506.745 | 17-MAR-15:00 | 218037.744 | 142955.664 | 147930.427 | 0 | 627181.77 | 0 | 3519.794 | 0 | 0 | 0 | 0 | 0 | 4881.346 | 0 | 0
April | 1063440000000 | 1182593.163 | 26-APR-15:09 | 218037.744 | 142955.664 | 147930.427 | 0 | 665153.01 | 0 | 3632.529 | 0 | 0 | 0 | 0 | 0 | 4883.789 | 0 | 0
May | 1345250000000 | 1333603.48 | 30-MAY-15:00 | 218037.744 | 142955.664 | 148332.279 | 0 | 815195.291 | 0 | 4186.269 | 0 | 0 | 0 | 0 | 0 | 4896.234 | 0 | 0
June | 1621130000000 | 1574642.437 | 28-JUN-15:39 | 218037.744 | 142955.664 | 151376.191 | 0 | 1044726.995 | 0 | 12619.497 | 0 | 0 | 0 | 0 | 0 | 4926.346 | 0 | 0
July | 1432930000000 | 1340751.533 | 11-JUL-15:00 | 121132.08 | 77805.312 | 148017.445 | 0 | 982165.049 | 0 | 6667.336 | 0 | 0 | 0 | 0 | 0 | 4964.312 | 0 | 0
August | 1452640000000 | 1334342.978 | 01-AUG-15:00 | 121132.08 | 77805.312 | 148018.794 | 0 | 975040.282 | 0 | 7387.768 | 0 | 0 | 0 | 0 | 0 | 4958.742 | 0 | 0
September | 1428640000000 | 1412468.35 | 08-SEP-15:00 | 218037.744 | 142877.04 | 148840.28 | 0 | 891598.474 | 0 | 6137.864 | 0 | 0 | 0 | 0 | 0 | 4976.949 | 0 | 0
October | 1173490000000 | 1191382.404 | 02-OCT-15:00 | 218037.744 | 142877.04 | 148031.66 | 0 | 673530.815 | 0 | 3699.162 | 0 | 0 | 0 | 0 | 0 | 5205.982 | 0 | 0
November | 942698000000 | 1075926.731 | 13-NOV-16:10 | 218037.744 | 142877.04 | 147930.427 | 0 | 558506.349 | 0 | 3368.774 | 0 | 0 | 0 | 0 | 0 | 5206.397 | 0 | 0
December | 796251000000 | 873672.317 | 11-DEC-16:10 | 218037.744 | 142877.04 | 147930.427 | 0 | 356886.181 | 0 | 2738.213 | 0 | 0 | 0 | 0 | 0 | 5202.711 | 0 | 0
Annual Sum or Average | 13847300000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 748108000000 | 873672.317 |  | 121132.08 | 77805.312 | 147930.427 | 0 | 356886.181 | 0 | 2738.213 | 0 | 0 | 0 | 0 | 0 | 4864.351 | 0 | 0
Maximum of Months | 1621130000000 | 1574642.437 |  | 218037.744 | 142955.664 | 151376.191 | 0 | 1044726.995 | 0 | 12619.497 | 0 | 0 | 0 | 0 | 0 | 5206.397 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 330677.67 | 20851.99 | 0 | 351529.66
Cost per Total Building Area ($/m2) | 16.88 | 1.06 | 0 | 17.94
Cost per Net Conditioned Building Area ($/m2) | 16.88 | 1.06 | 0 | 17.94

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16145.08 | 824.07 | 824.07
Net Site Energy | 16145.08 | 824.07 | 824.07
Total Source Energy | 43278.22 | 2208.97 | 2208.97
Net Source Energy | 43278.22 | 2208.97 | 2208.97
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4002.67 | 0 | 0 | 0 | 0
Cooling | 3089.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1858.07 | 0 | 0 | 0 | 0 | 0
Pumps | 38.07 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 309.32 | 0 | 0 | 0 | 2677.86
Refrigeration | 163.7 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11288.64 | 4856.45 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 25.2 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 25.2 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 21 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 21 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 21 | 21 | 3.18 | 0.402 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 21 | 21 | 3.18 | 0.402 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 53.2 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 19.6 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 53.2 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 19.6 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 33.6 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 72.8 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 33.6 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 72.8 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.402 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.402 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 49.41 | 49.41 | 3.18 | 0.262 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.402 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 36.4 | 36.4 | 3.18 | 0.262 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.402 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.38 | 0.315 | 0.43
North Total or Average |  |  | 753.18 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.48 | 0.271 | 0.331
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1541815.63 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2498006.87 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 362604.5 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 361956.39 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 381776.64 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 435478.1 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 640228.16 | 432847.52 | 207380.64 | 0.68 | 3.25
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 266422.2 | 209339.32 | 57082.88 | 0.79 | 3.7
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 348177.17 | 235396.74 | 112780.43 | 0.68 | 3.26
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 120645.19 | 81566.19 | 39079 | 0.68 | 3.51
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 140033.53 | 94674.32 | 45359.21 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 426446.16 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 226687.79 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 231915.47 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 80359.91 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 93274.18 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.46 | 55289.79 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.36 | 55054.73 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 26.72 | 60385.43 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 36.57 | 82663.16 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 25.78 | 42893.07 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.53 | 26141.43 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.02 | 23602.57 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.86 | 9114.27 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.64 | 10578.99 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13880.13 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14128.61 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 221795.8865 | 360.9839 | 783.6203 | 0 | 0.003 | 1393300 | 91508.9721
February | 190037.2265 | 316.1377 | 704.9575 | 0 | 0.0027 | 1253530 | 79037.8552
March | 192585.4272 | 348.5599 | 852.566 | 0 | 0.0032 | 1516340 | 82700.4617
April | 181498.7869 | 341.0101 | 864.8397 | 0 | 0.0032 | 1538290 | 79095.4877
May | 210378.5939 | 401.0865 | 1030.9595 | 0 | 0.0038 | 1833830 | 92218.1147
June | 238700.9655 | 457.3285 | 1180.7602 | 0 | 0.0043 | 2100310 | 104840.4136
July | 204218.195 | 391.3062 | 1010.4001 | 0 | 0.0037 | 1797280 | 89699.1621
August | 213243.4073 | 408.3737 | 1053.9467 | 0 | 0.0039 | 1874730 | 93642.4682
September | 219877.7407 | 421.0579 | 1086.6338 | 0 | 0.004 | 1932880 | 96553.8935
October | 187837.0975 | 352.7886 | 894.403 | 0 | 0.0033 | 1590880 | 81845.6324
November | 183429.6211 | 326.2177 | 783.743 | 0 | 0.0029 | 1393870 | 78235.7717
December | 201671.5241 | 338.0988 | 760.8945 | 0 | 0.0029 | 1353020 | 84117.388
Annual Sum or Average | 2445270 | 4462.9494 | 11007.7242 | 0 | 0.0407 | 19578300 | 1053500
Minimum of Months | 181498.7869 | 316.1377 | 704.9575 | 0 | 0.0027 | 1253530 | 78235.7717
Maximum of Months | 238700.9655 | 457.3285 | 1180.7602 | 0 | 0.0043 | 2100310 | 104840.4136
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 803366000000 | 674698.147 | 23-JAN-16:30 | 218037.744 | 142955.664 | 134666.107 | 0 | 170777.212 | 0 | 3050.358 | 0 | 0 | 0 | 0 | 0 | 5211.062 | 0 | 0
February | 722771000000 | 678638.358 | 21-FEB-13:00 | 218037.744 | 155696.336 | 134666.107 | 0 | 162382.497 | 0 | 2633.936 | 0 | 0 | 0 | 0 | 0 | 5221.739 | 0 | 0
March | 874306000000 | 806742.018 | 28-MAR-15:20 | 218037.744 | 142955.664 | 134666.107 | 0 | 301829.652 | 0 | 4043.018 | 0 | 0 | 0 | 0 | 0 | 5209.834 | 0 | 0
April | 886966000000 | 952214.959 | 13-APR-15:09 | 218037.744 | 142955.664 | 134666.107 | 0 | 447599.583 | 0 | 3737.464 | 0 | 0 | 0 | 0 | 0 | 5218.396 | 0 | 0
May | 1057370000000 | 1120308.683 | 15-MAY-14:00 | 218037.744 | 147825.664 | 137387.67 | 0 | 606833.651 | 0 | 5004.58 | 0 | 0 | 0 | 0 | 0 | 5219.373 | 0 | 0
June | 1211020000000 | 1244285.87 | 19-JUN-15:09 | 218037.744 | 142955.664 | 136643.167 | 0 | 736545.05 | 0 | 4885.52 | 0 | 0 | 0 | 0 | 0 | 5218.725 | 0 | 0
July | 1036290000000 | 1223389 | 03-JUL-11:00 | 121132.08 | 96547.328 | 134861.297 | 0 | 859973.31 | 0 | 5904.106 | 0 | 0 | 0 | 0 | 0 | 4970.878 | 0 | 0
August | 1080950000000 | 1124225.184 | 17-AUG-14:00 | 121132.08 | 82675.312 | 134666.107 | 0 | 775264.681 | 0 | 5516.802 | 0 | 0 | 0 | 0 | 0 | 4970.202 | 0 | 0
September | 1114480000000 | 1176375.579 | 11-SEP-13:00 | 218037.744 | 154674.224 | 136167.981 | 0 | 656916.298 | 0 | 5356.894 | 0 | 0 | 0 | 0 | 0 | 5222.438 | 0 | 0
October | 917285000000 | 1044105.367 | 12-OCT-15:00 | 218037.744 | 142877.04 | 134685.509 | 0 | 539686.645 | 0 | 3603.412 | 0 | 0 | 0 | 0 | 0 | 5215.017 | 0 | 0
November | 803695000000 | 732175.875 | 22-NOV-16:10 | 218037.744 | 142877.04 | 134666.107 | 0 | 228854.4 | 0 | 2524.635 | 0 | 0 | 0 | 0 | 0 | 5215.949 | 0 | 0
December | 780140000000 | 702194.329 | 26-DEC-13:00 | 218037.744 | 154674.224 | 134666.107 | 0 | 186428.033 | 0 | 3163.875 | 0 | 0 | 0 | 0 | 0 | 5224.345 | 0 | 0
Annual Sum or Average | 11288600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 722771000000 | 674698.147 |  | 121132.08 | 82675.312 | 134666.107 | 0 | 162382.497 | 0 | 2524.635 | 0 | 0 | 0 | 0 | 0 | 4970.202 | 0 | 0
Maximum of Months | 1211020000000 | 1244285.87 |  | 218037.744 | 155696.336 | 137387.67 | 0 | 859973.31 | 0 | 5904.106 | 0 | 0 | 0 | 0 | 0 | 5224.345 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 321437.38 | 47175.78 | 0 | 368613.16
Cost per Total Building Area ($/m2) | 16.41 | 2.41 | 0 | 18.81
Cost per Net Conditioned Building Area ($/m2) | 16.41 | 2.41 | 0 | 18.81

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11220.39 | 572.7 | 572.7
Net Site Energy | 11220.39 | 572.7 | 572.7
Total Source Energy | 31229.97 | 1594.02 | 1594.02
Net Source Energy | 31229.97 | 1594.02 | 1594.02
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 912.14 | 0 | 0 | 0 | 0
Cooling | 1550.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1593.1 | 0 | 0 | 0 | 0 | 0
Pumps | 27.52 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 289.35 | 0 | 0 | 0 | 2677.86
Refrigeration | 164.4 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9474.44 | 1745.95 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 25.2 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 25.2 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 21 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 21 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 21 | 21 | 3.18 | 0.402 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 21 | 21 | 3.18 | 0.402 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 53.2 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 19.6 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 53.2 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 19.6 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 33.6 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 72.8 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 33.6 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 72.8 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.402 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.402 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 49.41 | 49.41 | 3.18 | 0.262 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.402 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 36.4 | 36.4 | 3.18 | 0.262 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.402 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.38 | 0.315 | 0.43
North Total or Average |  |  | 753.18 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.48 | 0.271 | 0.331
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1545670.23 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2058064.98 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 503354.34 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 500923.09 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 243340.06 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 298052.73 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 398473.06 | 314606.03 | 83867.03 | 0.79 | 3.71
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 226710.31 | 181063.39 | 45646.93 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 197272.47 | 157552.7 | 39719.77 | 0.8 | 3.95
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76126.04 | 60798.46 | 15327.58 | 0.8 | 4.18
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 82120.1 | 65585.65 | 16534.45 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 283565.58 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 159110.18 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 143958.58 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 55552.59 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 59926.72 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 21.73 | 49315.2 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 21.61 | 49046.25 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.03 | 54306.6 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 32.68 | 73853.37 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 23.47 | 39262.3 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.7 | 23054.59 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.92 | 20191.27 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.6 | 8627.25 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.96 | 9306.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11435.6 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14163.93 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 79864.2114 | 69.0969 | 610.4316 | 0 | 0.0003 | 3682800 | 29503.5404
February | 70116.739 | 60.6468 | 538.9291 | 0 | 0.0003 | 3251430 | 25911.7728
March | 80870.1127 | 69.8062 | 646.927 | 0 | 0.0003 | 3903100 | 29963.0306
April | 72488.6036 | 62.4025 | 610.0982 | 0 | 0.0003 | 3681020 | 26949.8131
May | 79430.1093 | 68.268 | 688.2258 | 0 | 0.0003 | 4152470 | 29590.6442
June | 79537.8381 | 68.294 | 701.0717 | 0 | 0.0003 | 4230020 | 29667.1215
July | 64031.0306 | 54.997 | 561.2325 | 0 | 0.0003 | 3386270 | 23873.5456
August | 72255.1304 | 62.0389 | 637.2199 | 0 | 0.0003 | 3844760 | 26951.7548
September | 79540.7206 | 68.2603 | 707.565 | 0 | 0.0003 | 4269220 | 29687.9298
October | 79935.5656 | 68.6485 | 702.2493 | 0 | 0.0003 | 4237120 | 29808.3684
November | 77313.4779 | 66.5771 | 646.9296 | 0 | 0.0003 | 3903220 | 28732.0814
December | 76730.0595 | 66.2662 | 607.7794 | 0 | 0.0003 | 3666890 | 28410.7134
Annual Sum or Average | 912113.5985 | 785.3025 | 7658.6591 | 0 | 0.0036 | 46208300 | 339050.3161
Minimum of Months | 64031.0306 | 54.997 | 538.9291 | 0 | 0.0003 | 3251430 | 23873.5456
Maximum of Months | 80870.1127 | 69.8062 | 707.565 | 0 | 0.0003 | 4269220 | 29963.0306
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 755112000000 | 808090.298 | 26-JAN-12:00 | 218037.744 | 161697.68 | 120464.337 | 0 | 300455.005 | 0 | 2226.835 | 0 | 0 | 0 | 0 | 0 | 5208.697 | 0 | 0
February | 666665000000 | 782142.246 | 13-FEB-11:00 | 218037.744 | 161697.68 | 120464.337 | 0 | 274564.335 | 0 | 2165.408 | 0 | 0 | 0 | 0 | 0 | 5212.741 | 0 | 0
March | 800282000000 | 758750.31 | 30-MAR-11:00 | 218037.744 | 161697.68 | 120464.337 | 0 | 251278.149 | 0 | 2068.471 | 0 | 0 | 0 | 0 | 0 | 5203.929 | 0 | 0
April | 754747000000 | 858009.431 | 11-APR-15:00 | 218037.744 | 142955.664 | 120464.337 | 0 | 368995.872 | 0 | 2340.755 | 0 | 0 | 0 | 0 | 0 | 5215.059 | 0 | 0
May | 851413000000 | 850624.956 | 30-MAY-09:09 | 218037.744 | 161697.68 | 120503.195 | 0 | 341331.22 | 0 | 3831.625 | 0 | 0 | 0 | 0 | 0 | 5223.492 | 0 | 0
June | 867313000000 | 814230.559 | 28-JUN-12:00 | 218037.744 | 155696.336 | 120464.337 | 0 | 311237.689 | 0 | 3572.206 | 0 | 0 | 0 | 0 | 0 | 5222.247 | 0 | 0
July | 694312000000 | 674447.179 | 10-JUL-09:00 | 121132.08 | 96547.328 | 120464.337 | 0 | 327478.965 | 0 | 3855.139 | 0 | 0 | 0 | 0 | 0 | 4969.329 | 0 | 0
August | 788321000000 | 798713.436 | 08-AUG-09:00 | 121132.08 | 96547.328 | 120464.337 | 0 | 450902.384 | 0 | 4696.231 | 0 | 0 | 0 | 0 | 0 | 4971.076 | 0 | 0
September | 875351000000 | 950591.948 | 25-SEP-11:00 | 218037.744 | 160675.568 | 124242.489 | 0 | 436930.799 | 0 | 5488.924 | 0 | 0 | 0 | 0 | 0 | 5216.424 | 0 | 0
October | 868768000000 | 887515.06 | 19-OCT-10:00 | 218037.744 | 160675.568 | 120464.337 | 0 | 380698.353 | 0 | 2427.468 | 0 | 0 | 0 | 0 | 0 | 5211.59 | 0 | 0
November | 800308000000 | 813757.753 | 20-NOV-12:00 | 218037.744 | 160675.568 | 120602.993 | 0 | 304931.858 | 0 | 4293.393 | 0 | 0 | 0 | 0 | 0 | 5216.197 | 0 | 0
December | 751849000000 | 819569.368 | 19-DEC-12:00 | 218037.744 | 160675.568 | 120464.337 | 0 | 312915.015 | 0 | 2267.619 | 0 | 0 | 0 | 0 | 0 | 5209.085 | 0 | 0
Annual Sum or Average | 9474440000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 666665000000 | 674447.179 |  | 121132.08 | 96547.328 | 120464.337 | 0 | 251278.149 | 0 | 2068.471 | 0 | 0 | 0 | 0 | 0 | 4969.329 | 0 | 0
Maximum of Months | 875351000000 | 950591.948 |  | 218037.744 | 161697.68 | 124242.489 | 0 | 450902.384 | 0 | 5488.924 | 0 | 0 | 0 | 0 | 0 | 5223.492 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 163135.26 | 14924.23 | 0 | 178059.49
Cost per Total Building Area ($/m2) | 8.33 | 0.76 | 0 | 9.09
Cost per Net Conditioned Building Area ($/m2) | 8.33 | 0.76 | 0 | 9.09

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15185.6 | 775.09 | 775.09
Net Site Energy | 15185.6 | 775.09 | 775.09
Total Source Energy | 46809.68 | 2389.22 | 2389.22
Net Source Energy | 46809.68 | 2389.22 | 2389.22
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2214.12 | 0 | 0 | 0 | 0
Cooling | 3894.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.19 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1933.43 | 0 | 0 | 0 | 0 | 0
Pumps | 34.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 263.24 | 0 | 0 | 0 | 2677.86
Refrigeration | 162.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12163.79 | 3021.82 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 15.4 | 15.4 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 74.2 | 74.2 | 3.18 | 0.262 | 0.318 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 7 | 7 | 3.18 | 0.262 | 0.318 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.402 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.402 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 25.2 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 25.2 | 25.2 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_WEST | 23.8 | 23.8 | 3.18 | 0.262 | 0.318 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 21 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 21 | 21 | 3.18 | 0.262 | 0.318 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 21 | 21 | 3.18 | 0.402 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 4.2 | 4.2 | 3.18 | 0.262 | 0.318 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 21 | 21 | 3.18 | 0.402 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 53.2 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 19.6 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 53.2 | 53.2 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 19.6 | 19.6 | 3.18 | 0.262 | 0.318 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 33.6 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 72.8 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318 | 33.6 | 33.6 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 72.8 | 72.8 | 3.18 | 0.262 | 0.318 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.36_VT_0.457 | 1.49 | 1.49 | 6.53 | 0.36 | 0.457 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.402 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.402 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 12.6 | 12.6 | 3.18 | 0.262 | 0.318 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 49.41 | 49.41 | 3.18 | 0.262 | 0.318 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.402 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.25_VT_0.318_EAST | 36.4 | 36.4 | 3.18 | 0.262 | 0.318 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.402 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.38 | 0.315 | 0.43
North Total or Average |  |  | 753.18 | 3.18 | 0.402 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.48 | 0.271 | 0.331
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2776981.54 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2481591.17 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 582334.58 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 580477.29 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 628976.71 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 798285.02 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 565768.19 | 403113.26 | 162654.93 | 0.71 | 3.38
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 278836.01 | 222693.84 | 56142.16 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 244280.03 | 195095.53 | 49184.5 | 0.8 | 3.76
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87868.97 | 67391.38 | 20477.59 | 0.77 | 3.98
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 110369.26 | 82461.78 | 27907.48 | 0.75 | 3.86
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 365970.55 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 202341.12 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 206370.98 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 67831.91 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 80177.7 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 27.5 | 62157.87 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 27.4 | 61928.32 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 29.92 | 67623.51 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 40.2 | 90385.71 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 26.17 | 43537.65 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.84 | 28355.35 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.76 | 24841.29 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.85 | 9099.4 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.73 | 10755.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13788.92 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25447.19 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 211682.295 | 316.181 | 1166.6134 | 0 | 0.0023 | 5817140 | 86155.3347
February | 173485.8577 | 270.9623 | 1067.3355 | 0 | 0.002 | 5322620 | 71839.238
March | 206972.9356 | 325.0926 | 1290.5386 | 0 | 0.0025 | 6435770 | 85895.9808
April | 210408.1042 | 340.7687 | 1408.5872 | 0 | 0.0026 | 7024860 | 88390.1432
May | 262704.2743 | 427.8071 | 1780.6955 | 0 | 0.0033 | 8880710 | 110602.5694
June | 319410.2587 | 521.4824 | 2177.5786 | 0 | 0.0041 | 10860100 | 134615.0187
July | 279580.6197 | 456.6364 | 1907.7456 | 0 | 0.0036 | 9514390 | 117847.7303
August | 293120.7052 | 478.6102 | 1998.8123 | 0 | 0.0037 | 9968550 | 123540.4379
September | 279933.1843 | 456.8348 | 1906.6042 | 0 | 0.0036 | 9508680 | 117957.1174
October | 229975.8989 | 373.0185 | 1544.8343 | 0 | 0.0029 | 7704370 | 96668.4088
November | 190443.1921 | 300.3001 | 1198.4752 | 0 | 0.0023 | 5976700 | 79157.6494
December | 198863.1423 | 301.639 | 1139.2528 | 0 | 0.0022 | 5680910 | 81416.578
Annual Sum or Average | 2856580 | 4569.3332 | 18587.0733 | 0 | 0.0351 | 92694800 | 1194090
Minimum of Months | 173485.8577 | 270.9623 | 1067.3355 | 0 | 0.002 | 5322620 | 71839.238
Maximum of Months | 319410.2587 | 521.4824 | 2177.5786 | 0 | 0.0041 | 10860100 | 134615.0187
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 763348000000 | 704298.201 | 18-JAN-14:00 | 218037.744 | 155696.336 | 141396.02 | 0 | 181990.21 | 0 | 2090.41 | 0 | 0 | 0 | 0 | 0 | 5087.482 | 0 | 0
February | 698456000000 | 748344.627 | 08-FEB-16:10 | 218037.744 | 142955.664 | 141396.02 | 0 | 238487.567 | 0 | 2267.4 | 0 | 0 | 0 | 0 | 0 | 5200.232 | 0 | 0
March | 844527000000 | 878736.708 | 31-MAR-15:00 | 218037.744 | 142955.664 | 141396.02 | 0 | 368881.174 | 0 | 2592.686 | 0 | 0 | 0 | 0 | 0 | 4873.42 | 0 | 0
April | 921831000000 | 1105258.187 | 21-APR-15:09 | 218037.744 | 142955.664 | 141517.352 | 0 | 594485.457 | 0 | 3356.049 | 0 | 0 | 0 | 0 | 0 | 4905.921 | 0 | 0
May | 1165360000000 | 1227271.443 | 31-MAY-15:00 | 218037.744 | 142955.664 | 141993.742 | 0 | 715620.161 | 0 | 3790.173 | 0 | 0 | 0 | 0 | 0 | 4873.958 | 0 | 0
June | 1425110000000 | 1414600.179 | 27-JUN-15:00 | 218037.744 | 142955.664 | 146373.449 | 0 | 896630.74 | 0 | 5722.072 | 0 | 0 | 0 | 0 | 0 | 4880.509 | 0 | 0
July | 1248520000000 | 1182057.892 | 24-JUL-15:00 | 121132.08 | 77805.312 | 141768.578 | 0 | 832124.721 | 0 | 4275.702 | 0 | 0 | 0 | 0 | 0 | 4951.499 | 0 | 0
August | 1308110000000 | 1150942.856 | 04-AUG-14:00 | 121132.08 | 82675.312 | 141396.02 | 0 | 794400.044 | 0 | 6492.906 | 0 | 0 | 0 | 0 | 0 | 4846.494 | 0 | 0
September | 1247770000000 | 1231543.699 | 20-SEP-15:00 | 218037.744 | 142877.04 | 142777.109 | 0 | 719010.875 | 0 | 3975.916 | 0 | 0 | 0 | 0 | 0 | 4865.015 | 0 | 0
October | 1011000000000 | 1105803.633 | 03-OCT-15:09 | 218037.744 | 142877.04 | 141899.179 | 0 | 594658.566 | 0 | 3434.85 | 0 | 0 | 0 | 0 | 0 | 4896.255 | 0 | 0
November | 784287000000 | 758496.364 | 10-NOV-16:10 | 218037.744 | 142877.04 | 141396.02 | 0 | 249023.73 | 0 | 2297.621 | 0 | 0 | 0 | 0 | 0 | 4864.209 | 0 | 0
December | 745472000000 | 756568.384 | 05-DEC-14:00 | 218037.744 | 154674.224 | 141396.02 | 0 | 234930.363 | 0 | 2329.352 | 0 | 0 | 0 | 0 | 0 | 5200.681 | 0 | 0
Annual Sum or Average | 12163800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 698456000000 | 704298.201 |  | 121132.08 | 77805.312 | 141396.02 | 0 | 181990.21 | 0 | 2090.41 | 0 | 0 | 0 | 0 | 0 | 4846.494 | 0 | 0
Maximum of Months | 1425110000000 | 1414600.179 |  | 218037.744 | 155696.336 | 146373.449 | 0 | 896630.74 | 0 | 6492.906 | 0 | 0 | 0 | 0 | 0 | 5200.681 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 344946.93 | 23437.94 | 0 | 368384.86
Cost per Total Building Area ($/m2) | 17.61 | 1.2 | 0 | 18.8
Cost per Net Conditioned Building Area ($/m2) | 17.61 | 1.2 | 0 | 18.8

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14835.04 | 757.2 | 757.2
Net Site Energy | 14835.04 | 757.2 | 757.2
Total Source Energy | 35538.61 | 1813.93 | 1813.93
Net Source Energy | 35538.61 | 1813.93 | 1813.93
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4296.47 | 0 | 0 | 0 | 0
Cooling | 918.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2411.11 | 0 | 0 | 0 | 0 | 0
Pumps | 22.62 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 339.22 | 0 | 0 | 0 | 2677.86
Refrigeration | 163.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9654.89 | 5180.16 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 7 | 7 | 6.49 | 0.391 | 0.39 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 7 | 7 | 6.49 | 0.391 | 0.39 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 7 | 7 | 6.49 | 0.391 | 0.39 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 7 | 7 | 6.49 | 0.391 | 0.39 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 15.4 | 15.4 | 6.49 | 0.34 | 0.34 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 74.2 | 74.2 | 6.49 | 0.34 | 0.34 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 7 | 7 | 6.49 | 0.391 | 0.39 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 7 | 7 | 6.49 | 0.391 | 0.39 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 15.4 | 15.4 | 6.49 | 0.61 | 0.61 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 74.2 | 74.2 | 6.49 | 0.61 | 0.61 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 25.2 | 25.2 | 6.49 | 0.391 | 0.39 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 23.8 | 23.8 | 6.49 | 0.391 | 0.39 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 25.2 | 25.2 | 6.49 | 0.391 | 0.39 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39_WEST | 23.8 | 23.8 | 6.49 | 0.391 | 0.39 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 21 | 21 | 6.49 | 0.34 | 0.34 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 21 | 21 | 6.49 | 0.34 | 0.34 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 4.2 | 4.2 | 6.49 | 0.391 | 0.39 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 21 | 21 | 6.49 | 0.61 | 0.61 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 4.2 | 4.2 | 6.49 | 0.391 | 0.39 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 21 | 21 | 6.49 | 0.61 | 0.61 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 53.2 | 53.2 | 6.49 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 19.6 | 19.6 | 6.49 | 0.391 | 0.39 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 53.2 | 53.2 | 6.49 | 0.34 | 0.34 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 19.6 | 19.6 | 6.49 | 0.391 | 0.39 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 33.6 | 33.6 | 6.49 | 0.34 | 0.34 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 72.8 | 72.8 | 6.49 | 0.391 | 0.39 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.34_VT_0.34 | 33.6 | 33.6 | 6.49 | 0.34 | 0.34 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 72.8 | 72.8 | 6.49 | 0.391 | 0.39 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_6.922_SHGC_0.61_VT_0.775 | 1.49 | 1.49 | 6.53 | 0.61 | 0.775 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 53.2 | 53.2 | 6.49 | 0.61 | 0.61 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 53.2 | 53.2 | 6.49 | 0.61 | 0.61 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 12.6 | 12.6 | 6.49 | 0.391 | 0.39 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 49.41 | 49.41 | 6.49 | 0.391 | 0.39 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 33.6 | 33.6 | 6.49 | 0.61 | 0.61 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.39_VT_0.39 | 36.4 | 36.4 | 6.49 | 0.391 | 0.39 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_6.878_SHGC_0.61_VT_0.61 | 33.6 | 33.6 | 6.49 | 0.61 | 0.61 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 6.49 | 0.461 | 0.471
North Total or Average |  |  | 753.18 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 1469.82 | 6.49 | 0.385 | 0.399
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1791846.45 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2819371.25 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 302728.15 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 301505.99 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 315133.37 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 872478.94 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 676743.64 | 540484.87 | 136258.77 | 0.8 | 3.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 274602.41 | 219312.66 | 55289.75 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 342647.12 | 273656.92 | 68990.19 | 0.8 | 3.76
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87108.2 | 69569.42 | 17538.78 | 0.8 | 4.18
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 156034.59 | 124617.85 | 31416.74 | 0.8 | 4.15
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 545867.72 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 194962.78 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 276382.35 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 70262.29 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 125858.95 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 32.42 | 73273.25 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 32.26 | 72914.58 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 34.07 | 77014.91 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 40.34 | 90692.58 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 40.88 | 67726.95 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.59 | 27924.83 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 20.7 | 34844.42 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.26 | 9871.85 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 9.43 | 17415.25 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15665.79 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16419.79 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 111963.124 | 98.0951 | 636.2644 | 0 | 0.0004 | 3837760 | 40691.8431
February | 86115.2745 | 74.9173 | 584.4798 | 0 | 0.0003 | 3525930 | 31587.8663
March | 102108.3312 | 88.9597 | 669.9352 | 0 | 0.0004 | 4041340 | 37383.8111
April | 86639.0745 | 75.1392 | 629.8675 | 0 | 0.0003 | 3799930 | 31907.6302
May | 91787.1128 | 79.3333 | 715.7088 | 0 | 0.0004 | 4318010 | 33951.2733
June | 90503.0564 | 78.1845 | 712.6663 | 0 | 0.0003 | 4299680 | 33497.5768
July | 76973.7483 | 66.8008 | 551.7237 | 0 | 0.0003 | 3328460 | 28324.0311
August | 85828.4448 | 74.5368 | 605.9699 | 0 | 0.0003 | 3655680 | 31554.1593
September | 87663.1994 | 75.5606 | 720.8313 | 0 | 0.0003 | 4349060 | 32539.6086
October | 90096.0099 | 77.8299 | 709.9925 | 0 | 0.0003 | 4283550 | 33348.5396
November | 92647.2962 | 80.466 | 652.7678 | 0 | 0.0003 | 3937990 | 34056.9539
December | 104350.651 | 91.3013 | 615.2278 | 0 | 0.0004 | 3711000 | 37992.9715
Annual Sum or Average | 1106680 | 961.1245 | 7805.4351 | 0 | 0.0041 | 47088400 | 406836.2648
Minimum of Months | 76973.7483 | 66.8008 | 551.7237 | 0 | 0.0003 | 3328460 | 28324.0311
Maximum of Months | 111963.124 | 98.0951 | 720.8313 | 0 | 0.0004 | 4349060 | 40691.8431
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 786885000000 | 643950.162 | 27-JAN-14:00 | 218037.744 | 155696.336 | 185327.771 | 0 | 78499.624 | 0 | 1270.542 | 0 | 0 | 0 | 0 | 0 | 5118.145 | 0 | 0
February | 722948000000 | 763388.441 | 14-FEB-12:00 | 218037.744 | 161697.68 | 185327.771 | 0 | 190738.761 | 0 | 2377.581 | 0 | 0 | 0 | 0 | 0 | 5208.905 | 0 | 0
March | 828627000000 | 719958.032 | 01-MAR-12:00 | 218037.744 | 161697.68 | 185327.771 | 0 | 147187.539 | 0 | 2489.477 | 0 | 0 | 0 | 0 | 0 | 5217.821 | 0 | 0
April | 779128000000 | 783919.321 | 13-APR-15:09 | 218037.744 | 142955.664 | 185327.771 | 0 | 229976.545 | 0 | 2416.993 | 0 | 0 | 0 | 0 | 0 | 5204.605 | 0 | 0
May | 885354000000 | 901001.775 | 17-MAY-13:00 | 218037.744 | 155696.336 | 185327.771 | 0 | 332829.562 | 0 | 3894.4 | 0 | 0 | 0 | 0 | 0 | 5215.962 | 0 | 0
June | 881596000000 | 922621.85 | 15-JUN-12:00 | 218037.744 | 155696.336 | 185327.771 | 0 | 354435.093 | 0 | 3907.254 | 0 | 0 | 0 | 0 | 0 | 5217.653 | 0 | 0
July | 682460000000 | 843534.126 | 03-JUL-12:00 | 121132.08 | 90545.984 | 185327.771 | 0 | 437585.349 | 0 | 3979.31 | 0 | 0 | 0 | 0 | 0 | 4963.632 | 0 | 0
August | 749552000000 | 813282.319 | 15-AUG-11:00 | 121132.08 | 96547.328 | 185327.771 | 0 | 401351.822 | 0 | 3957.917 | 0 | 0 | 0 | 0 | 0 | 4965.402 | 0 | 0
September | 891721000000 | 1159651.133 | 28-SEP-15:09 | 218037.744 | 142877.04 | 185327.771 | 0 | 602548.925 | 0 | 5646.656 | 0 | 0 | 0 | 0 | 0 | 5212.998 | 0 | 0
October | 878289000000 | 866629.262 | 30-OCT-12:00 | 218037.744 | 160675.568 | 185327.771 | 0 | 294821.565 | 0 | 2561.637 | 0 | 0 | 0 | 0 | 0 | 5204.978 | 0 | 0
November | 807437000000 | 736009.419 | 16-NOV-15:00 | 218037.744 | 146803.552 | 185327.771 | 0 | 177353.872 | 0 | 3265.506 | 0 | 0 | 0 | 0 | 0 | 5220.974 | 0 | 0
December | 760893000000 | 657210.363 | 07-DEC-14:00 | 218037.744 | 154674.224 | 185327.771 | 0 | 91781.495 | 0 | 2172.882 | 0 | 0 | 0 | 0 | 0 | 5216.247 | 0 | 0
Annual Sum or Average | 9654890000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 682460000000 | 643950.162 |  | 121132.08 | 90545.984 | 185327.771 | 0 | 78499.624 | 0 | 1270.542 | 0 | 0 | 0 | 0 | 0 | 4963.632 | 0 | 0
Maximum of Months | 891721000000 | 1159651.133 |  | 218037.744 | 161697.68 | 185327.771 | 0 | 602548.925 | 0 | 5646.656 | 0 | 0 | 0 | 0 | 0 | 5220.974 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 423391.05 | 44210.87 | 0 | 467601.92
Cost per Total Building Area ($/m2) | 21.61 | 2.26 | 0 | 23.87
Cost per Net Conditioned Building Area ($/m2) | 21.61 | 2.26 | 0 | 23.87

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19393.94 | 989.89 | 989.89
Net Site Energy | 19393.94 | 989.89 | 989.89
Total Source Energy | 48501.78 | 2475.59 | 2475.59
Net Source Energy | 48501.78 | 2475.59 | 2475.59
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7493.33 | 0 | 0 | 0 | 0
Cooling | 2718.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.16 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1943.67 | 0 | 0 | 0 | 0 | 0
Pumps | 35.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 356.31 | 0 | 0 | 0 | 2677.86
Refrigeration | 163.01 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10999.84 | 8394.1 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 49.41 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 36.4 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.441 | 0.546
North Total or Average |  |  | 753.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.41 | 0.507
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1605187.27 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2748010.56 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 378644.97 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 377127.88 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 397467.87 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 451946.54 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 633843.48 | 428530.94 | 205312.54 | 0.68 | 3.26
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 274537.98 | 219261.2 | 55276.78 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 332269.6 | 224641.9 | 107627.7 | 0.68 | 3.26
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 117525.76 | 79457.19 | 38068.57 | 0.68 | 3.51
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 137034.1 | 92646.45 | 44387.64 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 469976.93 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 257949.69 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 246368.47 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 87142.01 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 101606.89 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 25.81 | 58335.22 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 25.64 | 57948.5 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 27.96 | 63205.28 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 37.74 | 85296.14 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 25.52 | 42692.16 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.58 | 27918.28 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.38 | 22524.21 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.73 | 8878.61 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.52 | 10352.39 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15269.28 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14709.32 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 251936.5997 | 379.7043 | 834.934 | 0 | 0.0036 | 51892.592 | 101004.677
February | 203591.6735 | 317.8851 | 735.6934 | 0 | 0.0031 | 45730.5099 | 82632.3525
March | 189483.4096 | 324.8256 | 844.666 | 0 | 0.0035 | 52518.3895 | 79555.0239
April | 152428.1532 | 283.0697 | 799.6699 | 0 | 0.0033 | 49729.3259 | 65987.5781
May | 170997.3869 | 331.5365 | 974.2928 | 0 | 0.0039 | 60593.3655 | 75304.8844
June | 207294.0158 | 410.067 | 1226.1409 | 0 | 0.0049 | 76258.869 | 92035.2889
July | 178761.3656 | 353.769 | 1058.1714 | 0 | 0.0043 | 65812.18 | 79380.4991
August | 192422.113 | 380.3726 | 1136.6559 | 0 | 0.0046 | 70693.3363 | 85407.2603
September | 172228.7658 | 338.9916 | 1009.2903 | 0 | 0.0041 | 62771.5088 | 76310.5398
October | 169516.6048 | 319.9927 | 917.9687 | 0 | 0.0037 | 57087.7552 | 73859.7588
November | 177795.0634 | 310.726 | 825.3461 | 0 | 0.0034 | 51319.5017 | 75190.5427
December | 219950.1536 | 343.1463 | 793.2561 | 0 | 0.0034 | 49308.4515 | 89246.1504
Annual Sum or Average | 2286410 | 4094.0864 | 11156.0854 | 0 | 0.0458 | 693715.7851 | 975914.5561
Minimum of Months | 152428.1532 | 283.0697 | 735.6934 | 0 | 0.0031 | 45730.5099 | 65987.5781
Maximum of Months | 251936.5997 | 410.067 | 1226.1409 | 0 | 0.0049 | 76258.869 | 101004.677
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 822830000000 | 665151.074 | 09-JAN-11:39 | 218037.744 | 161697.68 | 135682.185 | 0 | 139562.922 | 0 | 2401.533 | 0 | 0 | 0 | 0 | 0 | 7769.01 | 0 | 0
February | 725121000000 | 649704.271 | 15-FEB-14:00 | 218037.744 | 155696.336 | 135682.185 | 0 | 133559.121 | 0 | 1589.415 | 0 | 0 | 0 | 0 | 0 | 5139.469 | 0 | 0
March | 832753000000 | 872458.667 | 09-MAR-16:10 | 218037.744 | 142955.664 | 135682.185 | 0 | 367054.269 | 0 | 3510.121 | 0 | 0 | 0 | 0 | 0 | 5218.683 | 0 | 0
April | 788528000000 | 858967.431 | 04-APR-15:00 | 218037.744 | 142955.664 | 135682.185 | 0 | 353823.89 | 0 | 3250.756 | 0 | 0 | 0 | 0 | 0 | 5217.193 | 0 | 0
May | 960793000000 | 1135930.321 | 31-MAY-15:00 | 218037.744 | 142955.664 | 135682.185 | 0 | 628817.383 | 0 | 5211.901 | 0 | 0 | 0 | 0 | 0 | 5225.444 | 0 | 0
June | 1209190000000 | 1436254.703 | 30-JUN-15:00 | 218037.744 | 142955.664 | 136216.328 | 0 | 928066.324 | 0 | 5753.972 | 0 | 0 | 0 | 0 | 0 | 5224.671 | 0 | 0
July | 1043540000000 | 1339832.776 | 25-JUL-11:00 | 121132.08 | 96547.328 | 135682.185 | 0 | 975302.56 | 0 | 6195.775 | 0 | 0 | 0 | 0 | 0 | 4972.849 | 0 | 0
August | 1120940000000 | 1341339.671 | 09-AUG-14:00 | 121132.08 | 82675.312 | 135682.185 | 0 | 990263.57 | 0 | 6612.312 | 0 | 0 | 0 | 0 | 0 | 4974.213 | 0 | 0
September | 995330000000 | 1118663.27 | 08-SEP-15:09 | 218037.744 | 142877.04 | 136090.783 | 0 | 612609.369 | 0 | 3916.471 | 0 | 0 | 0 | 0 | 0 | 5131.863 | 0 | 0
October | 905207000000 | 982833.368 | 03-OCT-11:00 | 218037.744 | 160675.568 | 135682.185 | 0 | 458865.29 | 0 | 4349.595 | 0 | 0 | 0 | 0 | 0 | 5222.985 | 0 | 0
November | 813743000000 | 851349.66 | 03-NOV-13:00 | 218037.744 | 154674.224 | 135682.185 | 0 | 333964.145 | 0 | 3769.695 | 0 | 0 | 0 | 0 | 0 | 5221.667 | 0 | 0
December | 781855000000 | 586616.043 | 08-DEC-10:00 | 218037.744 | 160675.568 | 135682.185 | 0 | 65879.427 | 0 | 1130.036 | 0 | 0 | 0 | 0 | 0 | 5211.083 | 0 | 0
Annual Sum or Average | 10999800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 725121000000 | 586616.043 |  | 121132.08 | 82675.312 | 135682.185 | 0 | 65879.427 | 0 | 1130.036 | 0 | 0 | 0 | 0 | 0 | 4972.849 | 0 | 0
Maximum of Months | 1209190000000 | 1436254.703 |  | 218037.744 | 161697.68 | 136216.328 | 0 | 990263.57 | 0 | 6612.312 | 0 | 0 | 0 | 0 | 0 | 7769.01 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 244990.27 | 81433.37 | 0 | 326423.63
Cost per Total Building Area ($/m2) | 12.5 | 4.16 | 0 | 16.66
Cost per Net Conditioned Building Area ($/m2) | 12.5 | 4.16 | 0 | 16.66

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15951.34 | 814.18 | 814.18
Net Site Energy | 15951.34 | 814.18 | 814.18
Total Source Energy | 41208.24 | 2103.32 | 2103.32
Net Source Energy | 41208.24 | 2103.32 | 2103.32
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4372.54 | 0 | 0 | 0 | 0
Cooling | 2155.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2202.57 | 0 | 0 | 0 | 0 | 0
Pumps | 28.39 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 347.29 | 0 | 0 | 0 | 2677.86
Refrigeration | 162.11 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10687.05 | 5264.29 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 49.41 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 36.4 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.441 | 0.546
North Total or Average |  |  | 753.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.41 | 0.507
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2469058 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2470985.78 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 444363.95 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 441752.07 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 483355.09 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 632114.78 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 491053.98 | 392182.85 | 98871.14 | 0.8 | 3.74
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 309433.03 | 247130.31 | 62302.71 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 259960.48 | 207618.8 | 52341.68 | 0.8 | 3.76
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91787.62 | 73306.67 | 18480.95 | 0.8 | 4.18
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 105817.34 | 84511.57 | 21305.76 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 433985.17 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 217827.66 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 229748.66 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 81120.34 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 93519.57 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 29.4 | 66440.01 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 29.22 | 66033.36 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 32.03 | 72389.7 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 43.09 | 96870.15 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 29.66 | 49352.46 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 18.69 | 31466.82 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.7 | 26435.87 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.54 | 10402.16 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.39 | 11992.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13729.99 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22625.5 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 271776.8385 | 426.3397 | 973.4937 | 0 | 0.0039 | 1011960 | 111683.7215
February | 226892.925 | 364.4355 | 858.7592 | 0 | 0.0034 | 892764.5357 | 94073.4991
March | 249598.0598 | 410.4136 | 996.1629 | 0 | 0.0039 | 1035680 | 104420.156
April | 220827.1055 | 375.6254 | 949.0998 | 0 | 0.0037 | 986842.7632 | 93611.7978
May | 282266.8344 | 490.5973 | 1269.7961 | 0 | 0.005 | 1320360 | 120683.3232
June | 307538.4528 | 536.3148 | 1393.1916 | 0 | 0.0054 | 1448680 | 131664.1777
July | 263593.3415 | 459.9202 | 1195.4191 | 0 | 0.0047 | 1243040 | 112873.9285
August | 263088.0938 | 458.3357 | 1189.323 | 0 | 0.0046 | 1236690 | 112588.6226
September | 268321.6164 | 467.3759 | 1212.5635 | 0 | 0.0047 | 1260860 | 114820.7281
October | 238303.9709 | 406.4274 | 1030.0271 | 0 | 0.004 | 1071000 | 101125.8404
November | 238294.2291 | 390.1646 | 942.0525 | 0 | 0.0037 | 979412.888 | 99528.128
December | 269424.8103 | 420.7746 | 954.9183 | 0 | 0.0038 | 992639.6939 | 110533.2254
Annual Sum or Average | 3099930 | 5206.7249 | 12964.8069 | 0 | 0.051 | 13479900 | 1307610
Minimum of Months | 220827.1055 | 364.4355 | 858.7592 | 0 | 0.0034 | 892764.5357 | 93611.7978
Maximum of Months | 307538.4528 | 536.3148 | 1393.1916 | 0 | 0.0054 | 1448680 | 131664.1777
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 802298000000 | 622288.498 | 25-JAN-14:00 | 218037.744 | 155696.336 | 156146.85 | 0 | 86040.636 | 0 | 1279.557 | 0 | 0 | 0 | 0 | 0 | 5087.377 | 0 | 0
February | 707794000000 | 746755.789 | 14-FEB-16:10 | 218037.744 | 142955.664 | 156158.362 | 0 | 222254.826 | 0 | 2151.171 | 0 | 0 | 0 | 0 | 0 | 5198.022 | 0 | 0
March | 821101000000 | 767055.734 | 02-MAR-14:00 | 218037.744 | 155696.336 | 156454.834 | 0 | 229495.662 | 0 | 2291.273 | 0 | 0 | 0 | 0 | 0 | 5079.885 | 0 | 0
April | 782381000000 | 923366.833 | 21-APR-15:00 | 218037.744 | 142955.664 | 156281.015 | 0 | 398498.044 | 0 | 2733.103 | 0 | 0 | 0 | 0 | 0 | 4861.263 | 0 | 0
May | 1046800000000 | 1041197.092 | 31-MAY-15:00 | 218037.744 | 142955.664 | 156442.576 | 0 | 515756.725 | 0 | 3121.261 | 0 | 0 | 0 | 0 | 0 | 4883.122 | 0 | 0
June | 1148530000000 | 1162119.043 | 29-JUN-13:00 | 218037.744 | 155696.336 | 158023.067 | 0 | 621442.096 | 0 | 3769.946 | 0 | 0 | 0 | 0 | 0 | 5149.854 | 0 | 0
July | 985493000000 | 990178.83 | 31-JUL-14:00 | 121132.08 | 82675.312 | 156767.028 | 0 | 621080.124 | 0 | 3575.64 | 0 | 0 | 0 | 0 | 0 | 4948.645 | 0 | 0
August | 980464000000 | 972976.336 | 01-AUG-13:00 | 121132.08 | 90545.984 | 156164.876 | 0 | 595553.183 | 0 | 4684.946 | 0 | 0 | 0 | 0 | 0 | 4895.267 | 0 | 0
September | 999623000000 | 1010775.337 | 21-SEP-13:00 | 218037.744 | 154674.224 | 159719.617 | 0 | 469600.271 | 0 | 3588.654 | 0 | 0 | 0 | 0 | 0 | 5154.827 | 0 | 0
October | 849098000000 | 908048.48 | 11-OCT-15:00 | 218037.744 | 142877.04 | 156555.412 | 0 | 380698.266 | 0 | 4964.154 | 0 | 0 | 0 | 0 | 0 | 4915.864 | 0 | 0
November | 776490000000 | 701754.463 | 08-NOV-14:00 | 218037.744 | 154674.224 | 156245.958 | 0 | 165655.164 | 0 | 1938.934 | 0 | 0 | 0 | 0 | 0 | 5202.44 | 0 | 0
December | 786977000000 | 599424.073 | 05-DEC-13:00 | 218037.744 | 154674.224 | 156146.85 | 0 | 64265.835 | 0 | 1096.464 | 0 | 0 | 0 | 0 | 0 | 5202.956 | 0 | 0
Annual Sum or Average | 10687100000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 707794000000 | 599424.073 |  | 121132.08 | 82675.312 | 156146.85 | 0 | 64265.835 | 0 | 1096.464 | 0 | 0 | 0 | 0 | 0 | 4861.263 | 0 | 0
Maximum of Months | 1148530000000 | 1162119.043 |  | 218037.744 | 155696.336 | 159719.617 | 0 | 621442.096 | 0 | 4964.154 | 0 | 0 | 0 | 0 | 0 | 5202.956 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 109817.29 | 36403.48 | 0 | 146220.77
Cost per Total Building Area ($/m2) | 5.61 | 1.86 | 0 | 7.46
Cost per Net Conditioned Building Area ($/m2) | 5.61 | 1.86 | 0 | 7.46

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16104.57 | 822 | 822
Net Site Energy | 16104.57 | 822 | 822
Total Source Energy | 23129.94 | 1180.58 | 1180.58
Net Source Energy | 23129.94 | 1180.58 | 1180.58
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6658.34 | 0 | 0 | 0 | 0
Cooling | 582.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1628.6 | 0 | 0 | 0 | 0 | 0
Pumps | 16.34 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 372.91 | 0 | 0 | 0 | 2677.86
Refrigeration | 163.1 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8528.85 | 7575.71 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13_EXT-WALL | 0.3 | 0.704 | 0.79 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 49.41 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 36.4 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.441 | 0.546
North Total or Average |  |  | 753.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.41 | 0.507
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1072781.7 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2409760.15 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 248314.72 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 246518.3 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 267855.74 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 310092.94 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 422795.1 | 319536.81 | 103258.29 | 0.76 | 3.56
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 241285.44 | 192703.88 | 48581.55 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 183706.74 | 146718.35 | 36988.39 | 0.8 | 3.95
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75812.12 | 60547.75 | 15264.37 | 0.8 | 4.18
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 79330.98 | 62614.89 | 16716.1 | 0.79 | 4.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 359261.34 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 212975.14 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 176712.59 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 72925.78 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 74366.11 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 23.91 | 54040.9 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 23.67 | 53506.91 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 26.18 | 59165.77 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 33.49 | 75704.06 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 22.56 | 37736.48 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.58 | 24536.77 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.1 | 18802.79 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.58 | 8591.68 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.67 | 8761.37 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13389.79 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9830.56 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 107064.3134 | 121.6588 | 156.7139 | 0 | 0.0008 | 2066610 | 39676.3452
February | 77311.8462 | 91.8454 | 138.6701 | 0 | 0.0006 | 1829850 | 29078.3951
March | 85078.5137 | 102.3339 | 160.6573 | 0 | 0.0007 | 2120300 | 32134.7226
April | 61562.6011 | 78.5275 | 144.8486 | 0 | 0.0006 | 1912690 | 23732.3073
May | 51966.4102 | 72.715 | 163.3125 | 0 | 0.0007 | 2157690 | 20721.4445
June | 47347.2538 | 69.4898 | 169.4719 | 0 | 0.0007 | 2239510 | 19226.393
July | 37985.8015 | 55.4155 | 133.8262 | 0 | 0.0005 | 1768430 | 15389.1075
August | 41709.0281 | 60.2898 | 143.3847 | 0 | 0.0006 | 1894670 | 16837.7979
September | 47705.8147 | 68.7427 | 162.6249 | 0 | 0.0007 | 2148880 | 19235.6124
October | 58619.3756 | 77.5435 | 155.6113 | 0 | 0.0007 | 2055320 | 22894.3952
November | 85161.7385 | 100.9605 | 151.4064 | 0 | 0.0007 | 1997870 | 32008.3444
December | 103078.6034 | 117.4066 | 152.6473 | 0 | 0.0007 | 2013070 | 38228.9519
Annual Sum or Average | 804591.3004 | 1016.9292 | 1833.175 | 0 | 0.0079 | 24204900 | 309163.817
Minimum of Months | 37985.8015 | 55.4155 | 133.8262 | 0 | 0.0005 | 1768430 | 15389.1075
Maximum of Months | 107064.3134 | 121.6588 | 169.4719 | 0 | 0.0008 | 2239510 | 39676.3452
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 728193000000 | 510393.884 | 17-JAN-16:00 | 218037.744 | 142955.664 | 119819.969 | 0 | 0 | 23884.224 | 490.552 | 0 | 0 | 0 | 0 | 0 | 5205.731 | 0 | 0
February | 644769000000 | 598517.25 | 21-FEB-13:00 | 218037.744 | 155696.336 | 119819.969 | 0 | 98347.526 | 0 | 1408.604 | 0 | 0 | 0 | 0 | 0 | 5207.071 | 0 | 0
March | 747109000000 | 628252.958 | 29-MAR-15:00 | 218037.744 | 142955.664 | 119819.969 | 0 | 140559.01 | 0 | 1674.811 | 0 | 0 | 0 | 0 | 0 | 5205.761 | 0 | 0
April | 673957000000 | 603651.411 | 14-APR-13:00 | 218037.744 | 155696.336 | 119819.969 | 0 | 103536.866 | 0 | 1443.73 | 0 | 0 | 0 | 0 | 0 | 5116.766 | 0 | 0
May | 760285000000 | 764490.968 | 05-MAY-15:00 | 218037.744 | 142955.664 | 119819.969 | 0 | 275592.113 | 0 | 2868.359 | 0 | 0 | 0 | 0 | 0 | 5217.12 | 0 | 0
June | 789117000000 | 795675.814 | 28-JUN-15:09 | 218037.744 | 142955.664 | 120226.123 | 0 | 305822.645 | 0 | 3418.575 | 0 | 0 | 0 | 0 | 0 | 5215.063 | 0 | 0
July | 623124000000 | 702761.677 | 24-JUL-14:00 | 121132.08 | 82675.312 | 119877.253 | 0 | 370861.7 | 0 | 3252.923 | 0 | 0 | 0 | 0 | 0 | 4962.408 | 0 | 0
August | 667607000000 | 644629.937 | 07-AUG-14:00 | 121132.08 | 82675.312 | 119819.969 | 0 | 312941.476 | 0 | 3098.532 | 0 | 0 | 0 | 0 | 0 | 4962.568 | 0 | 0
September | 757181000000 | 830668.655 | 13-SEP-15:00 | 218037.744 | 142877.04 | 119819.969 | 0 | 341493.094 | 0 | 3224.955 | 0 | 0 | 0 | 0 | 0 | 5215.853 | 0 | 0
October | 724214000000 | 654070.26 | 17-OCT-15:00 | 218037.744 | 142877.04 | 119819.969 | 0 | 166345.392 | 0 | 1782.906 | 0 | 0 | 0 | 0 | 0 | 5207.21 | 0 | 0
November | 703970000000 | 591887.957 | 03-NOV-13:00 | 218037.744 | 154674.224 | 119819.969 | 0 | 92404.174 | 0 | 1730.731 | 0 | 0 | 0 | 0 | 0 | 5221.115 | 0 | 0
December | 709327000000 | 510667.534 | 13-DEC-11:39 | 218037.744 | 160675.568 | 119819.969 | 0 | 3915.145 | 0 | 626.65 | 0 | 0 | 0 | 0 | 0 | 7592.458 | 0 | 0
Annual Sum or Average | 8528850000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 623124000000 | 510393.884 |  | 121132.08 | 82675.312 | 119819.969 | 0 | 0 | 0 | 490.552 | 0 | 0 | 0 | 0 | 0 | 4962.408 | 0 | 0
Maximum of Months | 789117000000 | 830668.655 |  | 218037.744 | 160675.568 | 120226.123 | 0 | 370861.7 | 23884.224 | 3418.575 | 0 | 0 | 0 | 0 | 0 | 7592.458 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 171410.54 | 63725.42 | 0 | 235135.96
Cost per Total Building Area ($/m2) | 8.75 | 3.25 | 0 | 12
Cost per Net Conditioned Building Area ($/m2) | 8.75 | 3.25 | 0 | 12

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 21990.67 | 1122.43 | 1122.43
Net Site Energy | 21990.67 | 1122.43 | 1122.43
Total Source Energy | 48840.01 | 2492.85 | 2492.85
Net Source Energy | 48840.01 | 2492.85 | 2492.85
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10933.27 | 0 | 0 | 0 | 0
Cooling | 1814.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1970.67 | 0 | 0 | 0 | 0 | 0
Pumps | 29.73 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 396.33 | 0 | 0 | 0 | 2677.86
Refrigeration | 162.41 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10116.62 | 11874.05 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 49.41 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 36.4 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.441 | 0.546
North Total or Average |  |  | 753.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.41 | 0.507
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1563313.42 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2849666.45 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 369544.12 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 367953.44 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 388080.22 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 437735.64 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 627970.93 | 424560.61 | 203410.32 | 0.68 | 3.26
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 269224.93 | 212907.39 | 56317.53 | 0.79 | 3.72
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 314954.19 | 212935.24 | 102018.95 | 0.68 | 3.27
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 117997.75 | 79776.3 | 38221.45 | 0.68 | 3.51
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 134355.15 | 90835.26 | 43519.89 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 543943.3 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 291623.64 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 272810.75 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 102208.69 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 116377.34 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.94 | 56359.68 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.75 | 55950.09 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 27.12 | 61294.35 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 36.37 | 82206.43 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 25.29 | 42296.62 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.92 | 26794.23 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.68 | 21489.06 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.75 | 8914.27 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.41 | 10150.01 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15834.12 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14325.6 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 430846.3891 | 646.0751 | 1530.4099 | 0 | 0.0049 | 352138.1148 | 173496.757
February | 353838.3566 | 544.6935 | 1341.3693 | 0 | 0.0043 | 308669.213 | 143834.2269
March | 355829.8471 | 571.5986 | 1491.8304 | 0 | 0.0047 | 343337.2526 | 146923.0739
April | 269015.2733 | 464.9423 | 1324.4905 | 0 | 0.004 | 304880.4078 | 114213.2402
May | 312421.2983 | 559.1026 | 1652.9447 | 0 | 0.005 | 380513.8918 | 134471.8115
June | 383892.4932 | 695.0682 | 2079.4124 | 0 | 0.0063 | 478699.1563 | 166005.1534
July | 325906.8765 | 590.4781 | 1767.7073 | 0 | 0.0053 | 406942.3982 | 140968.6606
August | 320401.8999 | 579.1584 | 1729.7811 | 0 | 0.0052 | 398209.6673 | 138458.8542
September | 313805.2435 | 565.7356 | 1685.1829 | 0 | 0.0051 | 387940.8281 | 135464.8764
October | 290872.6908 | 510.3192 | 1477.6677 | 0 | 0.0045 | 340150.774 | 124219.7201
November | 321966.2048 | 525.6291 | 1400.382 | 0 | 0.0044 | 322305.1426 | 133746.5356
December | 396691.0655 | 603.4037 | 1460.3188 | 0 | 0.0047 | 336027.6788 | 160559.9178
Annual Sum or Average | 4075490 | 6856.2044 | 18941.497 | 0 | 0.0584 | 4359810 | 1712360
Minimum of Months | 269015.2733 | 464.9423 | 1324.4905 | 0 | 0.004 | 304880.4078 | 114213.2402
Maximum of Months | 430846.3891 | 695.0682 | 2079.4124 | 0 | 0.0063 | 478699.1563 | 173496.757
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 817110000000 | 527618.377 | 11-JAN-11:39 | 218037.744 | 161697.68 | 132188.077 | 0 | 7557.805 | 0 | 554.201 | 0 | 0 | 0 | 0 | 0 | 7582.871 | 0 | 0
February | 716244000000 | 527988.165 | 10-FEB-11:39 | 218037.744 | 161697.68 | 132188.077 | 0 | 7917.77 | 0 | 565.879 | 0 | 0 | 0 | 0 | 0 | 7581.015 | 0 | 0
March | 796688000000 | 718554.483 | 31-MAR-15:09 | 218037.744 | 142955.664 | 132188.077 | 0 | 218510.081 | 0 | 1969.889 | 0 | 0 | 0 | 0 | 0 | 4893.029 | 0 | 0
April | 707452000000 | 706002.04 | 07-APR-14:39 | 218037.744 | 147825.664 | 132188.077 | 0 | 198909.054 | 0 | 3831.412 | 0 | 0 | 0 | 0 | 0 | 5210.089 | 0 | 0
May | 882954000000 | 1086904.516 | 30-MAY-15:00 | 218037.744 | 142955.664 | 132188.077 | 0 | 583917.909 | 0 | 4584.141 | 0 | 0 | 0 | 0 | 0 | 5220.981 | 0 | 0
June | 1110790000000 | 1414178.151 | 08-JUN-12:00 | 218037.744 | 155696.336 | 133483.991 | 0 | 895297.581 | 0 | 6436.899 | 0 | 0 | 0 | 0 | 0 | 5225.599 | 0 | 0
July | 944279000000 | 1179344.828 | 13-JUL-12:00 | 121132.08 | 90545.984 | 132188.077 | 0 | 824790.915 | 0 | 5716.918 | 0 | 0 | 0 | 0 | 0 | 4970.855 | 0 | 0
August | 924016000000 | 1167199.088 | 04-AUG-14:00 | 121132.08 | 82675.312 | 132188.077 | 0 | 819863.93 | 0 | 6366.011 | 0 | 0 | 0 | 0 | 0 | 4973.679 | 0 | 0
September | 900187000000 | 1052283.336 | 06-SEP-10:00 | 218037.744 | 160675.568 | 132188.077 | 0 | 531924.466 | 0 | 4237.105 | 0 | 0 | 0 | 0 | 0 | 5220.376 | 0 | 0
October | 789294000000 | 837242.736 | 31-OCT-12:00 | 218037.744 | 160675.568 | 132188.077 | 0 | 317460.598 | 0 | 3658.287 | 0 | 0 | 0 | 0 | 0 | 5222.462 | 0 | 0
November | 747885000000 | 839877.125 | 02-NOV-11:00 | 218037.744 | 160675.568 | 132188.077 | 0 | 319894.523 | 0 | 3857.495 | 0 | 0 | 0 | 0 | 0 | 5223.719 | 0 | 0
December | 779727000000 | 525447.319 | 21-DEC-11:39 | 218037.744 | 160675.568 | 132188.077 | 0 | 6410.095 | 0 | 556.928 | 0 | 0 | 0 | 0 | 0 | 7578.906 | 0 | 0
Annual Sum or Average | 10116600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 707452000000 | 525447.319 |  | 121132.08 | 82675.312 | 132188.077 | 0 | 6410.095 | 0 | 554.201 | 0 | 0 | 0 | 0 | 0 | 4893.029 | 0 | 0
Maximum of Months | 1110790000000 | 1414178.151 |  | 218037.744 | 161697.68 | 133483.991 | 0 | 895297.581 | 0 | 6436.899 | 0 | 0 | 0 | 0 | 0 | 7582.871 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 234509 | 98826.01 | 0 | 333335.01
Cost per Total Building Area ($/m2) | 11.97 | 5.04 | 0 | 17.01
Cost per Net Conditioned Building Area ($/m2) | 11.97 | 5.04 | 0 | 17.01

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17922.67 | 914.8 | 914.8
Net Site Energy | 17922.67 | 914.8 | 914.8
Total Source Energy | 41774.58 | 2132.23 | 2132.23
Net Source Energy | 41774.58 | 2132.23 | 2132.23
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7011.21 | 0 | 0 | 0 | 0
Cooling | 1509.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 375 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2140.77 | 0 | 0 | 0 | 0 | 0
Pumps | 23.74 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 392.6 | 0 | 0 | 0 | 2677.86
Refrigeration | 161.91 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9974.4 | 7948.27 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 49.41 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 36.4 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.441 | 0.546
North Total or Average |  |  | 753.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.41 | 0.507
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2306714.4 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2526992.64 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 422194.2 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 419195.12 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 460596.54 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 594192 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 475495.28 | 379756.81 | 95738.47 | 0.8 | 3.74
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 292725.21 | 233786.53 | 58938.68 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 236934.96 | 189229.36 | 47705.61 | 0.8 | 3.76
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91028.12 | 72700.08 | 18328.03 | 0.8 | 4.18
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 100978.1 | 80646.69 | 20331.41 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 501639.39 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 247415.84 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 249962.33 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 96033.11 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 106530.17 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 27.57 | 62308.95 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 27.36 | 61832.23 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 30.18 | 68206.7 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.62 | 1388.3 | 40.18 | 90324.35 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 28.72 | 47788.76 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 17.68 | 29767.77 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.31 | 24094.36 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.5 | 10316.08 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.1 | 11443.7 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14041.19 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21137.84 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 302654.423 | 458.3807 | 995.347 | 0 | 0.0041 | 1034550 | 122764.1523
February | 251151.6339 | 387.2694 | 863.2687 | 0 | 0.0035 | 897329.1275 | 102549.3237
March | 265571.5457 | 424.3563 | 993.2186 | 0 | 0.004 | 1032530 | 109894.0095
April | 221551.9667 | 370.2249 | 916.3114 | 0 | 0.0036 | 952705.7667 | 93268.4024
May | 241400.1394 | 411.4049 | 1041.7695 | 0 | 0.0041 | 1083200 | 102409.9931
June | 262187.5293 | 454.4208 | 1172.5544 | 0 | 0.0046 | 1219240 | 111973.1119
July | 234920.3364 | 408.9664 | 1060.3783 | 0 | 0.0041 | 1102610 | 100505.0678
August | 242183.7719 | 421.1031 | 1090.4147 | 0 | 0.0043 | 1133840 | 103562.7325
September | 241761.8432 | 417.1733 | 1071.2156 | 0 | 0.0042 | 1113850 | 103068.7959
October | 235731.2065 | 398.1358 | 997.7777 | 0 | 0.0039 | 1037440 | 99651.1536
November | 252813.8183 | 401.1949 | 930.4815 | 0 | 0.0037 | 967289.6214 | 104342.5593
December | 299408.404 | 450.4473 | 968.3413 | 0 | 0.004 | 1006450 | 121151.5341
Annual Sum or Average | 3051340 | 5003.078 | 12101.0788 | 0 | 0.048 | 12581000 | 1275140
Minimum of Months | 221551.9667 | 370.2249 | 863.2687 | 0 | 0.0035 | 897329.1275 | 93268.4024
Maximum of Months | 302654.423 | 458.3807 | 1172.5544 | 0 | 0.0046 | 1219240 | 122764.1523
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 820203000000 | 659017.582 | 24-JAN-13:00 | 218037.744 | 155696.336 | 148267.117 | 0 | 130171.571 | 0 | 1644.842 | 0 | 0 | 0 | 0 | 0 | 5199.972 | 0 | 0
February | 711413000000 | 597587.091 | 07-FEB-14:00 | 218037.744 | 155696.336 | 148267.117 | 0 | 69281.95 | 0 | 1103.065 | 0 | 0 | 0 | 0 | 0 | 5200.88 | 0 | 0
March | 818603000000 | 785786.847 | 30-MAR-15:00 | 218037.744 | 142955.664 | 148267.117 | 0 | 269150.003 | 0 | 2180.596 | 0 | 0 | 0 | 0 | 0 | 5195.723 | 0 | 0
April | 755317000000 | 847029.628 | 25-APR-14:00 | 218037.744 | 147825.664 | 148748.669 | 0 | 324682.89 | 0 | 2526.835 | 0 | 0 | 0 | 0 | 0 | 5207.826 | 0 | 0
May | 858776000000 | 952097.15 | 23-MAY-15:00 | 218037.744 | 142955.664 | 148815.858 | 0 | 434561.197 | 0 | 2843.468 | 0 | 0 | 0 | 0 | 0 | 4883.22 | 0 | 0
June | 966628000000 | 1092106.792 | 28-JUN-11:00 | 218037.744 | 161697.68 | 149047.313 | 0 | 555042.78 | 0 | 3250.02 | 0 | 0 | 0 | 0 | 0 | 5031.255 | 0 | 0
July | 874162000000 | 929203.004 | 18-JUL-13:00 | 121132.08 | 90545.984 | 148380.72 | 0 | 557322.07 | 0 | 6960.639 | 0 | 0 | 0 | 0 | 0 | 4861.511 | 0 | 0
August | 898921000000 | 940385.483 | 30-AUG-13:00 | 121132.08 | 90545.984 | 148267.117 | 0 | 572351.098 | 0 | 3246.239 | 0 | 0 | 0 | 0 | 0 | 4842.964 | 0 | 0
September | 883078000000 | 1006241.961 | 05-SEP-13:00 | 218037.744 | 154674.224 | 148399.486 | 0 | 477055.763 | 0 | 2953.674 | 0 | 0 | 0 | 0 | 0 | 5121.07 | 0 | 0
October | 822493000000 | 926063.83 | 05-OCT-15:09 | 218037.744 | 142877.04 | 149022.049 | 0 | 408452.03 | 0 | 2807.28 | 0 | 0 | 0 | 0 | 0 | 4867.687 | 0 | 0
November | 766879000000 | 731919.524 | 10-NOV-13:00 | 218037.744 | 154674.224 | 148267.117 | 0 | 203784.088 | 0 | 2100.555 | 0 | 0 | 0 | 0 | 0 | 5055.795 | 0 | 0
December | 797928000000 | 576106.959 | 21-DEC-14:09 | 218037.744 | 154674.224 | 148267.117 | 0 | 49111.536 | 0 | 913.774 | 0 | 0 | 0 | 0 | 0 | 5102.564 | 0 | 0
Annual Sum or Average | 9974400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 711413000000 | 576106.959 |  | 121132.08 | 90545.984 | 148267.117 | 0 | 49111.536 | 0 | 913.774 | 0 | 0 | 0 | 0 | 0 | 4842.964 | 0 | 0
Maximum of Months | 966628000000 | 1092106.792 |  | 218037.744 | 161697.68 | 149047.313 | 0 | 572351.098 | 0 | 6960.639 | 0 | 0 | 0 | 0 | 0 | 5207.826 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 102507.11 | 55012.84 | 0 | 157519.95
Cost per Total Building Area ($/m2) | 5.23 | 2.81 | 0 | 8.04
Cost per Net Conditioned Building Area ($/m2) | 5.23 | 2.81 | 0 | 8.04

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25935.75 | 1323.79 | 1323.79
Net Site Energy | 25935.75 | 1323.79 | 1323.79
Total Source Energy | 51633.05 | 2635.42 | 2635.42
Net Source Energy | 51633.05 | 2635.42 | 2635.42
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15018.5 | 0 | 0 | 0 | 0
Cooling | 1534.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2075.94 | 0 | 0 | 0 | 0 | 0
Pumps | 30.39 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 431.98 | 0 | 0 | 0 | 2677.86
Refrigeration | 161.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9940.81 | 15994.94 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 49.41 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 36.4 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.441 | 0.546
North Total or Average |  |  | 753.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.41 | 0.507
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1475849.62 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2954734.5 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 347715.67 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 346034.32 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 366241.76 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 415857.87 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 624233.75 | 422033.97 | 202199.79 | 0.68 | 3.26
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 266373.05 | 212740.24 | 53632.81 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 302937.74 | 206709.14 | 96228.61 | 0.68 | 3.29
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 118895.96 | 80635.9 | 38260.06 | 0.68 | 3.52
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 134178.86 | 90716.08 | 43462.79 | 0.68 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 584344.41 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 314277.71 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 290829.11 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 112262.15 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 125604.66 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 25.12 | 56778.97 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.92 | 56326.08 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 27.31 | 61720.47 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 36.24 | 81915.78 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 25.14 | 42044.9 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.09 | 27087.97 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.51 | 21197.58 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.83 | 9059.91 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.4 | 10136.69 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16417.93 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 13524.12 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 397504.4997 | 532.4332 | 560.6427 | 0 | 0.0045 | 367824.3908 | 153981.2113
February | 316193.625 | 436.5793 | 488.4773 | 0 | 0.0039 | 320580.4995 | 123731.9223
March | 274232.2337 | 410.3101 | 526.7699 | 0 | 0.004 | 345937.4167 | 110338.7932
April | 187005.8759 | 311.719 | 463.1483 | 0 | 0.0034 | 304339.5004 | 78293.7561
May | 205584.6727 | 363.6379 | 577.3784 | 0 | 0.0042 | 379494.5427 | 88074.6907
June | 233206.568 | 421.0866 | 682.9275 | 0 | 0.005 | 448902.7308 | 100729.398
July | 192792.1094 | 348.6341 | 566.2746 | 0 | 0.0041 | 372226.2716 | 83322.935
August | 206307.0398 | 372.5439 | 604.2458 | 0 | 0.0044 | 397183.6736 | 89113.3143
September | 185345.2287 | 329.8541 | 527.0999 | 0 | 0.0039 | 346455.8166 | 79596.5665
October | 198143.9382 | 329.1399 | 487.0052 | 0 | 0.0036 | 320010.9498 | 82847.4826
November | 258943.1689 | 387.6868 | 498.2231 | 0 | 0.0038 | 327191.795 | 104211.2827
December | 357103.8589 | 489.2614 | 539.2916 | 0 | 0.0043 | 353901.9936 | 139377.1723
Annual Sum or Average | 3012360 | 4732.8863 | 6521.4845 | 0 | 0.0493 | 4284050 | 1233620
Minimum of Months | 185345.2287 | 311.719 | 463.1483 | 0 | 0.0034 | 304339.5004 | 78293.7561
Maximum of Months | 397504.4997 | 532.4332 | 682.9275 | 0 | 0.005 | 448902.7308 | 153981.2113
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 853509000000 | 526049.769 | 20-JAN-11:39 | 218037.744 | 161697.68 | 132151.075 | 0 | 5964.565 | 0 | 624.386 | 0 | 0 | 0 | 0 | 0 | 7574.318 | 0 | 0
February | 743883000000 | 526301.89 | 28-FEB-11:39 | 218037.744 | 161697.68 | 132151.075 | 0 | 5958.678 | 0 | 687.654 | 0 | 0 | 0 | 0 | 0 | 7769.06 | 0 | 0
March | 802722000000 | 615763.186 | 23-MAR-15:00 | 218037.744 | 142955.664 | 132151.075 | 0 | 116262.126 | 0 | 1463.089 | 0 | 0 | 0 | 0 | 0 | 4893.488 | 0 | 0
April | 706197000000 | 712481.452 | 14-APR-15:00 | 218037.744 | 142955.664 | 132151.075 | 0 | 212527.442 | 0 | 1923.262 | 0 | 0 | 0 | 0 | 0 | 4886.265 | 0 | 0
May | 880588000000 | 1027571.089 | 31-MAY-11:00 | 218037.744 | 161697.68 | 132476.549 | 0 | 505925.412 | 0 | 4213.237 | 0 | 0 | 0 | 0 | 0 | 5220.466 | 0 | 0
June | 1041640000000 | 1293253.883 | 29-JUN-15:09 | 218037.744 | 142955.664 | 133122.862 | 0 | 788522.074 | 0 | 5392.828 | 0 | 0 | 0 | 0 | 0 | 5222.712 | 0 | 0
July | 863723000000 | 1106560.558 | 13-JUL-14:00 | 121132.08 | 82675.312 | 132151.075 | 0 | 759958.822 | 0 | 5671.155 | 0 | 0 | 0 | 0 | 0 | 4972.114 | 0 | 0
August | 921635000000 | 1055448.523 | 25-AUG-15:00 | 121132.08 | 77805.312 | 132151.075 | 0 | 713840.636 | 0 | 5548.106 | 0 | 0 | 0 | 0 | 0 | 4971.314 | 0 | 0
September | 803925000000 | 999382.852 | 14-SEP-15:09 | 218037.744 | 142877.04 | 132251.577 | 0 | 497056.172 | 0 | 3942.129 | 0 | 0 | 0 | 0 | 0 | 5218.19 | 0 | 0
October | 742561000000 | 741990.133 | 06-OCT-15:09 | 218037.744 | 142877.04 | 132151.075 | 0 | 239861.435 | 0 | 3853.768 | 0 | 0 | 0 | 0 | 0 | 5209.071 | 0 | 0
November | 759224000000 | 645798.229 | 02-NOV-14:00 | 218037.744 | 154674.224 | 132151.075 | 0 | 134058.379 | 0 | 1666.792 | 0 | 0 | 0 | 0 | 0 | 5210.016 | 0 | 0
December | 821203000000 | 525081.431 | 04-DEC-11:39 | 218037.744 | 160675.568 | 132151.075 | 0 | 5667.837 | 0 | 780.124 | 0 | 0 | 0 | 0 | 0 | 7769.083 | 0 | 0
Annual Sum or Average | 9940810000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 706197000000 | 525081.431 |  | 121132.08 | 77805.312 | 132151.075 | 0 | 5667.837 | 0 | 624.386 | 0 | 0 | 0 | 0 | 0 | 4886.265 | 0 | 0
Maximum of Months | 1041640000000 | 1293253.883 |  | 218037.744 | 161697.68 | 133122.862 | 0 | 788522.074 | 0 | 5671.155 | 0 | 0 | 0 | 0 | 0 | 7769.083 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 177504.1 | 126126.73 | 0 | 303630.84
Cost per Total Building Area ($/m2) | 9.06 | 6.44 | 0 | 15.5
Cost per Net Conditioned Building Area ($/m2) | 9.06 | 6.44 | 0 | 15.5

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22376.32 | 1142.11 | 1142.11
Net Site Energy | 22376.32 | 1142.11 | 1142.11
Total Source Energy | 47084.4 | 2403.25 | 2403.25
Net Source Energy | 47084.4 | 2403.25 | 2403.25
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11896 | 0 | 0 | 0 | 0
Cooling | 1053.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.89 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2124.25 | 0 | 0 | 0 | 0 | 0
Pumps | 22.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 435.24 | 0 | 0 | 0 | 2677.86
Refrigeration | 161.41 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9500.61 | 12875.7 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-3.8 CI_EXT-WALL | 0.3 | 0.477 | 0.51 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 15.4 | 15.4 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 74.2 | 74.2 | 3.18 | 0.402 | 0.495 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 7 | 7 | 3.18 | 0.402 | 0.495 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 15.4 | 15.4 | 3.18 | 0.501 | 0.622 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 74.2 | 74.2 | 3.18 | 0.501 | 0.622 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 25.2 | 25.2 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_WEST | 23.8 | 23.8 | 3.18 | 0.402 | 0.495 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 21 | 21 | 3.18 | 0.402 | 0.495 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 4.2 | 4.2 | 3.18 | 0.402 | 0.495 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 21 | 21 | 3.18 | 0.501 | 0.622 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 53.2 | 53.2 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 19.6 | 19.6 | 3.18 | 0.402 | 0.495 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495 | 33.6 | 33.6 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 72.8 | 72.8 | 3.18 | 0.402 | 0.495 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.622 | 1.49 | 1.49 | 3.82 | 0.5 | 0.622 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 53.2 | 53.2 | 3.18 | 0.501 | 0.622 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 12.6 | 12.6 | 3.18 | 0.402 | 0.495 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 49.41 | 49.41 | 3.18 | 0.402 | 0.495 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.39_VT_0.495_EAST | 36.4 | 36.4 | 3.18 | 0.402 | 0.495 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.622 | 33.6 | 33.6 | 3.18 | 0.501 | 0.622 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.441 | 0.546
North Total or Average |  |  | 753.18 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.41 | 0.507
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2334642.9 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2777173.33 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 453900.79 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 450160.88 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 494450.72 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 634983.36 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 445245.06 | 355597.31 | 89647.75 | 0.8 | 3.74
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 279549.67 | 223263.82 | 56285.86 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 219598.58 | 175383.56 | 44215.02 | 0.8 | 3.94
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87555.56 | 69926.71 | 17628.85 | 0.8 | 4.18
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 93942.08 | 75027.33 | 18914.74 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 569746.77 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 290718.57 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 281003.86 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 112038.29 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 120210.64 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 26.8 | 60561.42 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 26.56 | 60041.09 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 29.25 | 66105.55 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 38.37 | 86715.26 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 26.9 | 44748.52 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.89 | 28427.93 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.27 | 22331.39 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.29 | 9922.54 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.68 | 10646.32 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 15431.32 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21393.77 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 352753.5798 | 492.3889 | 624.3395 | 0 | 0.0046 | 14792600 | 138733.3252
February | 288167.5975 | 412.3732 | 546.6862 | 0 | 0.004 | 12955300 | 114312.3158
March | 263001.4194 | 405.8224 | 605.4944 | 0 | 0.0043 | 14355800 | 107177.1817
April | 204585.7398 | 329.6086 | 521.3634 | 0 | 0.0037 | 12363800 | 84717.8318
May | 207339.3849 | 352.4392 | 594.9031 | 0 | 0.0042 | 14110900 | 87636.1477
June | 227034.2958 | 394.857 | 683.744 | 0 | 0.0048 | 16219500 | 96824.7765
July | 190196.3152 | 333.9894 | 584.3774 | 0 | 0.0041 | 13862900 | 81423.6516
August | 189673.5101 | 329.0014 | 568.0524 | 0 | 0.004 | 13475000 | 80806.4279
September | 199585.8486 | 343.4673 | 587.8737 | 0 | 0.0041 | 13944800 | 84765.6939
October | 212077.9056 | 348.5271 | 565.2215 | 0 | 0.004 | 13405000 | 88482.2329
November | 254769.7469 | 388.4043 | 569.4864 | 0 | 0.0041 | 13501100 | 103366.7477
December | 324733.4431 | 459.8489 | 598.5131 | 0 | 0.0044 | 14182300 | 128348.6203
Annual Sum or Average | 2913920 | 4590.7275 | 7050.0551 | 0 | 0.0503 | 167169000 | 1196590
Minimum of Months | 189673.5101 | 329.0014 | 521.3634 | 0 | 0.0037 | 12363800 | 80806.4279
Maximum of Months | 352753.5798 | 492.3889 | 683.744 | 0 | 0.0048 | 16219500 | 138733.3252
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 840698000000 | 547149.188 | 05-JAN-08:09 | 218037.744 | 155696.336 | 140136.891 | 0 | 0 | 23884.224 | 4744.297 | 0 | 0 | 0 | 0 | 0 | 4649.697 | 0 | 0
February | 736279000000 | 644013.451 | 02-FEB-14:00 | 218037.744 | 155696.336 | 140136.891 | 0 | 123409.569 | 0 | 1599.302 | 0 | 0 | 0 | 0 | 0 | 5133.609 | 0 | 0
March | 815872000000 | 720610.547 | 30-MAR-15:00 | 218037.744 | 142955.664 | 140136.891 | 0 | 212244.093 | 0 | 2035.568 | 0 | 0 | 0 | 0 | 0 | 5200.587 | 0 | 0
April | 702662000000 | 680330.905 | 06-APR-15:00 | 218037.744 | 142955.664 | 140136.891 | 0 | 172465.147 | 0 | 1873.91 | 0 | 0 | 0 | 0 | 0 | 4861.549 | 0 | 0
May | 801956000000 | 845785.489 | 16-MAY-15:00 | 218037.744 | 142955.664 | 140136.891 | 0 | 337006.832 | 0 | 2443.215 | 0 | 0 | 0 | 0 | 0 | 5205.144 | 0 | 0
June | 921795000000 | 1114017.594 | 30-JUN-15:09 | 218037.744 | 142955.664 | 141115.85 | 0 | 599756.653 | 0 | 7218.448 | 0 | 0 | 0 | 0 | 0 | 4933.235 | 0 | 0
July | 787860000000 | 877631.258 | 21-JUL-15:00 | 121132.08 | 77805.312 | 140136.891 | 0 | 530810.156 | 0 | 3134.525 | 0 | 0 | 0 | 0 | 0 | 4612.295 | 0 | 0
August | 765817000000 | 828586.569 | 09-AUG-15:00 | 121132.08 | 77805.312 | 140136.891 | 0 | 481907.796 | 0 | 2990.311 | 0 | 0 | 0 | 0 | 0 | 4614.179 | 0 | 0
September | 792517000000 | 884831.759 | 07-SEP-15:00 | 218037.744 | 142877.04 | 140156.748 | 0 | 376253.914 | 0 | 2605.207 | 0 | 0 | 0 | 0 | 0 | 4901.107 | 0 | 0
October | 761839000000 | 781865.042 | 06-OCT-15:00 | 218037.744 | 142877.04 | 140136.891 | 0 | 273677.269 | 0 | 2260.301 | 0 | 0 | 0 | 0 | 0 | 4875.797 | 0 | 0
November | 767302000000 | 576958.346 | 21-NOV-11:39 | 218037.744 | 160675.568 | 140136.891 | 0 | 49385.556 | 0 | 953.644 | 0 | 0 | 0 | 0 | 0 | 7768.943 | 0 | 0
December | 806015000000 | 544928.835 | 22-DEC-08:09 | 218037.744 | 154674.224 | 140136.891 | 0 | 2143.718 | 23884.224 | 851.737 | 0 | 0 | 0 | 0 | 0 | 5200.298 | 0 | 0
Annual Sum or Average | 9500610000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 702662000000 | 544928.835 |  | 121132.08 | 77805.312 | 140136.891 | 0 | 0 | 0 | 851.737 | 0 | 0 | 0 | 0 | 0 | 4612.295 | 0 | 0
Maximum of Months | 921795000000 | 1114017.594 |  | 218037.744 | 160675.568 | 141115.85 | 0 | 599756.653 | 23884.224 | 7218.448 | 0 | 0 | 0 | 0 | 0 | 7768.943 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 208821.22 | 104251.02 | 0 | 313072.23
Cost per Total Building Area ($/m2) | 10.66 | 5.32 | 0 | 15.98
Cost per Net Conditioned Building Area ($/m2) | 10.66 | 5.32 | 0 | 15.98

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 28510.22 | 1455.2 | 1455.2
Net Site Energy | 28510.22 | 1455.2 | 1455.2
Total Source Energy | 52523.88 | 2680.88 | 2680.88
Net Source Energy | 52523.88 | 2680.88 | 2680.88
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 18358.72 | 0 | 0 | 0 | 0
Cooling | 760.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 374.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2036.75 | 0 | 0 | 0 | 0 | 0
Pumps | 25.21 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 485.21 | 0 | 0 | 0 | 2677.86
Refrigeration | 160.95 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9121.84 | 19388.38 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-15 CI_ROOF | 0.3 | 0.357 | 0.38 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 3.18 | 0.501 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 3.18 | 0.501 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 3.18 | 0.651 | 0.64 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 3.18 | 0.651 | 0.64 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 25.2 | 25.2 | 3.18 | 0.501 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 23.8 | 23.8 | 3.18 | 0.501 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 25.2 | 25.2 | 3.18 | 0.501 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_WEST | 23.8 | 23.8 | 3.18 | 0.501 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 21 | 21 | 3.18 | 0.501 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 21 | 21 | 3.18 | 0.501 | 0.49 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 4.2 | 4.2 | 3.18 | 0.501 | 0.49 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 21 | 21 | 3.18 | 0.651 | 0.64 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 4.2 | 4.2 | 3.18 | 0.501 | 0.49 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 21 | 21 | 3.18 | 0.651 | 0.64 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 53.2 | 53.2 | 3.18 | 0.501 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 19.6 | 19.6 | 3.18 | 0.501 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 53.2 | 53.2 | 3.18 | 0.501 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 19.6 | 19.6 | 3.18 | 0.501 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 33.6 | 33.6 | 3.18 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 72.8 | 72.8 | 3.18 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49 | 33.6 | 33.6 | 3.18 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 72.8 | 72.8 | 3.18 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.919_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.82 | 0.5 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 53.2 | 53.2 | 3.18 | 0.651 | 0.64 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 53.2 | 53.2 | 3.18 | 0.651 | 0.64 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 12.6 | 12.6 | 3.18 | 0.501 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 49.41 | 49.41 | 3.18 | 0.501 | 0.49 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 33.6 | 33.6 | 3.18 | 0.651 | 0.64 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.49_VT_0.49_EAST | 36.4 | 36.4 | 3.18 | 0.501 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_3.237_SHGC_0.64_VT_0.64 | 33.6 | 33.6 | 3.18 | 0.651 | 0.64 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 3.22 | 0.552 | 0.541
North Total or Average |  |  | 753.18 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 1469.82 | 3.24 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1246113.15 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 2900309.81 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 291057.81 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 289137.81 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 309390.22 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 356527.31 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 588137.67 | 398668.01 | 189469.66 | 0.68 | 3.26
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 250352.42 | 199945.28 | 50407.14 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 232116 | 170124.93 | 61991.07 | 0.73 | 3.48
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 95851.53 | 70453.45 | 25398.09 | 0.74 | 3.8
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 116763.52 | 81408.22 | 35355.3 | 0.7 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 567593.02 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 314269.32 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 273993.66 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 113930.28 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 121521.52 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.47 | 55310.42 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 24.22 | 54743.74 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 26.72 | 60389.02 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 34.66 | 78341.12 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.61 | 1017.59 | 23.85 | 39898.94 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.12 | 25458.8 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.52 | 19510.51 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.79 | 8982.75 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.11 | 9581.28 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16115.52 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11418.9 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 397728.1604 | 531.1869 | 555.9244 | 0 | 0.0045 | 364716.6906 | 153920.0796
February | 332764.7192 | 452.0004 | 489.7892 | 0 | 0.0039 | 321388.1882 | 129503.4736
March | 311301.9521 | 446.0033 | 533.5989 | 0 | 0.0042 | 350308.6401 | 123364.1408
April | 208869.3817 | 328.7579 | 454.1101 | 0 | 0.0034 | 298313.9835 | 85592.4717
May | 192255.3793 | 324.2882 | 488.5843 | 0 | 0.0036 | 321070.7169 | 80856.5955
June | 190381.4742 | 339.8905 | 544.9178 | 0 | 0.004 | 358171.465 | 81861.9944
July | 169184.3183 | 303.0081 | 487.3762 | 0 | 0.0036 | 320353.3607 | 72839.3198
August | 163267.2134 | 285.0994 | 446.5242 | 0 | 0.0033 | 293473.2984 | 69592.9658
September | 176826.0125 | 303.966 | 467.9446 | 0 | 0.0035 | 307532.187 | 74912.6617
October | 207388.1383 | 334.1443 | 476.0201 | 0 | 0.0036 | 312746.2334 | 85723.1923
November | 285503.7765 | 412.6083 | 500.9904 | 0 | 0.0039 | 328924.0477 | 113481.5963
December | 374171.4173 | 504.8531 | 539.6939 | 0 | 0.0043 | 354109.0703 | 145293.7826
Annual Sum or Average | 3009640 | 4565.8063 | 5985.4742 | 0 | 0.0457 | 3931110 | 1216940
Minimum of Months | 163267.2134 | 285.0994 | 446.5242 | 0 | 0.0033 | 293473.2984 | 69592.9658
Maximum of Months | 397728.1604 | 531.1869 | 555.9244 | 0 | 0.0045 | 364716.6906 | 153920.0796
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 846298000000 | 518589.492 | 06-JAN-11:39 | 218037.744 | 161697.68 | 125371.284 | 0 | 5147.137 | 0 | 767.682 | 0 | 0 | 0 | 0 | 0 | 7567.966 | 0 | 0
February | 745757000000 | 518953.06 | 27-FEB-11:39 | 218037.744 | 161697.68 | 125371.284 | 0 | 5264.924 | 0 | 812.376 | 0 | 0 | 0 | 0 | 0 | 7769.053 | 0 | 0
March | 812865000000 | 519454.618 | 14-MAR-10:39 | 218037.744 | 161697.68 | 125371.284 | 0 | 6119.031 | 0 | 459.82 | 0 | 0 | 0 | 0 | 0 | 7769.059 | 0 | 0
April | 692215000000 | 603717.85 | 04-APR-14:00 | 218037.744 | 147825.664 | 125371.284 | 0 | 105881.649 | 0 | 1395.079 | 0 | 0 | 0 | 0 | 0 | 5206.431 | 0 | 0
May | 745020000000 | 752077.533 | 31-MAY-15:00 | 218037.744 | 142955.664 | 125412.75 | 0 | 258761.742 | 0 | 2029.45 | 0 | 0 | 0 | 0 | 0 | 4880.183 | 0 | 0
June | 831110000000 | 1036378.978 | 14-JUN-15:09 | 218037.744 | 142955.664 | 125713.38 | 0 | 539661.665 | 0 | 4788.215 | 0 | 0 | 0 | 0 | 0 | 5222.309 | 0 | 0
July | 743356000000 | 875674.534 | 06-JUL-14:00 | 121132.08 | 82675.312 | 125371.284 | 0 | 537007.555 | 0 | 4520.859 | 0 | 0 | 0 | 0 | 0 | 4967.445 | 0 | 0
August | 680983000000 | 832742.323 | 11-AUG-14:00 | 121132.08 | 82675.312 | 125371.284 | 0 | 494097.772 | 0 | 4497.54 | 0 | 0 | 0 | 0 | 0 | 4968.335 | 0 | 0
September | 713605000000 | 874266.496 | 07-SEP-15:09 | 218037.744 | 142877.04 | 125418.236 | 0 | 378854.885 | 0 | 3854.87 | 0 | 0 | 0 | 0 | 0 | 5223.721 | 0 | 0
October | 725704000000 | 621614.593 | 27-OCT-11:00 | 218037.744 | 160675.568 | 125371.284 | 0 | 110989.15 | 0 | 1499.393 | 0 | 0 | 0 | 0 | 0 | 5041.455 | 0 | 0
November | 763243000000 | 517881.25 | 10-NOV-11:39 | 218037.744 | 160675.568 | 125371.284 | 0 | 5568.525 | 0 | 577.865 | 0 | 0 | 0 | 0 | 0 | 7650.265 | 0 | 0
December | 821683000000 | 517805.538 | 04-DEC-11:39 | 218037.744 | 160675.568 | 125371.284 | 0 | 5051.458 | 0 | 900.429 | 0 | 0 | 0 | 0 | 0 | 7769.056 | 0 | 0
Annual Sum or Average | 9121840000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 680983000000 | 517805.538 |  | 121132.08 | 82675.312 | 125371.284 | 0 | 5051.458 | 0 | 459.82 | 0 | 0 | 0 | 0 | 0 | 4880.183 | 0 | 0
Maximum of Months | 846298000000 | 1036378.978 |  | 218037.744 | 161697.68 | 125713.38 | 0 | 539661.665 | 0 | 4788.215 | 0 | 0 | 0 | 0 | 0 | 7769.059 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 155783.73 | 152537.95 | 0 | 308321.68
Cost per Total Building Area ($/m2) | 7.95 | 7.79 | 0 | 15.74
Cost per Net Conditioned Building Area ($/m2) | 7.95 | 7.79 | 0 | 15.74

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40160.82 | 2049.86 | 2049.86
Net Site Energy | 40160.82 | 2049.86 | 2049.86
Total Source Energy | 65846.76 | 3360.9 | 3360.9
Net Source Energy | 65846.76 | 3360.9 | 3360.9
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 30200.7 | 0 | 0 | 0 | 0
Cooling | 527.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 3338.63 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 372.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2425.02 | 544.46 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2012.84 | 0 | 0 | 0 | 0 | 0
Pumps | 33.2 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 548.27 | 0 | 0 | 0 | 2677.86
Refrigeration | 158.26 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8867.39 | 31293.43 | 0 | 0 | 0 | 2677.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 5.38 | 10 | 4
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 15.06 | 4 | 20
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 5.38 |  | 4
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 14 |  | 4
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.68 | 10 | 4
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 11.84 | 20 | 10.8
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 80.28 | 15.06 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 266.35 | 15.06 | 3.33 | 5
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 9.68 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 12.9 | 6.67 | 1908.08
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 14 | 4.35 | 10
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 15.1 | 1.39 | 19.26
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 98.9318
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 16 | 100 | 4
Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2223 | 12.3655 | 3.25 | 30.5807
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 320 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 320 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 320 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 99 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 477 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1140 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 210 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 210 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 532 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1976 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 1248 | 90 | 0
AUDITORIUM_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 988 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 840 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | STEEL-FRAMED_R-13 + R-7.5 CI_EXT-WALL | 0.3 | 0.364 | 0.38 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 624 | 270 | 180
MECH_ZN_1_FLR_1_FLOOR | UNHEATED - 4IN SLAB WITH CARPET_EXT-SLAB | 0.3 | 1.862 | 3.4 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | IEAD_R-20 CI_ROOF | 0.3 | 0.273 | 0.29 | 342 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 15.4 | 15.4 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 74.2 | 74.2 | 2.58 | 0.504 | 0.49 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 7 | 7 | 2.58 | 0.504 | 0.49 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 15.4 | 15.4 | 2.58 | 0.654 | 0.64 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 74.2 | 74.2 | 2.58 | 0.654 | 0.64 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 25.2 | 25.2 | 2.58 | 0.504 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 23.8 | 23.8 | 2.58 | 0.504 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 25.2 | 25.2 | 2.58 | 0.504 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_WEST | 23.8 | 23.8 | 2.58 | 0.504 | 0.49 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 21 | 21 | 2.58 | 0.504 | 0.49 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 21 | 21 | 2.58 | 0.504 | 0.49 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 4.2 | 4.2 | 2.58 | 0.504 | 0.49 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 21 | 21 | 2.58 | 0.654 | 0.64 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 4.2 | 4.2 | 2.58 | 0.504 | 0.49 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 21 | 21 | 2.58 | 0.654 | 0.64 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 53.2 | 53.2 | 2.58 | 0.504 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 19.6 | 19.6 | 2.58 | 0.504 | 0.49 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 53.2 | 53.2 | 2.58 | 0.504 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 19.6 | 19.6 | 2.58 | 0.504 | 0.49 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_37 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_38 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_39 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_40 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_41 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_42 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_43 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_44 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_45 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_46 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_47 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_48 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_49 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_50 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_51 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_52 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_53 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
GYM_ZN_1_FLR_2_SKYLIGHT_54 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 33.6 | 33.6 | 2.58 | 0.504 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 72.8 | 72.8 | 2.58 | 0.504 | 0.49 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49 | 33.6 | 33.6 | 2.58 | 0.504 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 72.8 | 72.8 | 2.58 | 0.504 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_1 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_2 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_3 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_4 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_5 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_6 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_7 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_8 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_9 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_10 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_11 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_12 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_13 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_14 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_15 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_16 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_17 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_18 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_19 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_20 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_21 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_22 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_23 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_24 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_25 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_26 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_27 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_28 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_29 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_30 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_31 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_32 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_33 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_34 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_35 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUX_GYM_ZN_1_FLR_2_SKYLIGHT_36 | STD_WINDOW_UVALUE_3.294_SHGC_0.49_VT_0.49 | 1.49 | 1.49 | 3.23 | 0.501 | 0.49 | No | AUX_GYM_ZN_1_FLR_2_CEILING | 90
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 53.2 | 53.2 | 2.58 | 0.654 | 0.64 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 53.2 | 53.2 | 2.58 | 0.654 | 0.64 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 12.6 | 12.6 | 2.58 | 0.504 | 0.49 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 49.41 | 49.41 | 2.58 | 0.504 | 0.49 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 33.6 | 33.6 | 2.58 | 0.654 | 0.64 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.49_VT_0.49_EAST | 36.4 | 36.4 | 2.58 | 0.504 | 0.49 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | STD_WINDOW_UVALUE_2.612_SHGC_0.64_VT_0.64 | 33.6 | 33.6 | 2.58 | 0.654 | 0.64 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
Total or Average |  |  | 2223 | 2.62 | 0.554 | 0.541
North Total or Average |  |  | 753.18 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 1469.82 | 2.64 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2145826.16 | 2.8
HEATSYS1 BOILER | Boiler:HotWater | 3153411.01 | 0.79
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_POD_1_COOLC | Coil:Cooling:Water | 489998 | - | - | - | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 482730.56 | - | - | - | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 534806.08 | - | - | - | -
VAV_OTHER_COOLC | Coil:Cooling:Water | 626576.13 | - | - | - | -
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 327098.16 | 261238.67 | 65859.49 | 0.8 | 3.76
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 228757.04 | 182698.02 | 46059.03 | 0.8 | 3.76
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 150972.07 | 120574.64 | 30397.43 | 0.8 | 4.14
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75482.93 | 60284.84 | 15198.09 | 0.8 | 4.18
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74123.89 | 59199.43 | 14924.45 | 0.8 | 4.18
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | -99999 | -
VAV_POD_1_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_2_HEATC | Coil:Heating:Water | -99999 | -
VAV_POD_3_HEATC | Coil:Heating:Water | -99999 | -
VAV_OTHER_HEATC | Coil:Heating:Water | -99999 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 582221.41 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 376808.4 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 268724.14 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 134356.54 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 131937.5 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.45 | 125 | 0.3 | 83.33 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 0 | 0.28 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 125 | 2.83 | 353.96 | 1 | Zone Exhaust Fans
VAV_POD_1_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 23.12 | 52482.8 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 22.77 | 51690.41 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 25.22 | 57012.34 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.61 | 1388.3 | 29.86 | 67485.46 | 1 | Fan Energy
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.82 | 23262.73 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.6 | 1109.65 | 9.12 | 16850.21 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.56 | 8554.37 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 4.48 | 8400.35 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17521.88 | 0.9
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19663.53 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 462419.142 | 476.5253 | 1188.7937 | 0 | 0.0046 | 238291.7854 | 168778.0514
February | 403213.6246 | 417.2636 | 1073.1975 | 0 | 0.0042 | 215135.4315 | 147437.9581
March | 371718.2214 | 393.6446 | 1177.112 | 0 | 0.0044 | 236039.2211 | 137302.3925
April | 234928.1584 | 259.6749 | 971.7545 | 0 | 0.0035 | 194934.446 | 88451.6303
May | 166048.5156 | 198.9786 | 1009.842 | 0 | 0.0035 | 202655.4999 | 64893.9499
June | 165390.9425 | 203.4511 | 1115.896 | 0 | 0.0038 | 223957.1562 | 65446.464
July | 128308.1231 | 157.2115 | 852.6599 | 0 | 0.0029 | 171124.4218 | 50676.6094
August | 137350.6326 | 163.6435 | 815.5222 | 0 | 0.0028 | 163655.9462 | 53532.8678
September | 171207.6089 | 199.6738 | 926.4231 | 0 | 0.0032 | 185895.4513 | 66065.8134
October | 280326.1407 | 305.755 | 1073.7613 | 0 | 0.0039 | 215375.639 | 104913.2607
November | 399105.9152 | 417.5575 | 1157.3451 | 0 | 0.0044 | 232040.7414 | 146635.3166
December | 446606.574 | 461.9718 | 1184.5756 | 0 | 0.0046 | 237460.9247 | 163274.6188
Annual Sum or Average | 3366620 | 3655.3512 | 12546.883 | 0 | 0.0458 | 2516570 | 1257410
Minimum of Months | 128308.1231 | 157.2115 | 815.5222 | 0 | 0.0028 | 163655.9462 | 50676.6094
Maximum of Months | 462419.142 | 476.5253 | 1188.7937 | 0 | 0.0046 | 238291.7854 | 168778.0514
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 839647000000 | 528623.949 | 02-JAN-11:09 | 218037.744 | 161697.68 | 110538.309 | 0 | 0 | 23884.224 | 8518.987 | 0 | 0 | 0 | 0 | 0 | 5947.005 | 0 | 0
February | 758053000000 | 522379.777 | 03-FEB-08:09 | 218037.744 | 155696.336 | 110538.309 | 0 | 0 | 23884.224 | 9574.884 | 0 | 0 | 0 | 0 | 0 | 4648.28 | 0 | 0
March | 831710000000 | 518736.792 | 14-MAR-07:10 | 218037.744 | 155696.336 | 110538.309 | 0 | 0 | 23884.224 | 5931.416 | 0 | 0 | 0 | 0 | 0 | 4648.762 | 0 | 0
April | 686873000000 | 503607.873 | 19-APR-10:39 | 218037.744 | 161697.68 | 110538.309 | 0 | 5142.989 | 0 | 422.095 | 0 | 0 | 0 | 0 | 0 | 7769.056 | 0 | 0
May | 714079000000 | 645636.434 | 30-MAY-14:00 | 218037.744 | 147825.664 | 110768.279 | 0 | 162109.41 | 0 | 1807.78 | 0 | 0 | 0 | 0 | 0 | 5087.557 | 0 | 0
June | 789137000000 | 823934.849 | 20-JUN-15:00 | 218037.744 | 142955.664 | 111021.281 | 0 | 344161.03 | 0 | 2551.546 | 0 | 0 | 0 | 0 | 0 | 5207.584 | 0 | 0
July | 602975000000 | 636855.659 | 21-JUL-16:00 | 121132.08 | 43200.624 | 110538.309 | 0 | 354771.77 | 0 | 2588.018 | 0 | 0 | 0 | 0 | 0 | 4624.857 | 0 | 0
August | 576659000000 | 617525.335 | 15-AUG-13:00 | 121132.08 | 90545.984 | 110538.309 | 0 | 286153.742 | 0 | 4195.698 | 0 | 0 | 0 | 0 | 0 | 4959.521 | 0 | 0
September | 655023000000 | 562719.016 | 07-SEP-15:00 | 218037.744 | 142877.04 | 110538.309 | 0 | 84857.889 | 0 | 1203.218 | 0 | 0 | 0 | 0 | 0 | 5204.816 | 0 | 0
October | 758899000000 | 514995.224 | 20-OCT-07:00 | 218037.744 | 154674.224 | 110538.309 | 0 | 1962.666 | 23884.224 | 693.223 | 0 | 0 | 0 | 0 | 0 | 5204.834 | 0 | 0
November | 817621000000 | 519548.905 | 28-NOV-10:20 | 218037.744 | 160675.568 | 110538.309 | 0 | 292.647 | 23884.224 | 1225.046 | 0 | 0 | 0 | 0 | 0 | 4895.367 | 0 | 0
December | 836719000000 | 526158.831 | 29-DEC-11:09 | 218037.744 | 160675.568 | 110538.309 | 0 | 0 | 23884.224 | 7075.98 | 0 | 0 | 0 | 0 | 0 | 5947.005 | 0 | 0
Annual Sum or Average | 8867390000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 576659000000 | 503607.873 |  | 121132.08 | 43200.624 | 110538.309 | 0 | 0 | 0 | 422.095 | 0 | 0 | 0 | 0 | 0 | 4624.857 | 0 | 0
Maximum of Months | 839647000000 | 823934.849 |  | 218037.744 | 161697.68 | 111021.281 | 0 | 354771.77 | 23884.224 | 9574.884 | 0 | 0 | 0 | 0 | 0 | 7769.056 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 235278.39 | 129023.01 | 0 | 364301.4
Cost per Total Building Area ($/m2) | 12.01 | 6.59 | 0 | 18.59
Cost per Net Conditioned Building Area ($/m2) | 12.01 | 6.59 | 0 | 18.59

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 586.61
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1366.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5 | 2255.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5 | 1494.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
Showers_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8 | 1848.37
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Gym_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Gym_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Gym_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Gym_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720