## BuildingSummary
Building Summary Small Hotel new construction
|  | Value | Data Source
Program
| Building Name | Small Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 4013.63 | PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings
| Building Shape | Rectangle
| Aspect Ratio | 3
| Number of Floors | 4
Window Fraction (Window to Wall Ratio)
| South | 0.1524
| East | 0.0313
| North | 0.1139
| West | 0.0395
| Total | 0.1087
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 3.35 1st floor, 2.74 upper floors
| Floor to Floor Height (m) | 3.35 1st floor, 2.74 upper floors
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1694.66
| Net Dimensions - Total Area (m2) | 1510.43
| Wall to Skin Ratio | 0.62811
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1003.3894
| Net Dimensions - Total Area (m2) | 1003.3894
| Roof to Skin Ratio | 0.37189
Window Dimensions (m2)
| South | 96.83
| East | 6.62
| North | 72.38
| West | 8.38
| Total Area (m2) | 184.21
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
Dimensions - Total Area (m2)
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) |  | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 3470.09

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 37.6275 | 0 | 0.070528
REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.02 | 14.83 | 3.08 | 52.9416 | 11.8 | 15.4333 | 0 | 0 | 8 | 0 | 423.5325 | 0 | 0.18717
RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 9.7 | 10.7631 | 0 | 0 | 0 | 0 | 0 | 200 | 0.13229
MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.87 | 42.9251 | 14 | 12.9 | 0 | 0 | 10 | 0 | 429.2513 | 0 | 0.13223
MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 16.16 | 0 | 0 | 0 | 0 | 0.25 | 8.1525 | 0 | 0.13229
GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13229
GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13229
GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13229
GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.1323
GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.1323
EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 2.96 | 11.0169 | 12.9 | 77.1567 | 0 | 0 | 8 | 0 | 88.1351 | 0 | 0.1323
LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 8.89 | 11.0045 | 6.46 | 21.8668 | 184.2477 | 255.5145 | 13 | 0 | 143.0585 | 0 | 0.13227
ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.3696 | 0 | 0 | 0 | 5 | 75.25 | 0 | 0.13222
EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 2.96 | 11.0169 | 9.7 | 11.4999 | 0 | 0 | 10 | 0 | 110.1689 | 0 | 0.1323
FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.04 | 10.0031 | 11.84 | 12.9 | 0 | 0 | 10 | 0 | 100.0307 | 0 | 0.13225
FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57864
FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13226
REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57858
CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 31.355 | 0 | 0.058175
REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.40695
GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.84 | 14.3 | 0 | 19.8734 | 0 | 0 | 42.471 | 0 | 0.13225
GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13224
GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13232
GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13221
FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57849
REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57858
CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 31.355 | 0 | 0.058175
REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57847
GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.40695
GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.84 | 14.3 | 0 | 19.8734 | 0 | 0 | 42.471 | 0 | 0.13225
GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13224
GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13224
GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13232
GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.13226
GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.13226
FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13221
FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57849
REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9753
CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.38 | 0 | 0 | 0 | 0 | 0.25 | 31.355 | 0 | 0.45493
REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97512
GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.80368
GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52901
GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.84 | 14.3 | 0 | 19.8734 | 0 | 0 | 42.471 | 0 | 0.52901
GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52901
GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52898
GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52903
GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52902
ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52903
GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52903
GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.84 | 14.3 | 0 | 26.4978 | 0 | 0 | 56.628 | 0 | 0.52902
GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.84 | 14.3 | 0 | 6.6245 | 0 | 0 | 14.157 | 0 | 0.52903
FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52884
FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97528
Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.66 | 184.23 |  | 255.4127
Data Source | [7 empty] | 1 |  | 2 | 4 |  | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 3.1231 | 88.1153 | 9.1306 | 82.0032 |  | 34.8301 | 6.663 | 96.3435 | 6.2231 | 12.0231 | 111.6509 | 27.3736 | 32.6486 | 9.4333 | 6.2759 | 1.1875
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 3.2051
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| GUESTROOM101 PTAC DXCOIL | 1.8607 | 1.9355 | 1.8533 | 1.7618 | 1.4796 | 1.5511 | 1.7657 | 1.721 | 1.5245 | 1.4735 | 1.7371 | 1.5343 | 1.7108 | 1.5263 | 1.4735 | 1.6161
| GUESTROOM102 PTAC DXCOIL | 1.8828 | 1.9587 | 1.8808 | 1.7885 | 1.5048 | 1.5739 | 1.8128 | 1.7422 | 1.5478 | 1.5055 | 1.7593 | 1.5579 | 1.7344 | 1.5547 | 1.4974 | 1.6696
| GUESTROOM103 PTAC DXCOIL | 2.0322 | 2.1123 | 2.0542 | 1.903 | 1.5982 | 1.674 | 1.8247 | 1.8256 | 1.6062 | 1.5479 | 1.8315 | 1.6024 | 1.8092 | 1.5943 | 1.5245 | 1.6524
| GUESTROOM104 PTAC DXCOIL | 1.9525 | 1.9125 | 1.7759 | 1.7137 | 1.3541 | 1.4683 | 1.1033 | 1.6369 | 1.49 | 1.1845 | 1.6233 | 1.4441 | 1.5565 | 1.3692 | 1.2579 | 1.1372
| GUESTROOM105 PTAC DXCOIL | 1.953 | 1.9125 | 1.7492 | 1.7415 | 1.4453 | 1.516 | 1.2453 | 1.6867 | 1.6421 | 1.3043 | 1.679 | 1.6135 | 1.6164 | 1.5239 | 1.3935 | 1.3107
| GUESTROOM201 PTAC DXCOIL | 2.7046 | 2.7477 | 2.8891 | 2.3628 | 2.1364 | 2.5162 | 2.4312 | 2.206 | 2.3384 | 2.0695 | 2.2251 | 2.3199 | 2.1589 | 2.2607 | 2.1289 | 2.3784
| GUESTROOM202_205 PTAC DXCOIL | 8.0672 | 8.4052 | 8.6923 | 7.8575 | 6.9121 | 7.6289 | 9.0243 | 7.7915 | 7.8454 | 7.6298 | 7.9394 | 7.9049 | 7.8655 | 7.9091 | 7.6104 | 9.1293
| GUESTROOM206_208 PTAC DXCOIL | 6.3887 | 6.6592 | 6.9334 | 6.2524 | 5.5869 | 6.138 | 7.6627 | 6.2427 | 6.3069 | 6.304 | 6.3336 | 6.3686 | 6.3052 | 6.4568 | 6.2614 | 7.7576
| GUESTROOM209_212 PTAC DXCOIL | 7.9093 | 8.2319 | 8.4991 | 7.6924 | 6.7153 | 7.4526 | 8.7959 | 7.6205 | 7.605 | 7.3994 | 7.7679 | 7.6663 | 7.6926 | 7.6749 | 7.372 | 8.7979
| GUESTROOM213 PTAC DXCOIL | 2.2279 | 2.3178 | 2.4388 | 2.1509 | 1.9029 | 2.1538 | 2.3877 | 2.1026 | 2.1224 | 2.0531 | 2.1352 | 2.1197 | 2.1164 | 2.1205 | 2.0423 | 2.383
| GUESTROOM214 PTAC DXCOIL | 2.1754 | 2.1479 | 2.1859 | 1.9914 | 1.6875 | 2.0633 | 1.6175 | 1.9307 | 2.0321 | 1.678 | 1.9304 | 1.9853 | 1.8773 | 1.9095 | 1.8027 | 1.8265
| GUESTROOM215_218 PTAC DXCOIL | 8.2787 | 8.2096 | 8.1427 | 7.6503 | 6.714 | 7.7704 | 6.6464 | 7.5305 | 8.1655 | 6.7499 | 7.5447 | 8.0776 | 7.3204 | 7.6973 | 7.1874 | 7.2632
| GUESTROOM219 PTAC DXCOIL | 2.4571 | 2.4293 | 2.5092 | 2.3647 | 2.1753 | 2.479 | 2.1501 | 2.3926 | 2.6298 | 2.1864 | 2.3989 | 2.6062 | 2.3083 | 2.494 | 2.3128 | 2.3419
| GUESTROOM220_223 PTAC DXCOIL | 7.7475 | 7.6762 | 7.5827 | 7.1129 | 6.0237 | 7.0116 | 5.9307 | 6.9982 | 7.3249 | 6.0406 | 7.0092 | 7.2345 | 6.7897 | 6.8973 | 6.455 | 6.5314
| GUESTROOM224 PTAC DXCOIL | 2.1531 | 2.1226 | 2.1405 | 1.9737 | 1.693 | 2.0232 | 1.6308 | 1.9266 | 2.041 | 1.6882 | 1.9268 | 1.9998 | 1.8647 | 1.9136 | 1.7965 | 1.7841
| GUESTROOM301 PTAC DXCOIL | 2.6961 | 2.7402 | 2.8994 | 2.3601 | 2.1181 | 2.5266 | 2.4082 | 2.199 | 2.3284 | 2.0591 | 2.2168 | 2.3038 | 2.1481 | 2.2475 | 2.1181 | 2.3572
| GUESTROOM302_305 PTAC DXCOIL | 8.0602 | 8.3994 | 8.7465 | 7.8808 | 6.9003 | 7.7186 | 9.0609 | 7.7897 | 7.886 | 7.6515 | 7.9549 | 7.9337 | 7.8747 | 7.9291 | 7.6369 | 9.1545
| GUESTROOM306_308 PTAC DXCOIL | 6.4747 | 6.7586 | 7.0958 | 6.36 | 5.7046 | 6.3671 | 7.8764 | 6.3326 | 6.4864 | 6.4765 | 6.4553 | 6.5371 | 6.4241 | 6.6214 | 6.4382 | 8.0236
| GUESTROOM309_312 PTAC DXCOIL | 8.047 | 8.3869 | 8.7338 | 7.8716 | 6.8915 | 7.7051 | 9.05 | 7.7817 | 7.8736 | 7.6412 | 7.9478 | 7.921 | 7.8676 | 7.9186 | 7.6256 | 9.1353
| GUESTROOM313 PTAC DXCOIL | 2.2725 | 2.364 | 2.5166 | 2.2063 | 1.9502 | 2.257 | 2.4512 | 2.1592 | 2.2011 | 2.1233 | 2.1802 | 2.1888 | 2.1688 | 2.1883 | 2.1158 | 2.4762
| GUESTROOM314 PTAC DXCOIL | 2.2204 | 2.1957 | 2.2787 | 2.0461 | 1.7268 | 2.1701 | 1.6713 | 1.9855 | 2.1078 | 1.7397 | 1.9857 | 2.0511 | 1.9304 | 1.9794 | 1.8797 | 1.9105
| GUESTROOM315_318 PTAC DXCOIL | 8.0038 | 7.9413 | 7.9306 | 7.4012 | 6.3286 | 7.4986 | 6.302 | 7.2795 | 7.7669 | 6.4032 | 7.2946 | 7.6598 | 7.0694 | 7.3168 | 6.8701 | 6.9724
| GUESTROOM319 PTAC DXCOIL | 2.1077 | 2.0819 | 2.0999 | 1.9495 | 1.6917 | 2.0144 | 1.6784 | 1.9152 | 2.0742 | 1.7109 | 1.9185 | 2.0412 | 1.8582 | 1.9516 | 1.8328 | 1.8433
| GUESTROOM320_323 PTAC DXCOIL | 7.9054 | 7.843 | 7.8267 | 7.3033 | 6.2084 | 7.3605 | 6.1816 | 7.1844 | 7.619 | 6.2826 | 7.1991 | 7.5118 | 6.9751 | 7.1763 | 6.7422 | 6.8438
| GUESTROOM324 PTAC DXCOIL | 2.1995 | 2.1711 | 2.225 | 2.0295 | 1.732 | 2.1332 | 1.6845 | 1.9718 | 2.1102 | 1.7472 | 1.9804 | 2.0575 | 1.9169 | 1.9765 | 1.8671 | 1.8592
| GUESTROOM401 PTAC DXCOIL | 3.6256 | 3.7393 | 3.8226 | 3.2037 | 2.5604 | 3.3164 | 2.7405 | 2.9859 | 2.8771 | 2.4788 | 2.9798 | 2.7485 | 2.8277 | 2.6684 | 2.5018 | 2.7781
| GUESTROOM402_405 PTAC DXCOIL | 12.6235 | 13.2234 | 13.5161 | 12.2251 | 8.6207 | 11.5965 | 10.2934 | 12.1086 | 10.4676 | 9.5028 | 12.0654 | 10.0522 | 11.5666 | 9.9971 | 10.3076 | 11.9427
| GUESTROOM406_408 PTAC DXCOIL | 10.1962 | 10.6851 | 10.9637 | 9.9047 | 7.0775 | 9.5201 | 8.8849 | 9.8263 | 8.596 | 7.9648 | 9.8175 | 8.2697 | 9.4375 | 8.2781 | 8.3618 | 9.7573
| GUESTROOM409_412 PTAC DXCOIL | 12.6184 | 13.2193 | 13.5151 | 12.2298 | 8.6233 | 11.602 | 10.2985 | 12.1168 | 10.4756 | 9.5111 | 12.0731 | 10.0595 | 11.5747 | 10.0054 | 10.2963 | 11.9328
| GUESTROOM413 PTAC DXCOIL | 3.4873 | 3.657 | 3.7912 | 3.3643 | 2.4223 | 3.315 | 2.7689 | 3.2952 | 2.9055 | 2.6172 | 3.2846 | 2.7593 | 3.1373 | 2.7447 | 2.7193 | 3.1893
| GUESTROOM414 PTAC DXCOIL | 3.4487 | 3.5112 | 3.6463 | 3.2651 | 2.2083 | 3.2001 | 2.0171 | 3.1934 | 2.7697 | 2.2832 | 3.1579 | 2.5754 | 2.9913 | 2.6519 | 2.7439 | 3.1762
| GUESTROOM415_418 PTAC DXCOIL | 12.5514 | 12.9131 | 13.0471 | 11.9775 | 8.1685 | 11.2878 | 7.5737 | 11.826 | 10.2348 | 8.386 | 11.7572 | 9.6655 | 11.1155 | 9.7715 | 10.4186 | 11.9437
| GUESTROOM419 PTAC DXCOIL | 3.2632 | 3.3226 | 3.3987 | 3.0895 | 2.1047 | 2.9733 | 1.9509 | 3.052 | 2.6646 | 2.1791 | 3.0202 | 2.4991 | 2.9356 | 2.7107 | 2.8501 | 3.3195
| GUESTROOM420_423 PTAC DXCOIL | 12.4834 | 12.8443 | 12.9756 | 11.9095 | 8.1116 | 11.2027 | 7.5054 | 11.7615 | 10.1471 | 8.3167 | 11.6927 | 9.5762 | 11.0522 | 9.735 | 10.404 | 11.9069
| GUESTROOM424 PTAC DXCOIL | 3.4144 | 3.4659 | 3.544 | 3.2286 | 2.2011 | 3.159 | 2.0154 | 3.1682 | 2.7677 | 2.2776 | 3.1439 | 2.5795 | 2.97 | 2.6243 | 2.7188 | 3.1494
| PSZ-HEATCOOL:1_COOLC DXCOIL | 8.6292 | 8.5529 | 8.254 | 8.4135 | 7.5266 | 7.6509 | 6.6122 | 8.0672 | 8.7314 | 7.2381 | 8.0539 | 8.657 | 8.1362 | 8.2962 | 7.6019 | 6.9972
| PSZ-HEATCOOL:10_COOLC DXCOIL | 4.6635 | 4.6824 | 4.6509 | 4.2644 | 3.5574 | 4.133 | 3.7977 | 4.2875 | 4.2715 | 3.6663 | 4.3009 | 4.208 | 4.1656 | 4.052 | 3.8786 | 4.0508
| PSZ-HEATCOOL:11_COOLC DXCOIL | 4.3669 | 4.3817 | 4.4054 | 3.9741 | 3.1798 | 3.8695 | 3.4299 | 3.9966 | 3.8513 | 3.3273 | 4.0073 | 3.7426 | 3.8706 | 3.6312 | 3.5408 | 3.7076
| PSZ-HEATCOOL:12_COOLC DXCOIL | 11.2477 | 11.8438 | 11.794 | 10.4986 | 6.158 | 9.3997 | 4.8518 | 11.4356 | 7.8646 | 6.3078 | 15.3007 | 10.6575 | 17.1901 | 13.2274 | 17.0514 | 17.0965
| PSZ-HEATCOOL:2_COOLC DXCOIL | 18.8476 | 19.3971 | 20.0285 | 18.6672 | 17.4024 | 18.5567 | 15.449 | 17.9333 | 15.7062 | 15.2741 | 18.15 | 15.7136 | 18.2773 | 14.3834 | 18.5875 | 14.8453
| PSZ-HEATCOOL:3_COOLC DXCOIL | 1.2675 | 1.3147 | 1.2763 | 1.2611 | 1.2198 | 1.1678 | 1.1724 | 1.1822 | 1.2428 | 1.12 | 1.1883 | 1.2472 | 1.1981 | 1.2149 | 1.1032 | 1.1027
| PSZ-HEATCOOL:4_COOLC DXCOIL | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 8.5581 | 10.6599 | 10.4022 | 9.7293 | 10.6599 | 10.5319 | 10.6599 | 8.7855 | 10.6599 | 7.3274
| PSZ-HEATCOOL:5_COOLC DXCOIL | 1.1612 | 1.2057 | 1.0668 | 1.065 | 0.88881 | 0.84306 | 0.84353 | 1.021 | 0.83079 | 0.77469 | 1.0159 | 0.83711 | 0.98702 | 0.82504 | 0.79476 | 0.72832
| PSZ-HEATCOOL:6_COOLC DXCOIL | 7.9074 | 7.7648 | 6.9692 | 7.1809 | 5.9016 | 6.084 | 4.879 | 7.1514 | 5.9627 | 5.2312 | 7.1457 | 5.9455 | 6.8573 | 5.6229 | 5.8847 | 4.9567
| PSZ-HEATCOOL:7_COOLC DXCOIL | 31.5166 | 31.1472 | 30.1836 | 30.5079 | 27.237 | 28.511 | 25.7903 | 30.1619 | 31.9991 | 26.5613 | 30.2248 | 31.9451 | 29.834 | 30.1875 | 27.7925 | 26.2873
| PSZ-HEATCOOL:8_COOLC DXCOIL | 3.22 | 3.2197 | 3.1789 | 3.1867 | 2.8775 | 3.0251 | 2.0449 | 3.0159 | 2.2934 | 1.9042 | 3.025 | 2.2618 | 3.0567 | 2.1236 | 2.913 | 1.8752
| PSZ-HEATCOOL:9_COOLC DXCOIL | 9.173 | 8.97 | 7.7245 | 7.8712 | 6.1067 | 6.1885 | 4.4028 | 7.9708 | 5.6683 | 4.9599 | 7.9333 | 5.5508 | 7.7831 | 5.2316 | 5.801 | 4.3756
Heating (kW)
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.19863 | 0.04023 | 0.23883 | 0 | 0.10007 | 0 | 0.29413 | 0.1819 | 0.07503 | 0.61243 | 0.46222 | 0.79759 | 0.76692 | 0.89043 | 1.3394
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.33212 | 0.14821 | 0.33624 | 0 | 0.17317 | 0 | 0.36835 | 0.25454 | 0.18468 | 0.62753 | 0.49196 | 0.78107 | 0.75208 | 0.85541 | 1.2028
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.37792 | 0.18666 | 0.38114 | 0 | 0.21344 | 0.08542 | 0.41554 | 0.30036 | 0.23422 | 0.67753 | 0.54121 | 0.83063 | 0.80255 | 0.90571 | 1.2503
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.29957 | 1.0323 | 0.65609 | 1.1764 | 0.34023 | 0.8103 | 0.56448 | 1.3678 | 1.0716 | 0.95127 | 1.9593 | 1.6119 | 2.3142 | 2.2275 | 2.4847 | 3.3541
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.24897 | 0.10477 | 0.31958 | 0 | 0.17514 | 0.07443 | 0.41001 | 0.29093 | 0.23991 | 0.64646 | 0.50822 | 0.78928 | 0.7566 | 0.85851 | 1.198
| GUESTROOM101 PTAC HEAT COIL | 0.55632 | 0.80396 | 0.67996 | 0.87325 | 0.5786 | 0.7546 | 0.63954 | 0.97934 | 0.84409 | 0.77209 | 1.2749 | 1.0974 | 1.4445 | 1.3857 | 1.5252 | 1.9054
| GUESTROOM102 PTAC HEAT COIL | 0.55632 | 0.82554 | 0.69893 | 0.89448 | 0.5786 | 0.77368 | 0.63954 | 1.001 | 0.86521 | 0.79092 | 1.2984 | 1.1204 | 1.4689 | 1.4102 | 1.5502 | 1.9297
| GUESTROOM103 PTAC HEAT COIL | 0.55632 | 1.0405 | 0.89486 | 1.1052 | 0.5786 | 0.97122 | 0.76029 | 1.2078 | 1.0697 | 0.9673 | 1.5166 | 1.3374 | 1.694 | 1.6373 | 1.7786 | 2.1667
| GUESTROOM104 PTAC HEAT COIL | 0.55632 | 1.0297 | 0.88909 | 1.1012 | 0.5786 | 0.9779 | 0.75512 | 1.205 | 1.0667 | 0.98195 | 1.5112 | 1.3338 | 1.6848 | 1.6283 | 1.7687 | 2.1648
| GUESTROOM105 PTAC HEAT COIL | 0.55632 | 0.81571 | 0.69276 | 0.88972 | 0.5786 | 0.77192 | 0.63954 | 0.99761 | 0.86021 | 0.7863 | 1.2965 | 1.1197 | 1.4659 | 1.4077 | 1.5474 | 1.9371
| GUESTROOM201 PTAC HEAT COIL | 0.69482 | 1.2933 | 0.99197 | 1.2895 | 0.65362 | 1.0163 | 0.858 | 1.3706 | 1.1529 | 1.0792 | 1.7812 | 1.5251 | 2.0104 | 1.9285 | 2.1186 | 2.5769
| GUESTROOM202_205 PTAC HEAT COIL | 2.2253 | 3.2421 | 2.4785 | 3.3812 | 2.3144 | 2.6793 | 2.5582 | 3.7459 | 3.0974 | 3.0508 | 4.8584 | 4.0877 | 5.4672 | 5.1789 | 5.7482 | 7.0008
| GUESTROOM206_208 PTAC HEAT COIL | 1.669 | 2.4941 | 1.8885 | 2.5916 | 1.7358 | 2.0186 | 1.9186 | 2.8859 | 2.3843 | 2.2881 | 3.7821 | 3.1772 | 4.2695 | 4.0464 | 4.4988 | 5.4319
| GUESTROOM209_212 PTAC HEAT COIL | 2.2253 | 3.1671 | 2.4785 | 3.3197 | 2.3144 | 2.6793 | 2.5582 | 3.6862 | 3.0398 | 3.0508 | 4.7829 | 4.015 | 5.3831 | 5.093 | 5.6591 | 6.9049
| GUESTROOM213 PTAC HEAT COIL | 0.57954 | 1.035 | 0.83329 | 1.0662 | 0.5786 | 0.87629 | 0.7544 | 1.1524 | 0.98739 | 0.9438 | 1.4401 | 1.2458 | 1.5969 | 1.5261 | 1.6693 | 1.9871
| GUESTROOM214 PTAC HEAT COIL | 0.55632 | 1.0029 | 0.80574 | 1.0368 | 0.5786 | 0.84951 | 0.7188 | 1.1239 | 0.95815 | 0.91698 | 1.4104 | 1.2181 | 1.566 | 1.495 | 1.6396 | 1.9602
| GUESTROOM215_218 PTAC HEAT COIL | 2.2253 | 2.9377 | 2.4785 | 3.169 | 2.3144 | 2.6793 | 2.5582 | 3.5277 | 2.8029 | 3.0508 | 4.4889 | 3.7236 | 5.0929 | 4.8009 | 5.3754 | 6.6502
| GUESTROOM219 PTAC HEAT COIL | 0.6954 | 0.73442 | 0.66806 | 0.79225 | 0.69293 | 0.64253 | 0.69515 | 0.88192 | 0.57203 | 0.68556 | 1.0303 | 0.83647 | 1.1134 | 1.0146 | 1.1397 | 1.4664
| GUESTROOM220_223 PTAC HEAT COIL | 2.2253 | 3.0318 | 2.4785 | 3.1913 | 2.3144 | 2.6793 | 2.5582 | 3.5608 | 2.911 | 3.0508 | 4.6639 | 3.9033 | 5.2621 | 4.9706 | 5.5433 | 6.8114
| GUESTROOM224 PTAC HEAT COIL | 0.55632 | 0.92438 | 0.72872 | 0.95815 | 0.5786 | 0.77163 | 0.66574 | 1.0475 | 0.88038 | 0.83738 | 1.3409 | 1.1457 | 1.5001 | 1.4283 | 1.5753 | 1.9054
| GUESTROOM301 PTAC HEAT COIL | 0.75438 | 1.3433 | 1.0283 | 1.3394 | 0.69821 | 1.0534 | 0.8974 | 1.4216 | 1.1982 | 1.1251 | 1.8389 | 1.5789 | 2.0708 | 1.9894 | 2.1814 | 2.6328
| GUESTROOM302_305 PTAC HEAT COIL | 2.2253 | 3.3745 | 2.5706 | 3.5252 | 2.3144 | 2.7581 | 2.5582 | 3.9029 | 3.235 | 3.0915 | 5.0319 | 4.2482 | 5.6457 | 5.3584 | 5.9333 | 7.1521
| GUESTROOM306_308 PTAC HEAT COIL | 1.669 | 2.712 | 2.0626 | 2.8143 | 1.7358 | 2.1988 | 1.9406 | 3.1184 | 2.5982 | 2.4689 | 4.0302 | 3.413 | 4.5212 | 4.2981 | 4.7567 | 5.6562
| GUESTROOM309_312 PTAC HEAT COIL | 2.2253 | 3.3566 | 2.5588 | 3.5124 | 2.3144 | 2.7499 | 2.5582 | 3.8927 | 3.2257 | 3.0848 | 5.016 | 4.2334 | 5.6268 | 5.3388 | 5.9128 | 7.129
| GUESTROOM313 PTAC HEAT COIL | 0.65876 | 1.08 | 0.86836 | 1.1124 | 0.63188 | 0.9123 | 0.80814 | 1.2022 | 1.0321 | 0.98947 | 1.4949 | 1.2972 | 1.6534 | 1.583 | 1.7278 | 2.0387
| GUESTROOM314 PTAC HEAT COIL | 0.61935 | 1.0544 | 0.84607 | 1.0891 | 0.59493 | 0.88991 | 0.77822 | 1.179 | 1.0083 | 0.9676 | 1.4715 | 1.2755 | 1.6299 | 1.5583 | 1.7054 | 2.0168
| GUESTROOM315_318 PTAC HEAT COIL | 2.2253 | 3.3001 | 2.5136 | 3.4645 | 2.3144 | 2.7003 | 2.5582 | 3.844 | 3.1702 | 3.0508 | 4.9725 | 4.1958 | 5.581 | 5.2873 | 5.8704 | 7.0915
| GUESTROOM319 PTAC HEAT COIL | 0.55632 | 0.81524 | 0.61963 | 0.85502 | 0.5786 | 0.66983 | 0.63954 | 0.95414 | 0.77207 | 0.76269 | 1.2615 | 1.0552 | 1.4288 | 1.3539 | 1.5088 | 1.8451
| GUESTROOM320_323 PTAC HEAT COIL | 2.2253 | 3.2957 | 2.5157 | 3.462 | 2.3144 | 2.7045 | 2.5582 | 3.8413 | 3.1699 | 3.0508 | 4.9636 | 4.1888 | 5.5688 | 5.2751 | 5.8564 | 7.0762
| GUESTROOM324 PTAC HEAT COIL | 0.58152 | 0.98927 | 0.78208 | 1.0254 | 0.5786 | 0.82689 | 0.72947 | 1.1174 | 0.94475 | 0.9037 | 1.4146 | 1.2156 | 1.5754 | 1.503 | 1.6523 | 1.9703
| GUESTROOM401 PTAC HEAT COIL | 1.2295 | 2.1979 | 1.6868 | 2.3348 | 1.2402 | 1.8419 | 1.5586 | 2.5879 | 2.1709 | 2.041 | 3.3471 | 2.8709 | 3.7918 | 3.6613 | 4.0079 | 4.9392
| GUESTROOM402_405 PTAC HEAT COIL | 4.5589 | 8.227 | 6.2455 | 9.2101 | 4.8426 | 7.186 | 6.1171 | 10.584 | 8.664 | 8.3049 | 13.745 | 11.5251 | 15.6013 | 14.8679 | 16.4768 | 20.9102
| GUESTROOM406_408 PTAC HEAT COIL | 3.6872 | 6.649 | 5.0468 | 7.4243 | 3.9002 | 5.7921 | 4.9518 | 8.534 | 7.0017 | 6.6983 | 11.0884 | 9.3103 | 12.5829 | 11.9993 | 13.294 | 16.793
| GUESTROOM409_412 PTAC HEAT COIL | 4.5574 | 8.2168 | 6.24 | 9.204 | 4.8449 | 7.1834 | 6.1174 | 10.5804 | 8.6613 | 8.3044 | 13.7369 | 11.5179 | 15.5908 | 14.8569 | 16.4651 | 20.8965
| GUESTROOM413 PTAC HEAT COIL | 1.3591 | 2.3092 | 1.8024 | 2.5526 | 1.4287 | 2.0377 | 1.7584 | 2.8951 | 2.4122 | 2.3144 | 3.698 | 3.1415 | 4.1698 | 3.9897 | 4.393 | 5.51
| GUESTROOM414 PTAC HEAT COIL | 1.3363 | 2.2881 | 1.7829 | 2.534 | 1.4063 | 2.0175 | 1.7374 | 2.8759 | 2.3918 | 2.2939 | 3.6799 | 3.1249 | 4.1515 | 3.9696 | 4.3755 | 5.4918
| GUESTROOM415_418 PTAC HEAT COIL | 4.5474 | 8.2067 | 6.241 | 9.2076 | 4.8366 | 7.1838 | 6.1171 | 10.5837 | 8.6584 | 8.303 | 13.7445 | 11.5304 | 15.5982 | 14.8564 | 16.4765 | 20.9117
| GUESTROOM419 PTAC HEAT COIL | 1.2074 | 2.2137 | 1.678 | 2.4851 | 1.286 | 1.934 | 1.6361 | 2.8576 | 2.3408 | 2.2324 | 3.7228 | 3.1299 | 4.2323 | 4.0415 | 4.4751 | 5.6906
| GUESTROOM420_423 PTAC HEAT COIL | 4.5261 | 8.174 | 6.214 | 9.1749 | 4.8172 | 7.1566 | 6.0932 | 10.5497 | 8.627 | 8.2744 | 13.7035 | 11.4919 | 15.5535 | 14.8117 | 16.4298 | 20.8607
| GUESTROOM424 PTAC HEAT COIL | 1.3152 | 2.2592 | 1.7623 | 2.5092 | 1.3945 | 1.9994 | 1.7267 | 2.8539 | 2.3711 | 2.2777 | 3.6512 | 3.097 | 4.1199 | 3.9358 | 4.3419 | 5.4547
| REARSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.11069 | 0 | 0.14397 | 0 | 0 | 0 | 0.19765 | 0.08801 | 0 | 0.5026 | 0.35723 | 0.68274 | 0.65325 | 0.77193 | 1.2035
| REARSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.22001 | 0.03512 | 0.22272 | 0 | 0.06108 | 0 | 0.25363 | 0.14313 | 0.0762 | 0.50519 | 0.37407 | 0.64953 | 0.61856 | 0.71864 | 1.0511
| REARSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.24923 | 0.06428 | 0.25419 | 0 | 0.08664 | 0 | 0.28734 | 0.17409 | 0.1096 | 0.5395 | 0.40734 | 0.68454 | 0.65509 | 0.75605 | 1.0876
| REARSTAIRSFLR4 UNIT HEATER COIL | 0.13824 | 0.87083 | 0.50338 | 1.014 | 0.17011 | 0.65313 | 0.4021 | 1.2046 | 0.911 | 0.79586 | 1.7895 | 1.4433 | 2.1406 | 2.0517 | 2.3093 | 3.1719
| REARSTORAGEFLR1 UNIT HEATER COIL | 0 | 0.06178 | 0 | 0.05692 | 0 | 0 | 0 | 0.0694 | 0 | 0 | 0.28344 | 0.20694 | 0.40758 | 0.40569 | 0.47329 | 0.73662
| REARSTORAGEFLR2 UNIT HEATER COIL | 0 | 0.20135 | 0.06316 | 0.17551 | 0 | 0.06061 | 0 | 0.17572 | 0.11172 | 0.04394 | 0.34971 | 0.27501 | 0.45284 | 0.44581 | 0.50486 | 0.69967
| REARSTORAGEFLR3 UNIT HEATER COIL | 0 | 0.23251 | 0.09065 | 0.20686 | 0 | 0.08905 | 0 | 0.20761 | 0.14154 | 0.08524 | 0.3866 | 0.31058 | 0.49115 | 0.48498 | 0.54416 | 0.73713
| REARSTORAGEFLR4 UNIT HEATER COIL | 0.11414 | 0.62717 | 0.37527 | 0.68169 | 0.12121 | 0.447 | 0.27698 | 0.77601 | 0.61248 | 0.509 | 1.151 | 0.96609 | 1.3769 | 1.3528 | 1.4902 | 1.954
| PSZ-HEATCOOL:1_HEATC | 24.5112 | 24.9604 | 23.0552 | 24.0182 | 21.6267 | 20.7384 | 19.1786 | 23.9573 | 21.3347 | 21.0636 | 12.7897 | 11.3512 | 13.0405 | 11.8976 | 12.1924 | 12.406
| PSZ-HEATCOOL:10_HEATC | 11.5443 | 6.5633 | 6.5845 | 6.3174 | 10.1137 | 6.0986 | 10.9774 | 6.5045 | 5.8155 | 5.973 | 6.8179 | 6.0314 | 6.9771 | 6.4683 | 6.9192 | 7.9056
| PSZ-HEATCOOL:11_HEATC | 5.6522 | 6.0983 | 6.2506 | 5.8771 | 4.9444 | 5.7606 | 5.4363 | 6.0525 | 5.3356 | 5.5089 | 6.3645 | 5.5008 | 6.5177 | 5.9617 | 6.4736 | 7.4366
| PSZ-HEATCOOL:12_HEATC | 10.9057 | 12.0756 | 13.9232 | 11.3252 | 7.5813 | 12.4657 | 7.411 | 12.363 | 9.9222 | 9.5912 | 16.2201 | 13.3893 | 18.5176 | 17.5239 | 19.5752 | 25.743
| PSZ-HEATCOOL:2_HEATC | 24.1087 | 29.8367 | 26.7217 | 30.6199 | 23.8576 | 26.6193 | 28.3299 | 32.8227 | 27.7409 | 29.9627 | 37.2761 | 31.7423 | 39.7879 | 36.9618 | 40.6886 | 52.3024
| PSZ-HEATCOOL:3_HEATC | 3.7056 | 1.819 | 1.7028 | 1.6873 | 1.688 | 1.4984 | 1.6275 | 1.633 | 1.4197 | 1.5333 | 1.6137 | 1.4221 | 1.6145 | 1.4631 | 1.4555 | 1.5068
| PSZ-HEATCOOL:4_HEATC | 16.6197 | 21.9403 | 18.5109 | 23.6679 | 17.2852 | 20.0108 | 19.1295 | 26.3467 | 21.2685 | 22.7848 | 30.7783 | 25.3309 | 33.2623 | 30.3656 | 34.0465 | 42.4638
| PSZ-HEATCOOL:5_HEATC | 1.4189 | 1.5812 | 1.4042 | 1.4918 | 1.3714 | 1.2415 | 1.3465 | 1.4756 | 1.1925 | 1.3086 | 1.545 | 1.2752 | 1.5936 | 1.4067 | 1.4513 | 1.6116
| PSZ-HEATCOOL:6_HEATC | 14.5727 | 9.78 | 8.9566 | 10.0008 | 8.4615 | 9.0846 | 8.5063 | 10.4278 | 9.4387 | 9.3874 | 11.3351 | 10.241 | 11.8379 | 11.2306 | 11.8412 | 13.4256
| PSZ-HEATCOOL:7_HEATC | 78.4442 | 79.7741 | 77.5247 | 79.9542 | 76.9657 | 77.2868 | 74.8187 | 80.4991 | 78.2339 | 77.322 | 81.833 | 79.3238 | 45.0238 | 43.5989 | 44.6062 | 46.7318
| PSZ-HEATCOOL:8_HEATC | 5.2107 | 6.0723 | 5.1412 | 6.4708 | 4.7127 | 5.3787 | 4.8958 | 7.0131 | 5.8345 | 5.8386 | 8.1524 | 6.8544 | 8.8154 | 8.1313 | 8.8839 | 10.8779
| PSZ-HEATCOOL:9_HEATC | 10.0644 | 11.1969 | 9.8406 | 10.8985 | 8.7302 | 9.2978 | 7.9885 | 11.1904 | 9.4607 | 9.2573 | 12.1037 | 10.2629 | 12.6056 | 11.3675 | 12.0309 | 13.5387
HVAC Efficiency
Air Conditioning (COP)
| GUESTROOM101 PTAC DXCOIL | 3.6 | 3.6 | 3.62 | 3.62 | 3.7 | 3.66 | 3.7 | 3.61 | 3.7 | 3.7 | 3.61 | 3.7 | 3.62 | 3.7 | 3.68 | 3.7
| GUESTROOM102 PTAC DXCOIL | 3.6 | 3.6 | 3.62 | 3.63 | 3.7 | 3.66 | 3.7 | 3.61 | 3.7 | 3.7 | 3.61 | 3.7 | 3.63 | 3.7 | 3.69 | 3.7
| GUESTROOM103 PTAC DXCOIL | 3.61 | 3.6 | 3.63 | 3.64 | 3.7 | 3.67 | 3.7 | 3.62 | 3.7 | 3.7 | 3.62 | 3.7 | 3.64 | 3.7 | 3.69 | 3.7
| GUESTROOM104 PTAC DXCOIL | 3.63 | 3.63 | 3.66 | 3.65 | 3.7 | 3.7 | 3.7 | 3.63 | 3.7 | 3.7 | 3.63 | 3.7 | 3.65 | 3.7 | 3.69 | 3.7
| GUESTROOM105 PTAC DXCOIL | 3.63 | 3.63 | 3.66 | 3.66 | 3.7 | 3.7 | 3.7 | 3.64 | 3.7 | 3.7 | 3.64 | 3.7 | 3.66 | 3.7 | 3.7 | 3.7
| GUESTROOM201 PTAC DXCOIL | 3.49 | 3.48 | 3.46 | 3.61 | 3.67 | 3.57 | 3.59 | 3.63 | 3.62 | 3.69 | 3.63 | 3.62 | 3.66 | 3.64 | 3.67 | 3.6
| GUESTROOM202_205 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.05 | 3.05 | 3.05 | 3.01 | 3.05 | 3.05 | 3.01 | 3.05 | 3.03 | 3.05 | 3.05 | 3.05
| GUESTROOM206_208 PTAC DXCOIL | 3 | 3 | 3.02 | 3.03 | 3.05 | 3.05 | 3.05 | 3.01 | 3.05 | 3.05 | 3.02 | 3.05 | 3.03 | 3.05 | 3.05 | 3.05
| GUESTROOM209_212 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.05 | 3.05 | 3.05 | 3.01 | 3.05 | 3.05 | 3.01 | 3.05 | 3.02 | 3.05 | 3.05 | 3.05
| GUESTROOM213 PTAC DXCOIL | 3.59 | 3.56 | 3.56 | 3.64 | 3.7 | 3.67 | 3.6 | 3.64 | 3.68 | 3.69 | 3.63 | 3.68 | 3.65 | 3.68 | 3.7 | 3.6
| GUESTROOM214 PTAC DXCOIL | 3.62 | 3.63 | 3.66 | 3.68 | 3.7 | 3.69 | 3.7 | 3.67 | 3.7 | 3.7 | 3.67 | 3.7 | 3.69 | 3.7 | 3.7 | 3.7
| GUESTROOM215_218 PTAC DXCOIL | 3.02 | 3.02 | 3.04 | 3.04 | 3.05 | 3.05 | 3.05 | 3.03 | 3.05 | 3.05 | 3.03 | 3.05 | 3.05 | 3.05 | 3.05 | 3.05
| GUESTROOM219 PTAC DXCOIL | 3.56 | 3.58 | 3.57 | 3.61 | 3.66 | 3.58 | 3.67 | 3.57 | 3.53 | 3.66 | 3.58 | 3.54 | 3.62 | 3.57 | 3.62 | 3.61
| GUESTROOM220_223 PTAC DXCOIL | 3.01 | 3.01 | 3.04 | 3.03 | 3.05 | 3.05 | 3.05 | 3.02 | 3.05 | 3.05 | 3.02 | 3.05 | 3.04 | 3.05 | 3.05 | 3.05
| GUESTROOM224 PTAC DXCOIL | 3.62 | 3.64 | 3.67 | 3.68 | 3.7 | 3.7 | 3.7 | 3.66 | 3.7 | 3.7 | 3.67 | 3.7 | 3.69 | 3.7 | 3.7 | 3.7
| GUESTROOM301 PTAC DXCOIL | 3.49 | 3.48 | 3.46 | 3.61 | 3.68 | 3.56 | 3.6 | 3.63 | 3.62 | 3.69 | 3.63 | 3.63 | 3.66 | 3.64 | 3.68 | 3.61
| GUESTROOM302_305 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.05 | 3.05 | 3.05 | 3.01 | 3.05 | 3.05 | 3.01 | 3.05 | 3.03 | 3.05 | 3.05 | 3.05
| GUESTROOM306_308 PTAC DXCOIL | 3.01 | 3.01 | 3.03 | 3.03 | 3.05 | 3.05 | 3.05 | 3.02 | 3.05 | 3.05 | 3.02 | 3.05 | 3.03 | 3.05 | 3.05 | 3.05
| GUESTROOM309_312 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.05 | 3.05 | 3.05 | 3.01 | 3.05 | 3.05 | 3.01 | 3.05 | 3.03 | 3.05 | 3.05 | 3.05
| GUESTROOM313 PTAC DXCOIL | 3.58 | 3.55 | 3.54 | 3.63 | 3.7 | 3.64 | 3.58 | 3.63 | 3.65 | 3.68 | 3.62 | 3.66 | 3.64 | 3.66 | 3.68 | 3.58
| GUESTROOM314 PTAC DXCOIL | 3.61 | 3.62 | 3.63 | 3.69 | 3.7 | 3.66 | 3.7 | 3.67 | 3.68 | 3.7 | 3.68 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
| GUESTROOM315_318 PTAC DXCOIL | 3.01 | 3.01 | 3.04 | 3.04 | 3.05 | 3.05 | 3.05 | 3.03 | 3.05 | 3.05 | 3.03 | 3.05 | 3.04 | 3.05 | 3.05 | 3.05
| GUESTROOM319 PTAC DXCOIL | 3.63 | 3.64 | 3.67 | 3.68 | 3.7 | 3.7 | 3.7 | 3.66 | 3.69 | 3.7 | 3.67 | 3.7 | 3.69 | 3.7 | 3.7 | 3.7
| GUESTROOM320_323 PTAC DXCOIL | 3.01 | 3.01 | 3.04 | 3.03 | 3.05 | 3.05 | 3.05 | 3.02 | 3.05 | 3.05 | 3.03 | 3.05 | 3.04 | 3.05 | 3.05 | 3.05
| GUESTROOM324 PTAC DXCOIL | 3.61 | 3.63 | 3.65 | 3.69 | 3.7 | 3.67 | 3.7 | 3.67 | 3.68 | 3.7 | 3.68 | 3.69 | 3.69 | 3.7 | 3.7 | 3.7
| GUESTROOM401 PTAC DXCOIL | 3.22 | 3.19 | 3.21 | 3.35 | 3.55 | 3.35 | 3.5 | 3.39 | 3.47 | 3.58 | 3.39 | 3.5 | 3.45 | 3.52 | 3.57 | 3.49
| GUESTROOM402_405 PTAC DXCOIL | 2.97 | 2.98 | 3.02 | 3 | 3.05 | 3.05 | 3.05 | 2.99 | 3.05 | 3.05 | 2.99 | 3.05 | 3 | 3.05 | 3.04 | 3.05
| GUESTROOM406_408 PTAC DXCOIL | 2.98 | 2.98 | 3.02 | 3 | 3.05 | 3.05 | 3.05 | 2.99 | 3.05 | 3.05 | 2.99 | 3.05 | 3 | 3.05 | 3.04 | 3.05
| GUESTROOM409_412 PTAC DXCOIL | 2.97 | 2.98 | 3.02 | 3 | 3.05 | 3.05 | 3.05 | 2.99 | 3.05 | 3.05 | 2.99 | 3.05 | 3 | 3.05 | 3.04 | 3.05
| GUESTROOM413 PTAC DXCOIL | 3.22 | 3.18 | 3.19 | 3.28 | 3.59 | 3.35 | 3.5 | 3.29 | 3.46 | 3.54 | 3.29 | 3.5 | 3.34 | 3.5 | 3.5 | 3.38
| GUESTROOM414 PTAC DXCOIL | 3.23 | 3.22 | 3.23 | 3.31 | 3.65 | 3.38 | 3.7 | 3.31 | 3.5 | 3.63 | 3.32 | 3.55 | 3.37 | 3.53 | 3.49 | 3.38
| GUESTROOM415_418 PTAC DXCOIL | 2.98 | 2.98 | 3.02 | 3 | 3.05 | 3.05 | 3.05 | 2.99 | 3.05 | 3.05 | 2.99 | 3.05 | 3 | 3.05 | 3.03 | 3.05
| GUESTROOM419 PTAC DXCOIL | 3.27 | 3.26 | 3.29 | 3.35 | 3.68 | 3.44 | 3.7 | 3.34 | 3.53 | 3.66 | 3.35 | 3.57 | 3.38 | 3.51 | 3.45 | 3.35
| GUESTROOM420_423 PTAC DXCOIL | 2.98 | 2.98 | 3.02 | 3 | 3.05 | 3.05 | 3.05 | 2.99 | 3.05 | 3.05 | 2.99 | 3.05 | 2.99 | 3.05 | 3.03 | 3.05
| GUESTROOM424 PTAC DXCOIL | 3.24 | 3.23 | 3.26 | 3.32 | 3.65 | 3.39 | 3.7 | 3.32 | 3.5 | 3.63 | 3.32 | 3.55 | 3.38 | 3.54 | 3.49 | 3.39
| PSZ-HEATCOOL:1_COOLC DXCOIL | 4.02 | 4.03 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:10_COOLC DXCOIL | 3.87 | 3.88 | 3.98 | 3.94 | 4.04 | 4.04 | 4.04 | 3.9 | 4.04 | 4.04 | 3.91 | 4.04 | 3.95 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:11_COOLC DXCOIL | 3.85 | 3.86 | 3.97 | 3.92 | 4.04 | 4.04 | 4.04 | 3.88 | 4.04 | 4.04 | 3.89 | 4.04 | 3.93 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:12_COOLC DXCOIL | 3.65 | 3.67 | 3.84 | 3.72 | 3.82 | 3.99 | 4.04 | 3.69 | 4.04 | 4.04 | 3.69 | 4.04 | 3.71 | 4.04 | 3.78 | 4.01
| PSZ-HEATCOOL:2_COOLC DXCOIL | 3.65 | 3.45 | 3.45 | 3.65 | 3.67 | 3.65 | 3.91 | 3.65 | 3.84 | 3.81 | 3.65 | 3.84 | 3.65 | 3.9 | 3.65 | 4.01
| PSZ-HEATCOOL:3_COOLC DXCOIL | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:4_COOLC DXCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.83 | 3.65 | 3.7 | 3.72 | 3.65 | 3.69 | 3.65 | 3.81 | 3.65 | 4.04
| PSZ-HEATCOOL:5_COOLC DXCOIL | 3.8 | 3.81 | 3.87 | 3.86 | 4.04 | 3.98 | 4.04 | 3.82 | 4.04 | 4.04 | 3.83 | 4.04 | 3.86 | 4.04 | 3.96 | 4.04
| PSZ-HEATCOOL:6_COOLC DXCOIL | 3.65 | 3.67 | 3.76 | 3.73 | 3.85 | 3.88 | 4 | 3.7 | 4.04 | 3.96 | 3.71 | 4.04 | 3.75 | 4.04 | 3.88 | 4.04
| PSZ-HEATCOOL:7_COOLC DXCOIL | 3.63 | 3.64 | 3.69 | 3.68 | 3.75 | 3.77 | 3.77 | 3.66 | 3.73 | 3.77 | 3.67 | 3.73 | 3.69 | 3.73 | 3.76 | 3.77
| PSZ-HEATCOOL:8_COOLC DXCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.9 | 3.65 | 4 | 3.98 | 3.65 | 4.01 | 3.65 | 4.04 | 3.65 | 4.04
| PSZ-HEATCOOL:9_COOLC DXCOIL | 3.65 | 3.66 | 3.74 | 3.71 | 3.83 | 3.85 | 3.98 | 3.65 | 4.04 | 3.93 | 3.65 | 4.04 | 3.66 | 4.04 | 3.82 | 4.04
Heating Efficiency (%)
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-HEATCOOL:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:10_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:11_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:12_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:9_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| All GuestRoom & UnitHeater systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:10_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:11_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:12_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:7_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:9_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| FRONTSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.05
| FRONTSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
| FRONTSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
| FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.05 | 0.04 | 0.03 | 0.07 | 0.07 | 0.08 | 0.09 | 0.09 | 0.11
| FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
| GUESTROOM101 PTACFAN | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.11 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.1
| GUESTROOM102 PTACFAN | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.11 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.1
| GUESTROOM103 PTACFAN | 0.1 | 0.11 | 0.11 | 0.1 | 0.1 | 0.1 | 0.11 | 0.1 | 0.1 | 0.09 | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 0.1
| GUESTROOM104 PTACFAN | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.09 | 0.07 | 0.09 | 0.09 | 0.07 | 0.09 | 0.09 | 0.09 | 0.08 | 0.08 | 0.07
| GUESTROOM105 PTACFAN | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 0.09 | 0.08 | 0.09 | 0.1 | 0.08 | 0.09 | 0.1 | 0.09 | 0.09 | 0.08 | 0.08
| GUESTROOM201 PTACFAN | 0.15 | 0.16 | 0.17 | 0.14 | 0.13 | 0.15 | 0.15 | 0.13 | 0.14 | 0.13 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.14
| GUESTROOM202_205 PTACFAN | 0.42 | 0.43 | 0.48 | 0.43 | 0.42 | 0.46 | 0.55 | 0.42 | 0.47 | 0.46 | 0.43 | 0.48 | 0.44 | 0.48 | 0.46 | 0.55
| GUESTROOM206_208 PTACFAN | 0.33 | 0.35 | 0.38 | 0.35 | 0.34 | 0.37 | 0.46 | 0.34 | 0.38 | 0.38 | 0.35 | 0.38 | 0.36 | 0.39 | 0.38 | 0.47
| GUESTROOM209_212 PTACFAN | 0.4 | 0.42 | 0.46 | 0.42 | 0.41 | 0.45 | 0.53 | 0.4 | 0.46 | 0.45 | 0.41 | 0.46 | 0.43 | 0.46 | 0.45 | 0.53
| GUESTROOM213 PTACFAN | 0.12 | 0.12 | 0.14 | 0.12 | 0.11 | 0.13 | 0.14 | 0.12 | 0.13 | 0.12 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.14
| GUESTROOM214 PTACFAN | 0.12 | 0.12 | 0.13 | 0.12 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.11
| GUESTROOM215_218 PTACFAN | 0.45 | 0.45 | 0.48 | 0.45 | 0.41 | 0.47 | 0.4 | 0.43 | 0.49 | 0.41 | 0.43 | 0.49 | 0.43 | 0.46 | 0.43 | 0.44
| GUESTROOM219 PTACFAN | 0.14 | 0.14 | 0.15 | 0.14 | 0.13 | 0.15 | 0.13 | 0.14 | 0.16 | 0.13 | 0.14 | 0.16 | 0.14 | 0.15 | 0.14 | 0.14
| GUESTROOM220_223 PTACFAN | 0.41 | 0.41 | 0.44 | 0.4 | 0.36 | 0.42 | 0.36 | 0.38 | 0.44 | 0.36 | 0.39 | 0.44 | 0.39 | 0.42 | 0.39 | 0.39
| GUESTROOM224 PTACFAN | 0.12 | 0.12 | 0.13 | 0.12 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.11
| GUESTROOM301 PTACFAN | 0.15 | 0.16 | 0.18 | 0.14 | 0.13 | 0.15 | 0.15 | 0.13 | 0.14 | 0.12 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.14
| GUESTROOM302_305 PTACFAN | 0.42 | 0.43 | 0.48 | 0.44 | 0.42 | 0.47 | 0.55 | 0.42 | 0.48 | 0.46 | 0.43 | 0.48 | 0.44 | 0.48 | 0.46 | 0.55
| GUESTROOM306_308 PTACFAN | 0.34 | 0.36 | 0.4 | 0.36 | 0.34 | 0.38 | 0.48 | 0.35 | 0.39 | 0.39 | 0.36 | 0.39 | 0.37 | 0.4 | 0.39 | 0.48
| GUESTROOM309_312 PTACFAN | 0.42 | 0.43 | 0.48 | 0.44 | 0.42 | 0.47 | 0.55 | 0.42 | 0.48 | 0.46 | 0.43 | 0.48 | 0.44 | 0.48 | 0.46 | 0.55
| GUESTROOM313 PTACFAN | 0.12 | 0.13 | 0.14 | 0.13 | 0.12 | 0.14 | 0.15 | 0.12 | 0.13 | 0.13 | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.15
| GUESTROOM314 PTACFAN | 0.12 | 0.12 | 0.14 | 0.12 | 0.1 | 0.13 | 0.1 | 0.12 | 0.13 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.12
| GUESTROOM315_318 PTACFAN | 0.43 | 0.43 | 0.46 | 0.43 | 0.38 | 0.45 | 0.38 | 0.41 | 0.47 | 0.39 | 0.41 | 0.46 | 0.41 | 0.44 | 0.42 | 0.42
| GUESTROOM319 PTACFAN | 0.12 | 0.12 | 0.12 | 0.11 | 0.1 | 0.12 | 0.1 | 0.11 | 0.13 | 0.1 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.11
| GUESTROOM320_323 PTACFAN | 0.42 | 0.42 | 0.46 | 0.42 | 0.38 | 0.44 | 0.37 | 0.4 | 0.46 | 0.38 | 0.4 | 0.45 | 0.41 | 0.43 | 0.41 | 0.41
| GUESTROOM324 PTACFAN | 0.12 | 0.12 | 0.13 | 0.12 | 0.1 | 0.13 | 0.1 | 0.11 | 0.13 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11
| GUESTROOM401 PTACFAN | 0.2 | 0.2 | 0.23 | 0.18 | 0.15 | 0.2 | 0.17 | 0.16 | 0.17 | 0.15 | 0.16 | 0.17 | 0.16 | 0.16 | 0.15 | 0.17
| GUESTROOM402_405 PTACFAN | 0.59 | 0.63 | 0.73 | 0.63 | 0.52 | 0.7 | 0.62 | 0.6 | 0.63 | 0.57 | 0.6 | 0.61 | 0.59 | 0.6 | 0.59 | 0.72
| GUESTROOM406_408 PTACFAN | 0.49 | 0.52 | 0.6 | 0.52 | 0.43 | 0.58 | 0.54 | 0.49 | 0.52 | 0.48 | 0.5 | 0.5 | 0.49 | 0.5 | 0.49 | 0.59
| GUESTROOM409_412 PTACFAN | 0.59 | 0.63 | 0.73 | 0.63 | 0.52 | 0.7 | 0.62 | 0.6 | 0.63 | 0.57 | 0.6 | 0.61 | 0.6 | 0.6 | 0.59 | 0.72
| GUESTROOM413 PTACFAN | 0.17 | 0.18 | 0.21 | 0.18 | 0.15 | 0.2 | 0.17 | 0.17 | 0.18 | 0.16 | 0.17 | 0.17 | 0.17 | 0.17 | 0.16 | 0.19
| GUESTROOM414 PTACFAN | 0.17 | 0.18 | 0.21 | 0.17 | 0.13 | 0.19 | 0.12 | 0.16 | 0.17 | 0.14 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.19
| GUESTROOM415_418 PTACFAN | 0.6 | 0.62 | 0.71 | 0.61 | 0.49 | 0.68 | 0.46 | 0.58 | 0.62 | 0.51 | 0.58 | 0.58 | 0.57 | 0.59 | 0.59 | 0.72
| GUESTROOM419 PTACFAN | 0.16 | 0.16 | 0.19 | 0.16 | 0.13 | 0.18 | 0.12 | 0.15 | 0.16 | 0.13 | 0.15 | 0.15 | 0.15 | 0.16 | 0.16 | 0.2
| GUESTROOM420_423 PTACFAN | 0.59 | 0.61 | 0.7 | 0.61 | 0.48 | 0.68 | 0.45 | 0.58 | 0.61 | 0.5 | 0.58 | 0.58 | 0.56 | 0.59 | 0.59 | 0.72
| GUESTROOM424 PTACFAN | 0.17 | 0.17 | 0.2 | 0.17 | 0.13 | 0.19 | 0.12 | 0.16 | 0.17 | 0.14 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.19
| REARSTAIRSFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.02 | 0.01 | 0.02 | 0.03 | 0.03 | 0.04
| REARSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.04
| REARSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.04
| REARSTAIRSFLR4 UNIT HEATERFAN | 0 | 0.03 | 0.02 | 0.04 | 0.01 | 0.02 | 0.01 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.07 | 0.08 | 0.08 | 0.11
| REARSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02
| REARSTORAGEFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
| REARSTORAGEFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.03
| REARSTORAGEFLR4 UNIT HEATERFAN | 0 | 0.02 | 0.01 | 0.02 | 0 | 0.02 | 0.01 | 0.03 | 0.02 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
| PSZ-HEATCOOL:1_FAN | 0.51 | 0.52 | 0.5 | 0.51 | 0.45 | 0.46 | 0.4 | 0.49 | 0.53 | 0.44 | 0.49 | 0.52 | 0.49 | 0.5 | 0.46 | 0.42
| PSZ-HEATCOOL:10_FAN | 0.24 | 0.25 | 0.27 | 0.24 | 0.21 | 0.25 | 0.23 | 0.23 | 0.26 | 0.22 | 0.23 | 0.25 | 0.24 | 0.24 | 0.23 | 0.24
| PSZ-HEATCOOL:11_FAN | 0.22 | 0.23 | 0.25 | 0.22 | 0.19 | 0.23 | 0.21 | 0.21 | 0.23 | 0.2 | 0.21 | 0.23 | 0.21 | 0.22 | 0.21 | 0.22
| PSZ-HEATCOOL:12_FAN | 0.45 | 0.49 | 0.6 | 0.46 | 0.31 | 0.55 | 0.29 | 0.49 | 0.48 | 0.38 | 0.65 | 0.64 | 0.75 | 0.8 | 0.81 | 1.03
| PSZ-HEATCOOL:2_FAN | 0.76 | 0.78 | 0.81 | 0.75 | 0.72 | 0.75 | 0.84 | 0.72 | 0.8 | 0.75 | 0.73 | 0.8 | 0.74 | 0.78 | 0.75 | 0.9
| PSZ-HEATCOOL:3_FAN | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.08 | 0.07 | 0.07 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07
| PSZ-HEATCOOL:4_FAN | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.45 | 0.43 | 0.43 | 0.45 | 0.43 | 0.43 | 0.43 | 0.44
| PSZ-HEATCOOL:5_FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.04
| PSZ-HEATCOOL:6_FAN | 0.32 | 0.32 | 0.32 | 0.32 | 0.3 | 0.32 | 0.29 | 0.31 | 0.36 | 0.3 | 0.31 | 0.36 | 0.31 | 0.34 | 0.31 | 0.3
| PSZ-HEATCOOL:7_FAN | 1.65 | 1.65 | 1.68 | 1.69 | 1.62 | 1.72 | 1.56 | 1.63 | 1.93 | 1.6 | 1.66 | 1.93 | 1.66 | 1.82 | 1.67 | 1.59
| PSZ-HEATCOOL:8_FAN | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.11 | 0.12 | 0.13 | 0.11 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.11
| PSZ-HEATCOOL:9_FAN | 0.37 | 0.37 | 0.35 | 0.34 | 0.31 | 0.32 | 0.25 | 0.32 | 0.34 | 0.27 | 0.32 | 0.34 | 0.32 | 0.32 | 0.29 | 0.26
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.079041 | 0.10819 | 0.089002 | 0.1009 | 0.12387 | 0.094666 | 0.14494 | 0.068913 | 0.037251 | 0.07166 | 0.097912 | 0.037253 | 0.054556 | 0.07174 | 0.05487 | 0.091373
| Total Cost ($/m2) | 14.52 | 18.41 | 15.15 | 15.8 | 17.41 | 14.84 | 19.38 | 10.71 | 5.53 | 9.8 | 15.34 | 5.5 | 8.94 | 10.8 | 8.96 | 16.96
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011457 | 0.0081729 | 0.0085316 | 0.010563 | 0.0084185 | 0.0080584 | 0.0084276 | 0.0099809 | 0.0071406 | 0.0083123 | 0.0087584 | 0.0071382 | 0.0079456 | 0.0085967 | 0.0079436 | 0.0041721
| Total Cost ($/m2) | 1.65 | 1.58 | 1.48 | 2.51 | 1.65 | 1.63 | 2.08 | 2.95 | 1.85 | 2.45 | 3.02 | 2.19 | 3.15 | 3.15 | 3.65 | 2.54
Total Utility Costs
| Cost Intensity ($/m2) | 16.17 | 19.99 | 16.63 | 18.31 | 19.06 | 16.47 | 21.46 | 13.65 | 7.38 | 12.25 | 18.36 | 7.69 | 12.09 | 13.95 | 12.62 | 19.5
Energy - End Uses
Electricity (kWh)
| Heating | 152.7778 | 12016.6667 | 5241.6667 | 21813.8889 | 727.7778 | 8575 | 7919.4444 | 45655.5556 | 24544.4444 | 32380.5556 | 70005.5556 | 44725 | 104505.5556 | 76930.5556 | 132058.3333 | 225394.4444
| Cooling | 255144.4444 | 192038.8889 | 195094.4444 | 130944.4444 | 93344.4444 | 141938.8889 | 61633.3333 | 105316.6667 | 92438.8889 | 49072.2222 | 85122.2222 | 69738.8889 | 78255.5556 | 51075 | 49858.3333 | 42130.5556
| Interior Lighting | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889
| Exterior Lighting | 10847.2222 | 10827.7778 | 10825 | 10844.4444 | 10841.6667 | 10830.5556 | 10819.4444 | 10830.5556 | 10827.7778 | 10813.8889 | 10816.6667 | 10816.6667 | 10825 | 10811.1111 | 10808.3333 | 10744.4444
| Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 70133.3333 | 67236.1111 | 70997.2222 | 64100 | 58211.1111 | 67136.1111 | 55322.2222 | 60872.2222 | 66894.4444 | 55591.6667 | 61813.8889 | 66452.7778 | 63347.2222 | 64511.1111 | 61969.4444 | 65780.5556
| Pumps | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 737177.7778 | 683016.6667 | 683058.3333 | 628600 | 564027.7778 | 629377.7778 | 536594.4444 | 623575 | 595602.7778 | 548755.5556 | 628655.5556 | 592636.1111 | 657830.5556 | 604227.7778 | 655594.4444 | 744947.2222
Gas (MJ)
| Heating | 8160 | 127030 | 93050 | 229170 | 77120 | 154370 | 217040 | 402190 | 270670 | 369070 | 549590 | 400130 | 713310 | 582660 | 893530 | 1401770
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 380690 | 458620 | 413880 | 533690 | 519100 | 467800 | 583290 | 592660 | 581480 | 623370 | 644420 | 641740 | 689170 | 697300 | 762990 | 852320
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 578330 | 775120 | 696410 | 952340 | 785700 | 811650 | 989810 | 1184330 | 1041630 | 1181920 | 1383490 | 1231350 | 1591960 | 1469440 | 1846010 | 2443570
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3232170 | 3233990 | 3155420 | 3215300 | 2816190 | 3077410 | 2921550 | 3429190 | 3185800 | 3157440 | 3646650 | 3364840 | 3960150 | 3644660 | 4206140 | 5125380
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.13703 | 10.7784 | 4.7015 | 19.566 | 0.65278 | 7.6914 | 7.1034 | 40.9509 | 22.0152 | 29.0438 | 62.7917 | 40.1162 | 93.7365 | 69.0031 | 118.4501 | 202.1681
| Cooling (elec) | 228.8525 | 172.2498 | 174.9905 | 117.451 | 83.7255 | 127.3125 | 55.2822 | 94.4641 | 82.9133 | 44.0155 | 76.3506 | 62.5525 | 70.1915 | 45.8119 | 44.7206 | 37.7891
| Interior Lighting (elec) | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531
| Exterior Lighting (elec) | 9.7294 | 9.712 | 9.7095 | 9.727 | 9.7245 | 9.7145 | 9.7045 | 9.7145 | 9.712 | 9.6995 | 9.702 | 9.702 | 9.7095 | 9.6971 | 9.6946 | 9.6373
| Interior Equipment (elec) | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 62.9063 | 60.3076 | 63.6811 | 57.4947 | 52.2126 | 60.2179 | 49.6214 | 54.5995 | 60.0011 | 49.8631 | 55.4441 | 59.605 | 56.8195 | 57.8634 | 55.5837 | 59.002
| Pumps (elec) | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524 | 0.66524
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 661.2135 | 612.6336 | 612.671 | 563.8244 | 505.9062 | 564.522 | 481.2998 | 559.3172 | 534.2275 | 492.2077 | 563.8742 | 531.5665 | 590.0428 | 541.9637 | 588.0371 | 668.1824
Gas (MJ/m2)
| Heating (gas) | 2.0331 | 31.65 | 23.1837 | 57.0985 | 19.2147 | 38.4618 | 54.0763 | 100.207 | 67.4384 | 91.9551 | 136.9323 | 99.6938 | 177.7237 | 145.1718 | 222.6261 | 349.2559
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 94.8502 | 114.2668 | 103.1197 | 132.9707 | 129.3356 | 116.554 | 145.3287 | 147.6633 | 144.8778 | 155.3148 | 160.5595 | 159.8918 | 171.7091 | 173.7347 | 190.1016 | 212.3585
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 144.0929 | 193.1239 | 173.513 | 237.2788 | 195.7599 | 202.2254 | 246.6146 | 295.08 | 259.5258 | 294.4795 | 344.7014 | 306.7952 | 396.6424 | 366.1161 | 459.9399 | 608.824
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 805.3065 | 805.7599 | 786.1839 | 801.1033 | 701.6636 | 766.7475 | 727.9144 | 854.3947 | 793.7532 | 786.6872 | 908.5756 | 838.3617 | 986.6852 | 908.0798 | 1047.9745 | 1277.0064
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 129.5334 | 125.3521 | 106.1913 | 125.2321 | 101.7499 | 107.402 | 106.165 | 130.6121 | 118.613 | 110.5588 | 149.4379 | 137.8028 | 163.0119 | 161.4705 | 168.2543 | 216.853
| Feb | 133.2777 | 108.6671 | 104.0982 | 122.2267 | 107.7955 | 100.6978 | 101.716 | 119.5943 | 112.6239 | 104.829 | 130.9969 | 124.1667 | 159.7951 | 150.2187 | 168.5424 | 210.7056
| Mar | 132.4686 | 123.4679 | 121.012 | 108.3965 | 102.808 | 102.1233 | 100.4899 | 112.2603 | 103.3376 | 104.9491 | 114.489 | 112.9815 | 121.1837 | 133.1953 | 148.3167 | 168.3339
| Apr | 134.7988 | 132.4982 | 120.8539 | 119.2048 | 105.8202 | 118.3532 | 102.3764 | 105.4616 | 107.8388 | 101.5367 | 105.2354 | 104.7032 | 109.0972 | 105.765 | 117.8879 | 133.6135
| May | 143.8217 | 141.7196 | 141.6671 | 129.625 | 114.3911 | 125.7172 | 101.9981 | 117.4865 | 113.923 | 105.8695 | 116.7159 | 112.1962 | 130.419 | 103.3674 | 107.0365 | 103.5872
| Jun | 146.9543 | 139.4097 | 163.8123 | 133.5306 | 109.3129 | 148.4229 | 108.4072 | 135.3937 | 121.0518 | 112.0423 | 125.4914 | 115.4849 | 131.9812 | 122.3265 | 119.3205 | 113.9309
| Jul | 146.9282 | 148.6352 | 161.2653 | 143.0623 | 120.193 | 147.0444 | 119.9041 | 143.0624 | 127.6311 | 114.2904 | 137.9464 | 124.134 | 136.9317 | 121.6782 | 132.1591 | 117.4899
| Aug | 143.1469 | 151.2756 | 161.9153 | 133.6877 | 122.6993 | 144.2387 | 105.7014 | 143.0679 | 127.1155 | 113.4029 | 139.764 | 119.2149 | 135.8018 | 117.4694 | 126.8647 | 110.4404
| Sep | 144.764 | 146.5135 | 147.8567 | 126.0787 | 119.9507 | 132.1887 | 113.7185 | 125.4542 | 118.0743 | 117.7236 | 120.6296 | 117.8477 | 117.2711 | 113.6265 | 110.2025 | 111.8792
| Oct | 143.8347 | 130.097 | 124.5653 | 116.9073 | 112.0293 | 114.5113 | 104.7714 | 119.9122 | 107.3242 | 101.8761 | 109.9018 | 108.2235 | 110.0724 | 111.2085 | 111.8871 | 138.4383
| Nov | 128.7054 | 129.2811 | 106.1738 | 109.5741 | 106.9112 | 104.5499 | 102.4966 | 113.9412 | 111.2007 | 109.8277 | 110.7568 | 113.4475 | 120.2554 | 116.9042 | 148.6464 | 165.9488
| Dec | 129.2155 | 129.6366 | 114.969 | 115.9954 | 103.0049 | 107.0199 | 104.0231 | 122.4711 | 114.2415 | 109.8999 | 147.6586 | 130.6253 | 170.5933 | 156.8373 | 171.2899 | 192.7942
Time of Peak Electrical Demand
| Jan | 22-JAN-08:00 | 14-JAN-08:15 | 21-JAN-08:30 | 14-JAN-08:15 | 28-JAN-08:00 | 07-JAN-08:15 | 01-JAN-08:15 | 15-JAN-08:15 | 08-JAN-08:15 | 01-JAN-08:15 | 07-JAN-08:15 | 08-JAN-08:15 | 06-JAN-07:15 | 07-JAN-08:15 | 09-JAN-07:15 | 13-JAN-09:00
| Feb | 25-FEB-08:00 | 20-FEB-08:00 | 18-FEB-08:15 | 10-FEB-07:15 | 12-FEB-08:00 | 26-FEB-08:00 | 18-FEB-08:00 | 05-FEB-08:15 | 05-FEB-08:15 | 12-FEB-08:15 | 11-FEB-08:15 | 16-FEB-07:15 | 04-FEB-08:15 | 26-FEB-08:15 | 02-FEB-07:15 | 04-FEB-08:15
| Mar | 05-MAR-08:00 | 25-MAR-07:00 | 17-MAR-19:15 | 12-MAR-07:30 | 04-MAR-08:00 | 04-MAR-08:15 | 11-MAR-08:00 | 19-MAR-07:15 | 12-MAR-07:15 | 11-MAR-08:15 | 04-MAR-08:15 | 07-MAR-07:15 | 05-MAR-08:15 | 04-MAR-08:15 | 09-MAR-07:15 | 25-MAR-07:15
| Apr | 02-APR-07:00 | 30-APR-07:00 | 02-APR-19:15 | 16-APR-07:00 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-07:00 | 05-APR-19:15 | 22-APR-19:15 | 09-APR-07:15 | 02-APR-07:00 | 25-APR-19:30 | 09-APR-07:15 | 02-APR-07:15 | 03-APR-06:15 | 09-APR-07:15
| May | 20-MAY-07:00 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 28-MAY-07:00 | 31-MAY-19:15 | 29-MAY-07:00 | 15-MAY-19:15 | 30-MAY-19:15 | 07-MAY-07:00 | 28-MAY-07:00 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 28-MAY-07:00 | 29-MAY-19:00
| Jun | 27-JUN-19:15 | 11-JUN-07:00 | 27-JUN-19:15 | 08-JUN-19:15 | 17-JUN-07:00 | 27-JUN-19:15 | 17-JUN-07:00 | 30-JUN-19:15 | 28-JUN-19:30 | 18-JUN-07:00 | 17-JUN-07:00 | 27-JUN-19:30 | 25-JUN-07:00 | 25-JUN-19:15 | 14-JUN-19:00 | 24-JUN-07:00
| Jul | 29-JUL-07:00 | 04-JUL-07:00 | 11-JUL-19:15 | 02-JUL-19:15 | 09-JUL-07:00 | 25-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:15 | 09-JUL-07:00 | 02-JUL-07:00 | 16-JUL-07:00 | 22-JUL-07:00 | 08-JUL-07:00 | 29-JUL-19:45
| Aug | 19-AUG-07:00 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 13-AUG-07:00 | 05-AUG-07:00 | 27-AUG-07:00 | 17-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 27-AUG-07:00 | 11-AUG-19:45 | 13-AUG-19:30 | 15-AUG-19:15
| Sep | 02-SEP-07:00 | 16-SEP-07:00 | 09-SEP-19:15 | 10-SEP-19:15 | 09-SEP-07:00 | 02-SEP-07:00 | 28-SEP-19:00 | 17-SEP-07:00 | 03-SEP-07:00 | 02-SEP-19:15 | 16-SEP-07:00 | 02-SEP-07:00 | 03-SEP-07:00 | 02-SEP-19:15 | 08-SEP-19:15 | 30-SEP-07:00
| Oct | 07-OCT-07:00 | 29-OCT-07:00 | 13-OCT-19:15 | 21-OCT-07:00 | 07-OCT-07:00 | 07-OCT-07:00 | 21-OCT-07:00 | 14-OCT-07:00 | 01-OCT-19:15 | 29-OCT-07:15 | 21-OCT-07:15 | 21-OCT-07:15 | 08-OCT-07:00 | 29-OCT-07:15 | 29-OCT-07:15 | 22-OCT-07:15
| Nov | 19-NOV-08:00 | 26-NOV-08:00 | 12-NOV-08:00 | 23-NOV-08:00 | 12-NOV-08:00 | 11-NOV-08:00 | 12-NOV-08:00 | 04-NOV-07:00 | 23-NOV-08:15 | 18-NOV-08:15 | 18-NOV-08:15 | 18-NOV-08:15 | 30-NOV-07:15 | 04-NOV-07:15 | 25-NOV-08:15 | 23-NOV-08:15
| Dec | 16-DEC-08:00 | 03-DEC-08:00 | 23-DEC-08:15 | 22-DEC-07:15 | 16-DEC-08:00 | 30-DEC-08:15 | 25-DEC-08:15 | 21-DEC-07:15 | 16-DEC-08:15 | 10-DEC-08:15 | 31-DEC-08:15 | 12-DEC-07:15 | 31-DEC-08:15 | 11-DEC-07:15 | 31-DEC-08:15 | 29-DEC-08:00
Source Energy
| Total Source Energy (GJ) | 9434.33 | 9777.03 | 8538.33 | 8652.55 | 7142.36 | 8990.95 | 7059.6 | 9320.93 | 8251.83 | 4732.01 | 9535.94 | 8423.54 | 9877.88 | 9165.69 | 10127.62 | 12247.81
| Total Source Energy (MJ/m2) | 2350.6 | 2435.98 | 2127.36 | 2155.82 | 1779.55 | 2240.13 | 1758.92 | 2322.35 | 2055.97 | 1179 | 2375.92 | 2098.76 | 2461.11 | 2283.67 | 2523.33 | 3051.59
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
| Total Building | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
Emissions
| Carbon Equivalent (kg) | 212599.8061 | 241805.6795 | 218756.6238 | 210805.134 | 80083.6583 | 226909.7489 | 80558.3807 | 189631.6264 | 262086.3883 | 61281.3338 | 360115.6125 | 264294.9392 | 253877.9031 | 247305.4368 | 257693.4142 | 253682.9881
| CO2 (kg) | 498268.6883 | 612069.9256 | 521199.5326 | 489083.7248 | 216917.8361 | 545059.3233 | 218992.6745 | 439065.8069 | 621188.45 | 156521.4953 | 845402.2677 | 628247.358 | 602047.8015 | 590127.2431 | 613518.556 | 652408.6437
| NOX (kg) | 852.9652 | 788.0923 | 852.5279 | 893.6559 | 187.7653 | 862.9015 | 190.0949 | 810.519 | 1043.9514 | 208.4544 | 1473.5785 | 1047.9676 | 1022.5748 | 981.139 | 1031.3702 | 773.4292
| SO2 (kg) | 3155.5729 | 3258.2033 | 2746.8997 | 2206.6423 | 1641.4603 | 3462.3006 | 1561.6878 | 2276.6144 | 2601.1624 | 424.4609 | 4237.01 | 2588.2503 | 1553.0108 | 1613.7539 | 1547.7993 | 3792.7359
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0144 | 0.0092 | 0.0075 | 0.0082 | 0.0008 | 0.0066 | 0.0008 | 0.0093 | 0.0102 | 0.0018 | 0.0129 | 0.0102 | 0.0115 | 0.0113 | 0.0115 | 0.0131
| Water for Electricity (m3) | 390.5261 | 1111.35 | 20289.8 | 3924.73 | 9903.04 | 17266.4 | 9421.38 | 141.5749 | 2704.52 | 5606.53 | 975.3223 | 2691.04 | 1020.58 | 38274.3 | 1017.11 | 761.098

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3232.17 | 805.31 | 817.57
Net Site Energy | 3232.17 | 805.31 | 817.57
Total Source Energy | 9434.33 | 2350.6 | 2386.39
Net Source Energy | 9434.33 | 2350.6 | 2386.39
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.55 | 8.16 | 0 | 0 | 0 | 0
Cooling | 918.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 252.48 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 380.69 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2653.84 | 578.33 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.84 | 0.251 | 0.11
North Total or Average |  |  | 72.38 | 5.84 | 0.251 | 0.11
Non-North Total or Average |  |  | 111.83 | 5.84 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1860.74 | 1360.44 | 500.3 | 0.73 | 3.6
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1882.81 | 1379.79 | 503.02 | 0.73 | 3.6
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2032.16 | 1511.15 | 521.02 | 0.74 | 3.61
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1952.54 | 1467.41 | 485.13 | 0.75 | 3.63
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1952.96 | 1467.74 | 485.22 | 0.75 | 3.63
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2704.6 | 2103.81 | 600.79 | 0.78 | 3.49
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8067.18 | 6013.94 | 2053.24 | 0.75 | 3
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6388.65 | 4788.42 | 1600.23 | 0.75 | 3
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7909.31 | 5868.22 | 2041.09 | 0.74 | 3
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2227.88 | 1689.1 | 538.78 | 0.76 | 3.59
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2175.43 | 1670.94 | 504.48 | 0.77 | 3.62
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8278.7 | 6303.7 | 1975 | 0.76 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2457.06 | 1925.38 | 531.68 | 0.78 | 3.56
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7747.47 | 5828.31 | 1919.16 | 0.75 | 3.01
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2153.05 | 1650.79 | 502.26 | 0.77 | 3.62
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2696.14 | 2096.15 | 599.98 | 0.78 | 3.49
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8060.19 | 6007.72 | 2052.48 | 0.75 | 3
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6474.7 | 4869.67 | 1605.03 | 0.75 | 3.01
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8046.98 | 5996.06 | 2050.92 | 0.75 | 3
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2272.53 | 1728.86 | 543.66 | 0.76 | 3.58
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2220.39 | 1711.43 | 508.95 | 0.77 | 3.61
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8003.75 | 6057.3 | 1946.45 | 0.76 | 3.01
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2107.73 | 1610.06 | 497.67 | 0.76 | 3.63
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7905.38 | 5969.32 | 1936.06 | 0.76 | 3.01
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2199.51 | 1692.6 | 506.9 | 0.77 | 3.61
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3625.61 | 2753.61 | 872 | 0.76 | 3.22
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12623.5 | 9057.81 | 3565.7 | 0.72 | 2.97
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10196.18 | 7352.8 | 2843.38 | 0.72 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12618.44 | 9053.44 | 3565 | 0.72 | 2.97
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3487.27 | 2548.93 | 938.34 | 0.73 | 3.22
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3448.72 | 2530.36 | 918.35 | 0.73 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12551.36 | 9057.32 | 3494.05 | 0.72 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3263.22 | 2371.19 | 892.03 | 0.73 | 3.27
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12483.38 | 8999.58 | 3483.81 | 0.72 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3414.41 | 2505.32 | 909.09 | 0.73 | 3.24
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8629.2 | 6847.44 | 1781.76 | 0.79 | 4.02
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4663.53 | 3499.93 | 1163.6 | 0.75 | 3.87
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4366.89 | 3248 | 1118.89 | 0.74 | 3.85
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11247.73 | 7604.4 | 3643.33 | 0.68 | 3.65
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18847.56 | 12742.52 | 6105.04 | 0.68 | 3.65
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1267.49 | 1012.29 | 255.2 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1161.21 | 842.18 | 319.02 | 0.73 | 3.8
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7907.42 | 5347.83 | 2559.58 | 0.68 | 3.65
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31516.61 | 23622.62 | 7893.99 | 0.75 | 3.63
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3220.01 | 2177 | 1043.02 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9173.04 | 6201.74 | 2971.3 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 299.57 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 694.82 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1668.96 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 579.54 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 695.4 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 754.38 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 1668.96 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 658.76 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 619.35 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 581.52 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1229.52 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4558.86 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3687.23 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4557.37 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1359.09 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1336.33 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4547.36 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1207.43 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4526.1 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1315.21 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 138.24 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 114.14 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 24511.18 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 11544.32 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5652.23 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 10905.72 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 24108.74 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 3705.56 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 16619.71 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1418.89 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 14572.74 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 78444.16 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5210.68 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 10064.43 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.93 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.41 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59.44 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.44 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.46 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.48 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.12 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 265.34 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 212.83 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 257.22 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.23 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.7 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 286.12 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.62 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 260.34 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.6 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.7 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 265.01 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 217.45 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 264.39 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.38 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.91 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 272.74 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.38 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 267.97 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.88 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 124.56 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.31 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 309.41 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.08 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.39 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.19 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 381.51 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.9 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.54 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.12 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.43 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.35 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 596.2 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.24 | 283.96 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.22 | 260.32 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 525.38 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.76 | 880.36 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 88.81 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 65.12 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 369.69 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.65 | 1879.12 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 150.41 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 428.47 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37735.435 | 64.037 | 234.5686 | 0 | 0.0011 | 29029.199 | 16044.6657
February | 34451.3008 | 58.5752 | 215.0303 | 0 | 0.001 | 26611.3159 | 14659.4468
March | 38677.7674 | 65.8802 | 242.3466 | 0 | 0.0011 | 29991.9686 | 16469.7819
April | 39891.4299 | 68.2459 | 252.3005 | 0 | 0.0012 | 31224.0735 | 17016.4939
May | 43928.7818 | 75.3983 | 279.7662 | 0 | 0.0013 | 34623.3458 | 18763.2868
June | 44375.924 | 76.3275 | 283.8868 | 0 | 0.0013 | 35133.4324 | 18970.4799
July | 47515.4984 | 81.834 | 304.8088 | 0 | 0.0014 | 37722.7891 | 20323.2891
August | 47175.6153 | 81.2126 | 302.3454 | 0 | 0.0014 | 37417.8977 | 20174.3113
September | 44458.6275 | 76.4205 | 284.0282 | 0 | 0.0013 | 35150.8901 | 19000.8995
October | 43484.7566 | 74.5411 | 276.1897 | 0 | 0.0013 | 34180.655 | 18564.0999
November | 39021.4106 | 66.6363 | 245.844 | 0 | 0.0011 | 30424.9337 | 16633.2252
December | 37552.141 | 63.8567 | 234.4578 | 0 | 0.0011 | 29015.5951 | 15979.8261
Annual Sum or Average | 498268.6883 | 852.9652 | 3155.5729 | 0 | 0.0144 | 390526.0961 | 212599.8061
Minimum of Months | 34451.3008 | 58.5752 | 215.0303 | 0 | 0.001 | 26611.3159 | 14659.4468
Maximum of Months | 47515.4984 | 81.834 | 304.8088 | 0 | 0.0014 | 37722.7891 | 20323.2891
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 197270000000 | 129533.368 | 22-JAN-08:00 | 26328.66 | 57998.833 | 8648.432 | 0 | 36472.665 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 180839000000 | 133277.685 | 25-FEB-08:00 | 26328.66 | 57998.833 | 8828.995 | 0 | 40036.42 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 203812000000 | 132468.562 | 05-MAR-08:00 | 26328.66 | 57998.833 | 8770.413 | 0 | 39285.878 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 212185000000 | 134798.757 | 02-APR-07:00 | 26328.66 | 57998.833 | 8898.312 | 0 | 41488.175 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 235285000000 | 143821.731 | 20-MAY-07:00 | 26328.66 | 57998.833 | 9361.206 | 0 | 50048.255 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 238751000000 | 146954.262 | 27-JUN-19:15 | 36517.967 | 38824.77 | 10164.65 | 0 | 58881.097 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 256347000000 | 146928.203 | 29-JUL-07:00 | 26328.66 | 57998.833 | 9512.194 | 0 | 53003.738 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 254275000000 | 143146.853 | 19-AUG-07:00 | 26328.66 | 57998.833 | 9321.018 | 0 | 49413.565 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 238870000000 | 144763.977 | 02-SEP-07:00 | 26328.66 | 57998.833 | 9383.413 | 0 | 50968.294 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 232277000000 | 143834.742 | 07-OCT-07:00 | 26328.66 | 57998.833 | 9366.017 | 0 | 50056.454 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 206754000000 | 128705.404 | 19-NOV-08:00 | 26328.66 | 57998.833 | 8680.538 | 0 | 35612.595 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 197177000000 | 129215.457 | 16-DEC-08:00 | 26328.66 | 57998.833 | 8590.431 | 0 | 36212.755 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2653840000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 180839000000 | 128705.404 |  | 26328.66 | 38824.77 | 8590.431 | 0 | 35612.595 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 256347000000 | 146954.262 |  | 36517.967 | 57998.833 | 10164.65 | 0 | 58881.097 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 58267.38 | 6625.76 | 0 | 64893.14
Cost per Total Building Area ($/m2) | 14.52 | 1.65 | 0 | 16.17
Cost per Net Conditioned Building Area ($/m2) | 14.74 | 1.68 | 0 | 16.41

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3233.99 | 805.76 | 818.03
Net Site Energy | 3233.99 | 805.76 | 818.03
Total Source Energy | 9777.03 | 2435.98 | 2473.08
Net Source Energy | 9777.03 | 2435.98 | 2473.08
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 43.26 | 127.03 | 0 | 0 | 0 | 0
Cooling | 691.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 242.05 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 458.62 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2458.86 | 775.12 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.84 | 0.251 | 0.11
North Total or Average |  |  | 72.38 | 5.84 | 0.251 | 0.11
Non-North Total or Average |  |  | 111.83 | 5.84 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1935.51 | 1414.91 | 520.6 | 0.73 | 3.6
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1958.68 | 1435.12 | 523.56 | 0.73 | 3.6
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2112.26 | 1569.5 | 542.76 | 0.74 | 3.6
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1912.46 | 1445.07 | 467.39 | 0.76 | 3.63
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1912.53 | 1445.11 | 467.42 | 0.76 | 3.63
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2747.68 | 2152.2 | 595.47 | 0.78 | 3.48
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8405.18 | 6256.3 | 2148.89 | 0.74 | 3
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6659.23 | 4988.14 | 1671.09 | 0.75 | 3
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8231.94 | 6104.05 | 2127.89 | 0.74 | 3
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2317.78 | 1754.89 | 562.89 | 0.76 | 3.56
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2147.91 | 1660.57 | 487.34 | 0.77 | 3.63
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8209.59 | 6279.95 | 1929.64 | 0.76 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2429.33 | 1915.89 | 513.44 | 0.79 | 3.58
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7676.19 | 5801.84 | 1874.35 | 0.76 | 3.01
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2122.57 | 1637.66 | 484.9 | 0.77 | 3.64
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2740.24 | 2145.46 | 594.78 | 0.78 | 3.48
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8399.41 | 6251.19 | 2148.23 | 0.74 | 3
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6758.6 | 5075.63 | 1682.97 | 0.75 | 3.01
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8386.87 | 6240.2 | 2146.67 | 0.74 | 3
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2364.02 | 1795.79 | 568.23 | 0.76 | 3.55
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2195.74 | 1703.83 | 491.91 | 0.78 | 3.62
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7941.31 | 6039.13 | 1902.18 | 0.76 | 3.01
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2081.91 | 1600.96 | 480.95 | 0.77 | 3.64
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7842.97 | 5951.03 | 1891.94 | 0.76 | 3.01
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2171.13 | 1681.56 | 489.57 | 0.77 | 3.63
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3739.32 | 2859.16 | 880.16 | 0.76 | 3.19
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13223.43 | 9551.19 | 3672.24 | 0.72 | 2.98
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10685.11 | 7756.82 | 2928.28 | 0.73 | 2.98
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13219.28 | 9547.69 | 3671.59 | 0.72 | 2.98
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3656.98 | 2687.13 | 969.85 | 0.73 | 3.18
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3511.16 | 2591.62 | 919.53 | 0.74 | 3.22
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12913.09 | 9333.93 | 3579.17 | 0.72 | 2.98
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3322.62 | 2429.5 | 893.12 | 0.73 | 3.26
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12844.3 | 9275.61 | 3568.69 | 0.72 | 2.98
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3465.92 | 2557.33 | 908.59 | 0.74 | 3.23
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8552.93 | 6823.08 | 1729.85 | 0.8 | 4.03
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4682.36 | 3527.12 | 1155.25 | 0.75 | 3.88
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4381.74 | 3273.99 | 1107.76 | 0.75 | 3.86
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11843.84 | 8077.89 | 3765.95 | 0.68 | 3.67
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19397.05 | 13114.02 | 6283.03 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1314.69 | 1049.98 | 264.71 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1205.72 | 878.73 | 326.99 | 0.73 | 3.81
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7764.8 | 5285.83 | 2478.96 | 0.68 | 3.67
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31147.22 | 23441.34 | 7705.87 | 0.75 | 3.64
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3219.7 | 2176.79 | 1042.92 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8970.03 | 6091.83 | 2878.2 | 0.68 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 198.63 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 332.12 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 377.92 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1032.35 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 248.97 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 803.96 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 825.54 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1040.51 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1029.73 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 815.71 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1293.35 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3242.14 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2494.13 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3167.13 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1035.04 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1002.89 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2937.68 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 734.42 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3031.81 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 924.38 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1343.29 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3374.48 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2712 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3356.64 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1079.96 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1054.36 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3300.1 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 815.24 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3295.66 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 989.27 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2197.92 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8227.04 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6648.97 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8216.78 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2309.17 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2288.13 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8206.66 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2213.69 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8173.99 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2259.21 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 110.69 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 220.01 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 249.23 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 870.83 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 61.78 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 201.35 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 232.51 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 627.17 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 24960.37 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6563.31 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6098.3 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 12075.59 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 29836.71 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1819 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 21940.3 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1581.24 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9780.05 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 79774.15 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 6072.34 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 11196.88 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.62 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.03 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.18 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.21 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.77 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 60.74 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.81 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 68.94 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.93 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.93 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.24 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.46 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 221.52 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 267.34 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.06 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.86 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 286.75 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.87 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 260.79 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.6 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.87 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.18 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 226.2 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 274.6 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.26 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.22 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 273.65 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.6 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 268.87 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 130.48 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 402.87 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.62 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 402.69 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 116.2 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 112.78 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 394.14 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.32 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 391.14 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 111.23 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.34 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.68 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.78 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.71 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.19 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.63 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.72 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.95 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 597.82 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 287.6 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 264.05 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 566.65 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.78 | 906.03 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 92.12 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 68.43 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 369.59 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.65 | 1874.99 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 150.39 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 424.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47613.5154 | 60.5209 | 242.457 | 0 | 0.0007 | 82696.7525 | 18709.0451
February | 41531.0437 | 52.7081 | 210.342 | 0 | 0.0006 | 71742.6369 | 16308.516
March | 45209.6102 | 57.8693 | 235.8737 | 0 | 0.0007 | 80453.2722 | 17816.5363
April | 47426.13 | 61.1216 | 253.2509 | 0 | 0.0007 | 86382.3538 | 18743.5371
May | 54072.8393 | 69.952 | 292.4449 | 0 | 0.0008 | 99752.4337 | 21404.4836
June | 56889.503 | 73.7746 | 310.1833 | 0 | 0.0009 | 105803.7559 | 22542.4998
July | 62291.5835 | 80.8831 | 341.0803 | 0 | 0.001 | 116343.2268 | 24696.3565
August | 60733.2958 | 78.8275 | 332.0967 | 0 | 0.0009 | 113278.7664 | 24074.4002
September | 54830.7633 | 71.0526 | 298.2273 | 0 | 0.0008 | 101725.3322 | 21719.9959
October | 50490.6915 | 65.187 | 271.2389 | 0 | 0.0008 | 92518.4861 | 19969.6411
November | 45135.484 | 57.9284 | 237.6437 | 0 | 0.0007 | 81057.7433 | 17807.1741
December | 45845.466 | 58.2672 | 233.3645 | 0 | 0.0007 | 79595.4627 | 18013.4939
Annual Sum or Average | 612069.9256 | 788.0923 | 3258.2033 | 0 | 0.0092 | 1111350 | 241805.6795
Minimum of Months | 41531.0437 | 52.7081 | 210.342 | 0 | 0.0006 | 71742.6369 | 16308.516
Maximum of Months | 62291.5835 | 80.8831 | 341.0803 | 0 | 0.001 | 116343.2268 | 24696.3565
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 182967000000 | 125352.076 | 14-JAN-08:15 | 26328.66 | 57998.833 | 7562.7 | 33313.46 | 63.645 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 158731000000 | 108667.139 | 20-FEB-08:00 | 26328.66 | 57998.833 | 7487.684 | 0 | 16767.184 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 178003000000 | 123467.854 | 25-MAR-07:00 | 26328.66 | 57998.833 | 8409.906 | 0 | 30645.678 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 191121000000 | 132498.239 | 30-APR-07:00 | 26328.66 | 57998.833 | 8889.165 | 0 | 39196.803 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 220702000000 | 141719.606 | 26-MAY-19:15 | 36517.967 | 38824.77 | 10004.65 | 0 | 53806.441 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 234091000000 | 139409.668 | 11-JUN-07:00 | 26328.66 | 57998.833 | 9217.814 | 0 | 45779.583 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 257410000000 | 148635.243 | 04-JUL-07:00 | 26328.66 | 57998.833 | 9709.827 | 0 | 54513.146 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 250629000000 | 151275.606 | 06-AUG-19:15 | 36433.634 | 38807.225 | 10537.629 | 0 | 62931.34 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 225067000000 | 146513.457 | 16-SEP-07:00 | 26328.66 | 57998.833 | 9555.417 | 0 | 52545.77 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 204697000000 | 130097.011 | 29-OCT-07:00 | 26328.66 | 57998.833 | 8711.69 | 0 | 36973.05 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 179340000000 | 129281.071 | 26-NOV-08:00 | 26328.66 | 57998.833 | 8678.067 | 0 | 36190.733 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 176105000000 | 129636.559 | 03-DEC-08:00 | 26328.66 | 57998.833 | 8722.302 | 0 | 36501.986 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2458860000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 158731000000 | 108667.139 |  | 26328.66 | 38807.225 | 7487.684 | 0 | 63.645 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 257410000000 | 151275.606 |  | 36517.967 | 57998.833 | 10537.629 | 33313.46 | 62931.34 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 73896.15 | 6335 | 0 | 80231.14
Cost per Total Building Area ($/m2) | 18.41 | 1.58 | 0 | 19.99
Cost per Net Conditioned Building Area ($/m2) | 18.69 | 1.6 | 0 | 20.29

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3155.42 | 786.18 | 798.16
Net Site Energy | 3155.42 | 786.18 | 798.16
Total Source Energy | 8538.33 | 2127.36 | 2159.75
Net Source Energy | 8538.33 | 2127.36 | 2159.75
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 18.87 | 93.05 | 0 | 0 | 0 | 0
Cooling | 702.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 255.59 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 413.88 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2459.01 | 696.41 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.704 | 0.787 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.251 | 0.11 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.84 | 0.251 | 0.11
North Total or Average |  |  | 72.38 | 5.84 | 0.251 | 0.11
Non-North Total or Average |  |  | 111.83 | 5.84 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1853.32 | 1379.38 | 473.94 | 0.74 | 3.62
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1880.77 | 1403.21 | 477.56 | 0.75 | 3.62
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2054.23 | 1554.16 | 500.07 | 0.76 | 3.63
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1775.86 | 1371.88 | 403.98 | 0.77 | 3.66
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1749.15 | 1352.07 | 397.08 | 0.77 | 3.66
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2889.08 | 2307.38 | 581.7 | 0.8 | 3.46
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8692.34 | 6642.72 | 2049.62 | 0.76 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6933.42 | 5328.78 | 1604.64 | 0.77 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8499.08 | 6473.57 | 2025.52 | 0.76 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2438.79 | 1893.94 | 544.85 | 0.78 | 3.56
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2185.93 | 1742.69 | 443.24 | 0.8 | 3.66
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8142.73 | 6428.05 | 1714.68 | 0.79 | 3.04
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2509.23 | 2004.01 | 505.22 | 0.8 | 3.57
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7582.72 | 5924.15 | 1658.57 | 0.78 | 3.04
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2140.53 | 1701.65 | 438.88 | 0.79 | 3.67
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2899.44 | 2315.65 | 583.79 | 0.8 | 3.46
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8746.45 | 6690.1 | 2056.35 | 0.76 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7095.82 | 5471.29 | 1624.53 | 0.77 | 3.03
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8733.82 | 6679.05 | 2054.77 | 0.76 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2516.56 | 1962.46 | 554.09 | 0.78 | 3.54
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2278.72 | 1819.91 | 458.81 | 0.8 | 3.63
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7930.6 | 6236.95 | 1693.66 | 0.79 | 3.04
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2099.94 | 1664.98 | 434.96 | 0.79 | 3.67
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7826.74 | 6143.48 | 1683.26 | 0.78 | 3.04
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2224.96 | 1776.98 | 447.98 | 0.8 | 3.65
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3822.62 | 3052.95 | 769.66 | 0.8 | 3.21
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13516.12 | 10285.61 | 3230.51 | 0.76 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10963.72 | 8383.91 | 2579.81 | 0.76 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13515.12 | 10284.76 | 3230.36 | 0.76 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3791.23 | 2933.7 | 857.53 | 0.77 | 3.19
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3646.34 | 2824.84 | 821.51 | 0.77 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13047.1 | 9936.84 | 3110.27 | 0.76 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3398.72 | 2608.75 | 789.97 | 0.77 | 3.29
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12975.65 | 9874.96 | 3100.69 | 0.76 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3544.02 | 2752.72 | 791.3 | 0.78 | 3.26
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8253.95 | 6592.06 | 1661.89 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4650.94 | 3637.36 | 1013.58 | 0.78 | 3.98
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4405.36 | 3439.48 | 965.88 | 0.78 | 3.97
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11793.99 | 8738.05 | 3055.94 | 0.74 | 3.84
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20028.48 | 13540.92 | 6487.56 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1276.35 | 1019.37 | 256.99 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1066.84 | 799.53 | 267.32 | 0.75 | 3.87
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6969.21 | 4961.82 | 2007.39 | 0.71 | 3.76
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30183.58 | 23220.47 | 6963.1 | 0.77 | 3.69
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3178.94 | 2149.23 | 1029.71 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7724.51 | 5461.4 | 2263.11 | 0.71 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 40.23 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 148.21 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 186.66 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 656.09 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 104.77 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 679.96 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 698.93 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 894.86 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 889.09 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 692.76 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 991.97 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2478.51 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1888.52 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2478.51 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 833.29 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 805.74 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2478.51 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 668.06 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2478.51 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 728.72 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1028.33 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2570.55 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2062.6 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2558.83 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 868.36 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 846.07 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2513.63 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 619.63 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2515.66 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 782.08 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1686.77 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6245.49 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 5046.75 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6240.01 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1802.39 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1782.88 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6241.01 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1678.02 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6214 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1762.33 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 35.12 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 64.28 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 503.38 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 63.16 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 90.65 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 375.27 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 23055.19 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6584.49 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6250.56 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 13923.24 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 26721.72 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1702.78 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 18510.92 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1404.23 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 8956.56 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 77524.66 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5141.22 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 9840.55 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.13 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.48 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.6 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.12 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.34 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 60.73 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.98 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.95 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 63.43 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 62.56 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 111.09 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 302.93 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 244.79 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 293.95 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.15 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.73 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.25 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.49 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 277.79 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.48 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.49 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.44 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 252.38 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 304.86 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.81 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.62 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 294.83 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.48 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 289.73 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.56 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 146.99 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.73 | 466.49 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 382.65 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.73 | 466.45 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 135.93 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 131.08 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.71 | 451.16 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 119.64 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.7 | 447.9 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 128.15 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.11 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.21 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.62 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.2 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.29 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.21 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 578.35 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 311.19 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 293.65 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 696.56 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.81 | 935.52 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 89.43 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 64.75 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 373.19 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.68 | 1911.39 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 148.49 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 406.36 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37485.3972 | 59.8285 | 186.8078 | 0 | 0.0005 | 1379770 | 15582.9685
February | 33926.3014 | 54.1902 | 169.3761 | 0 | 0.0005 | 1251020 | 14107.688
March | 39250.0051 | 63.6964 | 203.2079 | 0 | 0.0006 | 1500960 | 16422.854
April | 39979.8602 | 65.3903 | 210.6719 | 0 | 0.0006 | 1556120 | 16779.7528
May | 44457.2741 | 73.2136 | 237.8834 | 0 | 0.0007 | 1757140 | 18709.522
June | 49991.4156 | 82.8285 | 271.1209 | 0 | 0.0007 | 2002680 | 21089.2013
July | 55434.9603 | 92.065 | 302.2155 | 0 | 0.0008 | 2232370 | 23407.5749
August | 53823.2592 | 89.3053 | 292.8282 | 0 | 0.0008 | 2163030 | 22718.6316
September | 48668.9807 | 80.5025 | 262.9725 | 0 | 0.0007 | 1942480 | 20517.6754
October | 42588.7464 | 69.894 | 226.1314 | 0 | 0.0006 | 1670320 | 17898.6494
November | 37364.2817 | 60.6294 | 193.3958 | 0 | 0.0005 | 1428480 | 15633.1484
December | 38229.0506 | 60.9843 | 190.2882 | 0 | 0.0005 | 1405470 | 15888.9575
Annual Sum or Average | 521199.5326 | 852.5279 | 2746.8997 | 0 | 0.0075 | 20289800 | 218756.6238
Minimum of Months | 33926.3014 | 54.1902 | 169.3761 | 0 | 0.0005 | 1251020 | 14107.688
Maximum of Months | 55434.9603 | 92.065 | 302.2155 | 0 | 0.0008 | 2232370 | 23407.5749
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 167220000000 | 106191.277 | 21-JAN-08:30 | 26328.66 | 57998.833 | 7433.004 | 9585.627 | 4760.375 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 151616000000 | 104098.218 | 18-FEB-08:15 | 26328.66 | 57998.833 | 7393.059 | 7596.91 | 4695.978 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 181907000000 | 121012.004 | 17-MAR-19:15 | 36517.967 | 38824.77 | 9374.941 | 0 | 33728.548 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 188592000000 | 120853.884 | 02-APR-19:15 | 36433.634 | 38807.225 | 9432.39 | 0 | 33614.857 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 212955000000 | 141667.13 | 28-MAY-19:30 | 36433.634 | 38807.225 | 10673.012 | 0 | 53187.482 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 242713000000 | 163812.329 | 27-JUN-19:15 | 36517.967 | 38824.77 | 11835.41 | 0 | 76549.404 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 270550000000 | 161265.25 | 11-JUL-19:15 | 36517.967 | 38824.77 | 11767.477 | 0 | 74070.257 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 262146000000 | 161915.345 | 01-AUG-19:30 | 36517.967 | 38824.77 | 11632.793 | 0 | 72374.036 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 235417000000 | 147856.743 | 09-SEP-19:15 | 36349.301 | 38772.136 | 11011.067 | 0 | 59158.462 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 202433000000 | 124565.288 | 13-OCT-19:15 | 36517.967 | 38824.77 | 9583.28 | 0 | 37073.492 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 173124000000 | 106173.767 | 12-NOV-08:00 | 26328.66 | 57998.833 | 7664.199 | 0 | 14097.297 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 170335000000 | 114969.005 | 23-DEC-08:15 | 26328.66 | 57998.833 | 7900.54 | 21487.222 | 1168.972 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2459010000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 151616000000 | 104098.218 |  | 26328.66 | 38772.136 | 7393.059 | 0 | 1168.972 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 270550000000 | 163812.329 |  | 36517.967 | 57998.833 | 11835.41 | 21487.222 | 76549.404 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 60793.81 | 5941.48 | 0 | 66735.29
Cost per Total Building Area ($/m2) | 15.15 | 1.48 | 0 | 16.63
Cost per Net Conditioned Building Area ($/m2) | 15.38 | 1.5 | 0 | 16.88

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3215.3 | 801.1 | 813.3
Net Site Energy | 3215.3 | 801.1 | 813.3
Total Source Energy | 8652.55 | 2155.82 | 2188.64
Net Source Energy | 8652.55 | 2155.82 | 2188.64
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 78.53 | 229.17 | 0 | 0 | 0 | 0
Cooling | 471.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.04 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 230.76 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 533.69 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2262.96 | 952.34 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.35 | 0.242
North Total or Average |  |  | 72.38 | 3.69 | 0.361 | 0.251
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.343 | 0.237
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1761.78 | 1322.15 | 439.63 | 0.75 | 3.62
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1788.48 | 1343.75 | 444.73 | 0.75 | 3.63
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1903.01 | 1445.98 | 457.03 | 0.76 | 3.64
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1713.7 | 1318.67 | 395.04 | 0.77 | 3.65
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1741.5 | 1343.9 | 397.6 | 0.77 | 3.66
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2362.77 | 1881.8 | 480.97 | 0.8 | 3.61
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7857.46 | 6027.53 | 1829.94 | 0.77 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6252.44 | 4819.65 | 1432.79 | 0.77 | 3.03
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7692.35 | 5879.27 | 1813.07 | 0.76 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2150.9 | 1674.95 | 475.95 | 0.78 | 3.64
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1991.39 | 1575.39 | 415.99 | 0.79 | 3.68
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7650.34 | 6012.37 | 1637.98 | 0.79 | 3.04
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2364.66 | 1888.54 | 476.11 | 0.8 | 3.61
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7112.86 | 5520.71 | 1592.15 | 0.78 | 3.03
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1973.65 | 1559.12 | 414.53 | 0.79 | 3.68
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2360.11 | 1879.34 | 480.77 | 0.8 | 3.61
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7880.81 | 6048.45 | 1832.35 | 0.77 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6360.03 | 4923.89 | 1436.13 | 0.77 | 3.03
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7871.6 | 6040.19 | 1831.41 | 0.77 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2206.27 | 1724.97 | 481.29 | 0.78 | 3.63
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2046.06 | 1625.69 | 420.37 | 0.79 | 3.69
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7401.21 | 5784.09 | 1617.11 | 0.78 | 3.04
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1949.48 | 1536.92 | 412.56 | 0.79 | 3.68
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7303.26 | 5694.52 | 1608.74 | 0.78 | 3.03
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2029.51 | 1610.48 | 419.03 | 0.79 | 3.69
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3203.74 | 2497.14 | 706.6 | 0.78 | 3.35
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12225.11 | 9102.24 | 3122.86 | 0.74 | 3
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9904.65 | 7412.67 | 2491.99 | 0.75 | 3
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12229.82 | 9106.28 | 3123.54 | 0.74 | 3
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3364.25 | 2548.69 | 815.56 | 0.76 | 3.28
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3265.13 | 2465.9 | 799.22 | 0.76 | 3.31
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11977.5 | 8902.73 | 3074.77 | 0.74 | 3
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3089.48 | 2316.73 | 772.75 | 0.75 | 3.35
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11909.53 | 8843.81 | 3065.72 | 0.74 | 3
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3228.64 | 2438.66 | 789.98 | 0.76 | 3.32
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8413.51 | 6719.49 | 1694.02 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4264.37 | 3289.7 | 974.67 | 0.77 | 3.94
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3974.14 | 3043.62 | 930.51 | 0.77 | 3.92
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10498.57 | 7352.07 | 3146.49 | 0.7 | 3.72
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18667.19 | 12620.57 | 6046.62 | 0.68 | 3.65
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1261.12 | 1007.2 | 253.92 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1065.04 | 795.06 | 269.98 | 0.75 | 3.86
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7180.86 | 5045.4 | 2135.46 | 0.7 | 3.73
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30507.87 | 23426.4 | 7081.47 | 0.77 | 3.68
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3186.72 | 2154.49 | 1032.23 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7871.21 | 5480.84 | 2390.37 | 0.7 | 3.71
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 238.83 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 336.24 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 381.14 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1176.41 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 319.58 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 873.25 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 894.48 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1105.19 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1101.16 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 889.72 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1289.47 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3381.16 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2591.61 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3319.69 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1066.21 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1036.75 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3169 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 792.25 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3191.31 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 958.15 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1339.44 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3525.24 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2814.29 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3512.45 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1112.4 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1089.13 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3464.54 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 855.02 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3462 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1025.39 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2334.79 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 9210.1 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7424.34 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 9203.96 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2552.64 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2534.01 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 9207.62 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2485.06 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 9174.9 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2509.22 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 143.97 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 222.72 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 254.19 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1014 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 56.92 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 175.51 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 206.86 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 681.69 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 24018.15 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6317.38 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5877.1 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 11325.24 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 30619.93 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1687.29 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 23667.93 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1491.77 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 10000.77 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 79954.23 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 6470.77 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 10898.46 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.77 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.08 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.23 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.78 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.03 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.87 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59.92 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.45 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 60.67 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 62.05 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.31 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 276.22 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 222.24 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 268.16 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.22 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 283.97 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.93 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 256.78 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.1 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.17 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 277.36 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 228.29 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 276.91 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.96 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.8 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 271.33 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.87 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 266.37 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.95 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 116.76 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 400.92 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 328.81 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 401.13 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 114.91 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.72 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 391.21 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.04 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 388.12 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.52 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.46 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.72 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.82 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.26 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.18 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.56 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.67 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.19 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 589.53 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.24 | 276.68 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.22 | 253.63 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 538.82 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 871.93 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 88.37 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 64.04 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 371.73 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.69 | 1923.77 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 148.85 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 398.01 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 41782.4625 | 73.7207 | 175.6485 | 0 | 0.0007 | 312381.7612 | 17766.7257
February | 37042.8628 | 65.6781 | 157.2923 | 0 | 0.0006 | 279739.6341 | 15780.9047
March | 37277.6734 | 67.0648 | 163.0459 | 0 | 0.0006 | 289982.511 | 15970.5493
April | 37241.358 | 67.9991 | 167.7877 | 0 | 0.0006 | 298426.1875 | 16047.3165
May | 41322.6201 | 76.5571 | 191.5971 | 0 | 0.0007 | 340784.551 | 17908.0759
June | 43324.7999 | 80.7871 | 203.4324 | 0 | 0.0007 | 361840.5164 | 18823.8434
July | 47165.9318 | 88.2449 | 222.9164 | 0 | 0.0008 | 396498.9866 | 20520.0225
August | 46231.0469 | 86.4547 | 218.2962 | 0 | 0.0008 | 388280.8111 | 20109.4919
September | 42567.691 | 79.3624 | 199.814 | 0 | 0.0007 | 355404.3813 | 18493.6986
October | 38386.314 | 70.5828 | 175.3634 | 0 | 0.0006 | 311905.3 | 16586.2185
November | 36445.7672 | 65.6486 | 159.8016 | 0 | 0.0006 | 284213.3004 | 15621.5722
December | 40295.1972 | 71.5557 | 171.647 | 0 | 0.0006 | 305270.1932 | 17176.7148
Annual Sum or Average | 489083.7248 | 893.6559 | 2206.6423 | 0 | 0.0082 | 3924730 | 210805.134
Minimum of Months | 36445.7672 | 65.6486 | 157.2923 | 0 | 0.0006 | 279739.6341 | 15621.5722
Maximum of Months | 47165.9318 | 88.2449 | 222.9164 | 0 | 0.0008 | 396498.9866 | 20520.0225
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 180116000000 | 125232.094 | 14-JAN-08:15 | 26328.66 | 57998.833 | 7345.554 | 33370.576 | 103.694 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 161295000000 | 122226.684 | 10-FEB-07:15 | 24311.729 | 51279.599 | 7493.391 | 36255.701 | 320.485 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 167201000000 | 108396.479 | 12-MAR-07:30 | 26328.66 | 57998.833 | 7020.809 | 11923.992 | 5039.407 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 172070000000 | 119204.83 | 16-APR-07:00 | 26328.66 | 57998.833 | 8319.841 | 0 | 26472.718 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 196493000000 | 129625.036 | 14-MAY-19:30 | 36433.634 | 38807.225 | 9603.768 | 0 | 42214.63 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 208634000000 | 133530.55 | 08-JUN-19:15 | 36517.967 | 38824.77 | 9871.637 | 0 | 48231.397 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 228618000000 | 143062.319 | 02-JUL-19:15 | 36433.634 | 38807.225 | 10505.089 | 0 | 57231.593 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 223879000000 | 133687.679 | 14-AUG-19:30 | 36517.967 | 38824.77 | 9775.717 | 0 | 46003.447 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 204923000000 | 126078.736 | 10-SEP-19:15 | 36433.634 | 38807.225 | 9384.231 | 0 | 38887.868 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 179842000000 | 116907.292 | 21-OCT-07:00 | 26328.66 | 57998.833 | 8160.783 | 0 | 24334.238 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 163875000000 | 109574.142 | 23-NOV-08:00 | 26328.66 | 57998.833 | 7611.42 | 0 | 17550.45 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 176016000000 | 115995.351 | 22-DEC-07:15 | 24311.729 | 51279.599 | 7292.71 | 29913.636 | 631.898 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2262960000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 161295000000 | 108396.479 |  | 24311.729 | 38807.225 | 7020.809 | 0 | 103.694 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 228618000000 | 143062.319 |  | 36517.967 | 57998.833 | 10505.089 | 36255.701 | 57231.593 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63425.01 | 10059.28 | 0 | 73484.3
Cost per Total Building Area ($/m2) | 15.8 | 2.51 | 0 | 18.31
Cost per Net Conditioned Building Area ($/m2) | 16.04 | 2.54 | 0 | 18.59

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2816.19 | 701.66 | 712.35
Net Site Energy | 2816.19 | 701.66 | 712.35
Total Source Energy | 7142.36 | 1779.55 | 1806.64
Net Source Energy | 7142.36 | 1779.55 | 1806.64
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.62 | 77.12 | 0 | 0 | 0 | 0
Cooling | 336.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 39.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 209.56 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 519.1 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2030.5 | 785.7 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.35 | 0.242
North Total or Average |  |  | 72.38 | 3.69 | 0.361 | 0.251
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.343 | 0.237
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1479.57 | 1181.66 | 297.9 | 0.8 | 3.7
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1504.76 | 1201.79 | 302.98 | 0.8 | 3.7
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1598.23 | 1276.43 | 321.8 | 0.8 | 3.7
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1354.14 | 1081.49 | 272.65 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1445.28 | 1154.28 | 291 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2136.39 | 1706.24 | 430.15 | 0.8 | 3.67
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6912.11 | 5520.39 | 1391.72 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5586.85 | 4461.97 | 1124.88 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6715.32 | 5363.23 | 1352.1 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1902.89 | 1519.75 | 383.14 | 0.8 | 3.7
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1687.47 | 1347.71 | 339.76 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6713.99 | 5362.17 | 1351.83 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2175.27 | 1737.29 | 437.98 | 0.8 | 3.66
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6023.66 | 4810.83 | 1212.83 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1693.04 | 1352.16 | 340.89 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2118.15 | 1691.67 | 426.48 | 0.8 | 3.68
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6900.34 | 5511 | 1389.35 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5704.61 | 4556.01 | 1148.59 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6891.47 | 5503.91 | 1387.56 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1950.15 | 1557.5 | 392.65 | 0.8 | 3.7
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1726.75 | 1379.08 | 347.67 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6328.64 | 5054.4 | 1274.24 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1691.66 | 1351.05 | 340.61 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6208.41 | 4958.38 | 1250.03 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1731.95 | 1383.23 | 348.72 | 0.8 | 3.7
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2560.36 | 2044.84 | 515.51 | 0.8 | 3.55
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8620.66 | 6884.94 | 1735.72 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7077.5 | 5652.48 | 1425.02 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8623.28 | 6887.03 | 1736.25 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2422.29 | 1934.58 | 487.72 | 0.8 | 3.59
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2208.27 | 1763.64 | 444.62 | 0.8 | 3.65
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8168.52 | 6487.82 | 1680.7 | 0.79 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2104.65 | 1679.77 | 424.88 | 0.8 | 3.68
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8111.59 | 6436.93 | 1674.66 | 0.79 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2201.1 | 1757.92 | 443.18 | 0.8 | 3.65
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7526.59 | 6011.15 | 1515.44 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3557.39 | 2841.13 | 716.26 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3179.84 | 2539.59 | 640.24 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6158.02 | 4523.69 | 1634.33 | 0.73 | 3.82
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17402.37 | 11885.72 | 5516.64 | 0.68 | 3.67
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1219.85 | 974.24 | 245.61 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 888.81 | 709.85 | 178.96 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5901.64 | 4385.88 | 1515.76 | 0.74 | 3.85
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27236.97 | 21596.2 | 5640.76 | 0.79 | 3.75
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2877.51 | 1945.43 | 932.07 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6106.68 | 4490.3 | 1616.38 | 0.74 | 3.83
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 340.23 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 653.62 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1735.79 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 692.93 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 698.21 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 1735.79 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 631.88 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 594.93 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2314.39 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1240.16 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4842.65 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3900.15 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4844.87 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1428.72 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1406.34 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4836.63 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1285.99 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4817.21 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1394.47 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 170.11 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 121.21 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 21626.74 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 10113.73 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 4944.44 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7581.32 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 23857.56 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1687.98 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 17285.21 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1371.42 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 8461.52 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 76965.66 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 4712.7 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 8730.23 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.06 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.89 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 57.86 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.46 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 52.07 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.58 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.15 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 265.79 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 214.83 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 258.23 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 73.17 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.89 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 258.18 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.65 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 231.63 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.1 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.45 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 265.34 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 219.36 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 265 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.99 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.4 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 243.36 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.05 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 238.73 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.6 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.45 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 331.49 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 272.15 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 331.59 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.15 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.92 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 310.34 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.81 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 307.58 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.64 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.53 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.38 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 527.39 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.21 | 249.27 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.19 | 222.81 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 356.32 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.72 | 835.78 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 85.48 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 62.28 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 351.11 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.62 | 1845.07 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 134.41 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 354.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 18051.7277 | 15.6632 | 129.8862 | 0 | 0.0001 | 783584.6047 | 6644.0109
February | 16290.4869 | 14.1339 | 117.4153 | 0 | 0.0001 | 708350.36 | 5996.3943
March | 17833.9199 | 15.4609 | 130.6958 | 0 | 0.0001 | 788479.2653 | 6571.0974
April | 17308.2623 | 14.9931 | 129.0184 | 0 | 0.0001 | 778368.9553 | 6384.0488
May | 18172.8714 | 15.7255 | 138.4226 | 0 | 0.0001 | 835116.7175 | 6711.9832
June | 17728.3973 | 15.3307 | 136.8575 | 0 | 0.0001 | 825681.7049 | 6553.3749
July | 19156.4265 | 16.5499 | 150.6922 | 0 | 0.0001 | 909160.1883 | 7089.8275
August | 19465.688 | 16.8145 | 153.5823 | 0 | 0.0001 | 926598.5004 | 7205.681
September | 18652.0413 | 16.1149 | 146.5826 | 0 | 0.0001 | 884365.0076 | 6902.7205
October | 18634.8321 | 16.1123 | 144.2575 | 0 | 0.0001 | 870328.7815 | 6889.6707
November | 17516.696 | 15.1675 | 131.6738 | 0 | 0.0001 | 794393.5079 | 6464.2895
December | 18106.4867 | 15.699 | 132.3761 | 0 | 0.0001 | 798614.779 | 6670.5596
Annual Sum or Average | 216917.8361 | 187.7653 | 1641.4603 | 0 | 0.0008 | 9903040 | 80083.6583
Minimum of Months | 16290.4869 | 14.1339 | 117.4153 | 0 | 0.0001 | 708350.36 | 5996.3943
Maximum of Months | 19465.688 | 16.8145 | 153.5823 | 0 | 0.0001 | 926598.5004 | 7205.681
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 160664000000 | 101749.94 | 28-JAN-08:00 | 26328.66 | 57998.833 | 6840.391 | 0 | 10497.278 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 145238000000 | 107795.49 | 12-FEB-08:00 | 26328.66 | 57998.833 | 7228.336 | 0 | 16154.883 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 161668000000 | 102808.003 | 04-MAR-08:00 | 26328.66 | 57998.833 | 6919.846 | 0 | 11475.886 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 159595000000 | 105820.172 | 11-APR-19:15 | 36517.967 | 38824.77 | 7806.515 | 0 | 20105.142 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 171230000000 | 114391.068 | 28-MAY-07:00 | 26328.66 | 57998.833 | 7705.065 | 0 | 22273.731 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 169296000000 | 109312.857 | 17-JUN-07:00 | 26328.66 | 57998.833 | 7559.201 | 0 | 17341.386 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 186412000000 | 120193.037 | 09-JUL-07:00 | 26328.66 | 57998.833 | 7991.654 | 0 | 27789.112 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 189988000000 | 122699.281 | 13-AUG-07:00 | 26328.66 | 57998.833 | 8151.254 | 0 | 30135.756 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 181328000000 | 119950.667 | 09-SEP-07:00 | 26328.66 | 57998.833 | 7988.082 | 0 | 27550.314 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 178450000000 | 112029.263 | 07-OCT-07:00 | 26328.66 | 57998.833 | 7697.339 | 0 | 19919.653 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 162881000000 | 106911.205 | 12-NOV-08:00 | 26328.66 | 57998.833 | 7330.442 | 0 | 15168.492 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 163746000000 | 103004.919 | 16-DEC-08:00 | 26328.66 | 57998.833 | 6956.832 | 0 | 11635.817 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2030500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 145238000000 | 101749.94 |  | 26328.66 | 38824.77 | 6840.391 | 0 | 10497.278 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 189988000000 | 122699.281 |  | 36517.967 | 57998.833 | 8151.254 | 0 | 30135.756 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 69866.37 | 6614.42 | 0 | 76480.79
Cost per Total Building Area ($/m2) | 17.41 | 1.65 | 0 | 19.06
Cost per Net Conditioned Building Area ($/m2) | 17.67 | 1.67 | 0 | 19.35

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3077.41 | 766.75 | 778.42
Net Site Energy | 3077.41 | 766.75 | 778.42
Total Source Energy | 8990.95 | 2240.13 | 2274.24
Net Source Energy | 8990.95 | 2240.13 | 2274.24
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 30.87 | 154.37 | 0 | 0 | 0 | 0
Cooling | 510.98 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 241.69 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 467.8 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2265.76 | 811.65 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.252 | 0.162 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.252 | 0.162 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.252 | 0.162 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.35 | 0.242
North Total or Average |  |  | 72.38 | 3.69 | 0.361 | 0.251
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.343 | 0.237
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1551.11 | 1201.74 | 349.37 | 0.77 | 3.66
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1573.88 | 1222.01 | 351.87 | 0.78 | 3.66
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1673.96 | 1311.29 | 362.67 | 0.78 | 3.67
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1468.31 | 1172.67 | 295.64 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1515.99 | 1210.75 | 305.24 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2516.17 | 2009.56 | 506.62 | 0.8 | 3.57
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7628.87 | 6087.5 | 1541.37 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6137.96 | 4902.11 | 1235.85 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7452.55 | 5929.05 | 1523.5 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2153.77 | 1720.12 | 433.65 | 0.8 | 3.67
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2063.25 | 1647.83 | 415.42 | 0.8 | 3.69
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7770.41 | 6205.88 | 1564.53 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2478.99 | 1979.85 | 499.13 | 0.8 | 3.58
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7011.57 | 5599.82 | 1411.74 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2023.24 | 1615.87 | 407.37 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2526.55 | 2017.85 | 508.71 | 0.8 | 3.56
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7718.57 | 6164.47 | 1554.09 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6367.06 | 5085.09 | 1281.97 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7705.12 | 6153.73 | 1551.38 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2256.99 | 1802.56 | 454.43 | 0.8 | 3.64
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2170.08 | 1733.14 | 436.93 | 0.8 | 3.66
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7498.6 | 5988.79 | 1509.8 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2014.38 | 1608.79 | 405.58 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7360.48 | 5878.49 | 1481.99 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2133.22 | 1703.71 | 429.51 | 0.8 | 3.67
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3316.39 | 2648.65 | 667.74 | 0.8 | 3.35
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11596.47 | 9261.58 | 2334.89 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9520.12 | 7603.29 | 1916.83 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11602.01 | 9266.01 | 2336 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3314.99 | 2647.53 | 667.46 | 0.8 | 3.35
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3200.11 | 2555.78 | 644.33 | 0.8 | 3.38
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11287.76 | 9015.03 | 2272.73 | 0.8 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2973.28 | 2374.63 | 598.65 | 0.8 | 3.44
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11202.73 | 8947.12 | 2255.61 | 0.8 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3158.99 | 2522.94 | 636.05 | 0.8 | 3.39
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7650.89 | 6110.42 | 1540.47 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4132.95 | 3300.8 | 832.15 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3869.5 | 3090.4 | 779.1 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9399.69 | 7394.6 | 2005.09 | 0.79 | 3.99
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18556.66 | 12545.85 | 6010.81 | 0.68 | 3.65
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1167.82 | 932.68 | 235.13 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 843.06 | 659.82 | 183.23 | 0.78 | 3.98
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6084.03 | 4585.43 | 1498.61 | 0.75 | 3.88
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28510.97 | 22770.44 | 5740.53 | 0.8 | 3.77
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3025.07 | 2045.2 | 979.87 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6188.5 | 4604.29 | 1584.21 | 0.74 | 3.85
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 100.07 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 173.17 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 213.44 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 810.3 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 175.14 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 754.6 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 773.68 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 971.22 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 977.9 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 771.92 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1016.29 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2679.33 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2018.64 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2679.33 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 876.29 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 849.51 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2679.33 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 642.53 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2679.33 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 771.63 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1053.43 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2758.09 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2198.85 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2749.94 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 912.3 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 889.91 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2700.31 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 669.83 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2704.5 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 826.89 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1841.87 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 7185.97 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 5792.07 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 7183.44 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2037.71 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2017.54 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 7183.84 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1933.98 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 7156.58 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1999.41 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 61.08 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 86.64 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 653.13 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 60.61 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 89.05 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 447 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 20738.4 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6098.63 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5760.62 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 12465.72 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 26619.33 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1498.44 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 20010.79 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1241.54 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9084.59 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 77286.76 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5378.74 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 9297.8 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.34 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.58 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.72 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.72 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.59 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.77 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.86 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.69 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.46 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.29 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.76 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 292.8 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 236.02 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 284.17 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.82 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.34 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 298.8 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.33 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 269.62 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.8 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.15 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 296.8 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 244.83 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 296.29 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.79 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.45 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 288.35 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.46 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 283.03 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.03 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 127.53 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.7 | 445.92 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.08 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.7 | 446.14 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 127.47 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 123.05 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 434.05 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 114.33 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 430.78 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 121.47 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.2 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.29 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.19 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.2 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.3 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.5 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 536.1 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 289.6 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 271.14 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 637.19 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 866.77 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 81.83 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 56.5 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 374.16 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.72 | 1962.09 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 141.3 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 369.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43027.7552 | 66.2625 | 255.8718 | 0 | 0.0005 | 1275950 | 17719.6465
February | 36775.0099 | 57.1735 | 223.7666 | 0 | 0.0004 | 1115880 | 15200.7975
March | 40605.0916 | 63.2836 | 248.5336 | 0 | 0.0005 | 1239390 | 16800.1116
April | 41799.0656 | 66.2384 | 266.1242 | 0 | 0.0005 | 1327150 | 17407.817
May | 45587.7069 | 72.6947 | 294.4985 | 0 | 0.0006 | 1468670 | 19032.6801
June | 51258.2375 | 82.3307 | 336.7113 | 0 | 0.0006 | 1679210 | 21461.8167
July | 56522.9968 | 91.0203 | 373.4884 | 0 | 0.0007 | 1862630 | 23690.4251
August | 55570.2465 | 89.4441 | 366.7979 | 0 | 0.0007 | 1829260 | 23286.7316
September | 49030.0207 | 78.6457 | 321.0772 | 0 | 0.0006 | 1601240 | 20517.8374
October | 43707.0574 | 69.5129 | 280.6302 | 0 | 0.0005 | 1399500 | 18228.5053
November | 39112.7147 | 61.2488 | 242.1354 | 0 | 0.0005 | 1207490 | 16212.908
December | 42063.4206 | 65.0464 | 252.6654 | 0 | 0.0005 | 1259970 | 17350.4721
Annual Sum or Average | 545059.3233 | 862.9015 | 3462.3006 | 0 | 0.0066 | 17266400 | 226909.7489
Minimum of Months | 36775.0099 | 57.1735 | 223.7666 | 0 | 0.0004 | 1115880 | 15200.7975
Maximum of Months | 56522.9968 | 91.0203 | 373.4884 | 0 | 0.0007 | 1862630 | 23690.4251
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 167436000000 | 107402.009 | 07-JAN-08:15 | 26328.66 | 57998.833 | 7312.464 | 11095.047 | 4582.227 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 146430000000 | 100697.839 | 26-FEB-08:00 | 26328.66 | 57998.833 | 7256.259 | 0 | 9029.31 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 162638000000 | 102123.255 | 04-MAR-08:15 | 26328.66 | 57998.833 | 7081.573 | 5652.224 | 4977.188 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 174154000000 | 118353.163 | 21-APR-19:15 | 36517.967 | 38824.77 | 9262.837 | 0 | 31181.811 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 192725000000 | 125717.226 | 31-MAY-19:15 | 36517.967 | 38824.77 | 9758.653 | 0 | 38050.058 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 220353000000 | 148422.886 | 27-JUN-19:15 | 36517.967 | 38824.77 | 11111.911 | 0 | 59402.46 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 244422000000 | 147044.448 | 25-JUL-19:15 | 36517.967 | 38824.77 | 10970.611 | 0 | 58165.322 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 240043000000 | 144238.651 | 05-AUG-07:00 | 26328.66 | 57998.833 | 10173.326 | 0 | 49653.054 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 210121000000 | 132188.681 | 02-SEP-07:00 | 26328.66 | 57998.833 | 9416.679 | 0 | 38359.731 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 183649000000 | 114511.307 | 07-OCT-07:00 | 26328.66 | 57998.833 | 8381.213 | 0 | 21717.822 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 158452000000 | 104549.941 | 11-NOV-08:00 | 26328.66 | 57998.833 | 7701.383 | 0 | 12436.287 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 165339000000 | 107019.899 | 30-DEC-08:15 | 26328.66 | 57998.833 | 7290.68 | 10924.142 | 4392.806 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2265760000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 146430000000 | 100697.839 |  | 26328.66 | 38824.77 | 7081.573 | 0 | 4392.806 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 244422000000 | 148422.886 |  | 36517.967 | 57998.833 | 11111.911 | 11095.047 | 59402.46 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 59580.84 | 6540.61 | 0 | 66121.45
Cost per Total Building Area ($/m2) | 14.84 | 1.63 | 0 | 16.47
Cost per Net Conditioned Building Area ($/m2) | 15.07 | 1.65 | 0 | 16.73

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2921.55 | 727.91 | 739
Net Site Energy | 2921.55 | 727.91 | 739
Total Source Energy | 7059.6 | 1758.92 | 1785.71
Net Source Energy | 7059.6 | 1758.92 | 1785.71
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 28.51 | 217.04 | 0 | 0 | 0 | 0
Cooling | 221.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 199.16 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 583.29 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1931.74 | 989.81 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.477 | 0.514 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.39 | 0.223 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.39 | 0.223 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.39 | 0.223 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.39 | 0.223 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 5.838 | 0.61 | 0.474 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.39 | 0.223 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.39 | 0.223 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.39 | 0.223 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.84 | 0.548 | 0.403
North Total or Average |  |  | 72.38 | 5.84 | 0.565 | 0.423
Non-North Total or Average |  |  | 111.83 | 5.84 | 0.536 | 0.39
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1765.71 | 1410.19 | 355.52 | 0.8 | 3.7
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1812.82 | 1447.82 | 365 | 0.8 | 3.7
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1824.71 | 1457.31 | 367.39 | 0.8 | 3.7
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1103.26 | 881.12 | 222.14 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1245.26 | 994.53 | 250.73 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2431.17 | 1941.66 | 489.5 | 0.8 | 3.59
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9024.25 | 7207.27 | 1816.99 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7662.74 | 6119.88 | 1542.85 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8795.92 | 7024.91 | 1771.01 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2387.66 | 1906.91 | 480.74 | 0.8 | 3.6
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1617.47 | 1291.8 | 325.67 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6646.37 | 5308.15 | 1338.21 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2150.1 | 1717.19 | 432.91 | 0.8 | 3.67
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5930.72 | 4736.6 | 1194.12 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1630.77 | 1302.42 | 328.35 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2408.24 | 1923.35 | 484.89 | 0.8 | 3.6
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9060.91 | 7236.54 | 1824.37 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7876.42 | 6290.54 | 1585.87 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9050.05 | 7227.87 | 1822.18 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2451.21 | 1957.68 | 493.54 | 0.8 | 3.58
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1671.32 | 1334.81 | 336.51 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6302 | 5033.12 | 1268.87 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1678.45 | 1340.5 | 337.95 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6181.65 | 4937 | 1244.64 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1684.45 | 1345.3 | 339.16 | 0.8 | 3.7
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2740.47 | 2188.69 | 551.78 | 0.8 | 3.5
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10293.43 | 8220.9 | 2072.53 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8884.88 | 7095.95 | 1788.92 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10298.54 | 8224.99 | 2073.56 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2768.93 | 2211.42 | 557.51 | 0.8 | 3.5
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2017.1 | 1610.97 | 406.13 | 0.8 | 3.7
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7573.74 | 6048.81 | 1524.93 | 0.8 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1950.88 | 1558.08 | 392.8 | 0.8 | 3.7
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7505.41 | 5994.24 | 1511.18 | 0.8 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2015.41 | 1609.62 | 405.79 | 0.8 | 3.7
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6612.22 | 5280.89 | 1331.34 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3797.71 | 3033.06 | 764.65 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3429.88 | 2739.29 | 690.59 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4851.83 | 3874.94 | 976.89 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15449.01 | 11746.78 | 3702.23 | 0.76 | 3.91
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1172.38 | 936.33 | 236.05 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8558.14 | 6307.38 | 2250.76 | 0.74 | 3.83
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 843.53 | 673.69 | 169.84 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4878.97 | 3853.95 | 1025.02 | 0.79 | 4
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25790.3 | 20597.56 | 5192.74 | 0.8 | 3.77
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2044.93 | 1550.83 | 494.11 | 0.76 | 3.9
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4402.76 | 3443.13 | 959.63 | 0.78 | 3.98
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 85.42 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 564.48 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 74.43 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 639.54 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 639.54 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 760.29 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 755.12 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 639.54 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 858 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1918.62 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 754.4 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 718.8 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 695.15 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 665.74 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 897.4 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 1940.58 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 808.14 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 778.22 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 639.54 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 729.47 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1558.6 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6117.09 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4951.81 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6117.36 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1758.36 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1737.44 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6117.1 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1636.12 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6093.21 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1726.71 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 402.1 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 276.98 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 19178.58 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 10977.44 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5436.34 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7411.02 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 28329.92 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1627.5 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 19129.53 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1346.5 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 8506.34 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 74818.66 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 4895.82 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 7988.46 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.26 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.75 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.23 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 67.9 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.71 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.17 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 42.42 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 47.88 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.49 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 347.01 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 294.66 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 338.23 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.81 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 62.2 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 255.57 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.68 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 228.06 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 62.71 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.6 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 348.42 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 302.87 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 348 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.26 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.27 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 242.33 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.54 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 237.7 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.77 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.38 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 395.82 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 341.65 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 396.01 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.47 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.56 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 291.24 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.02 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 288.61 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.5 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.25 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.86 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 463.32 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 266.11 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.21 | 240.33 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 339.97 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.84 | 969.75 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 82.15 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 499.11 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 59.11 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 333.74 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.56 | 1774.86 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.11 | 127.59 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 294.56 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19765.2707 | 17.2074 | 131.9505 | 0 | 0.0001 | 795994.1193 | 7243.3692
February | 16872.2726 | 14.6662 | 116.6734 | 0 | 0.0001 | 703853.4216 | 6195.4878
March | 18639.9615 | 16.2084 | 127.9002 | 0 | 0.0001 | 771576.4678 | 6841.5404
April | 17758.1766 | 15.4265 | 124.5593 | 0 | 0.0001 | 751434.5028 | 6526.1603
May | 18149.6898 | 15.7494 | 130.3744 | 0 | 0.0001 | 786529.3776 | 6679.4055
June | 17541.7477 | 15.2083 | 128.4295 | 0 | 0.0001 | 774806.0626 | 6463.0616
July | 18393.8185 | 15.9323 | 137.3157 | 0 | 0.0001 | 828427.2606 | 6785.0762
August | 18352.1869 | 15.8954 | 137.1419 | 0 | 0.0001 | 827379.4186 | 6770.1373
September | 18110.3737 | 15.6804 | 136.3375 | 0 | 0.0001 | 822530.7286 | 6683.9912
October | 18376.2814 | 15.926 | 135.5942 | 0 | 0.0001 | 818034.723 | 6773.7543
November | 17671.5036 | 15.345 | 125.0477 | 0 | 0.0001 | 754385.7964 | 6497.6528
December | 19361.3916 | 16.8496 | 130.3635 | 0 | 0.0001 | 786425.7721 | 7098.7441
Annual Sum or Average | 218992.6745 | 190.0949 | 1561.6878 | 0 | 0.0008 | 9421380 | 80558.3807
Minimum of Months | 16872.2726 | 14.6662 | 116.6734 | 0 | 0.0001 | 703853.4216 | 6195.4878
Maximum of Months | 19765.2707 | 17.2074 | 137.3157 | 0 | 0.0001 | 828427.2606 | 7243.3692
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 163209000000 | 106164.978 | 01-JAN-08:15 | 26328.66 | 57998.833 | 6581.041 | 10709.509 | 4462.157 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 144316000000 | 101716.044 | 18-FEB-08:00 | 26328.66 | 57998.833 | 6782.992 | 0 | 10520.781 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 158202000000 | 100489.904 | 11-MAR-08:00 | 26328.66 | 57998.833 | 6645.157 | 0 | 9432.476 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 154072000000 | 102376.377 | 29-APR-07:00 | 26328.66 | 57998.833 | 6790.72 | 0 | 11173.387 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 161268000000 | 101998.06 | 29-MAY-07:00 | 26328.66 | 57998.833 | 6760.791 | 0 | 10824.999 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 158864000000 | 108407.191 | 17-JUN-07:00 | 26328.66 | 57998.833 | 7363.099 | 0 | 16631.821 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 169859000000 | 119904.073 | 02-JUL-19:30 | 36433.634 | 38807.225 | 8883.441 | 0 | 33213.994 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 169644000000 | 105701.44 | 27-AUG-07:00 | 26328.66 | 57998.833 | 7145.465 | 0 | 14143.704 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 168650000000 | 113718.455 | 28-SEP-19:00 | 36517.967 | 38824.77 | 8390.777 | 0 | 27419.163 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 167728000000 | 104771.431 | 21-OCT-07:00 | 26328.66 | 57998.833 | 7064.673 | 0 | 13294.487 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 154677000000 | 102496.621 | 12-NOV-08:00 | 26328.66 | 57998.833 | 6875.678 | 0 | 11208.672 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 161247000000 | 104023.071 | 25-DEC-08:15 | 26328.66 | 57998.833 | 6498.627 | 8354.635 | 4757.537 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1931740000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 144316000000 | 100489.904 |  | 26328.66 | 38807.225 | 6498.627 | 0 | 4462.157 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 169859000000 | 119904.073 |  | 36517.967 | 57998.833 | 8883.441 | 10709.509 | 33213.994 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 77772.93 | 8341.77 | 0 | 86114.7
Cost per Total Building Area ($/m2) | 19.38 | 2.08 | 0 | 21.46
Cost per Net Conditioned Building Area ($/m2) | 19.67 | 2.11 | 0 | 21.78

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3429.19 | 854.4 | 867.41
Net Site Energy | 3429.19 | 854.4 | 867.41
Total Source Energy | 9320.93 | 2322.35 | 2357.71
Net Source Energy | 9320.93 | 2322.35 | 2357.71
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 164.36 | 402.19 | 0 | 0 | 0 | 0
Cooling | 379.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 219.14 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 592.66 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2244.87 | 1184.33 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.388 | 0.283
North Total or Average |  |  | 72.38 | 3.69 | 0.388 | 0.281
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.387 | 0.285
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1721 | 1271.05 | 449.95 | 0.74 | 3.61
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1742.16 | 1289.64 | 452.52 | 0.74 | 3.61
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1825.57 | 1365.33 | 460.24 | 0.75 | 3.62
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1636.91 | 1238.24 | 398.67 | 0.76 | 3.63
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1686.7 | 1282.88 | 403.82 | 0.76 | 3.64
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2205.99 | 1722.38 | 483.61 | 0.78 | 3.63
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7791.54 | 5899.09 | 1892.45 | 0.76 | 3.01
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6242.73 | 4739.75 | 1502.98 | 0.76 | 3.01
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7620.48 | 5747.41 | 1873.07 | 0.75 | 3.01
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2102.64 | 1615.01 | 487.62 | 0.77 | 3.64
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1930.73 | 1506.6 | 424.13 | 0.78 | 3.67
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7530.51 | 5837.11 | 1693.4 | 0.78 | 3.03
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2392.61 | 1863.15 | 529.46 | 0.78 | 3.57
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6998.17 | 5356.52 | 1641.65 | 0.77 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1926.6 | 1499.11 | 427.49 | 0.78 | 3.66
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2198.98 | 1716.03 | 482.96 | 0.78 | 3.63
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7789.7 | 5907.13 | 1882.57 | 0.76 | 3.01
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6332.62 | 4834.95 | 1497.67 | 0.76 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7781.73 | 5900.06 | 1881.68 | 0.76 | 3.01
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2159.15 | 1665.48 | 493.67 | 0.77 | 3.63
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1985.45 | 1556.39 | 429.06 | 0.78 | 3.67
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7279.48 | 5610.12 | 1669.36 | 0.77 | 3.03
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1915.21 | 1488.78 | 426.43 | 0.78 | 3.66
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7184.42 | 5524.33 | 1660.09 | 0.77 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1971.82 | 1543.97 | 427.85 | 0.78 | 3.67
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2985.88 | 2276.6 | 709.27 | 0.76 | 3.39
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12108.59 | 8881.19 | 3227.4 | 0.73 | 2.99
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9826.35 | 7247.08 | 2579.26 | 0.74 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12116.84 | 8888.25 | 3228.59 | 0.73 | 2.99
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3295.2 | 2458.21 | 836.99 | 0.75 | 3.29
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3193.36 | 2370.32 | 823.04 | 0.74 | 3.31
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11825.99 | 8653.35 | 3172.65 | 0.73 | 2.99
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3051.97 | 2248.69 | 803.29 | 0.74 | 3.34
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11761.53 | 8598.39 | 3163.14 | 0.73 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3168.19 | 2352.7 | 815.49 | 0.74 | 3.32
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8067.21 | 6442.92 | 1624.29 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4287.52 | 3257.8 | 1029.72 | 0.76 | 3.9
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3996.62 | 3012.12 | 984.5 | 0.75 | 3.88
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11435.64 | 7897.12 | 3538.53 | 0.69 | 3.69
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17933.28 | 12124.39 | 5808.89 | 0.68 | 3.65
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1182.17 | 944.15 | 238.02 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1020.96 | 749.22 | 271.74 | 0.73 | 3.82
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7151.44 | 4955.79 | 2195.66 | 0.69 | 3.7
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30161.89 | 22937.95 | 7223.94 | 0.76 | 3.66
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3015.92 | 2039.01 | 976.91 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7970.79 | 5388.92 | 2581.87 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 294.13 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 368.35 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 415.54 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1367.82 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 410.01 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 979.34 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1000.97 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1207.83 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1205.05 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 997.61 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1370.6 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3745.9 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2885.89 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3686.17 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1152.44 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1123.92 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3527.66 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 881.92 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3560.85 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1047.49 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1421.58 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3902.95 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3118.36 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3892.68 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1202.21 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1179 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3844.04 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 954.14 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3841.35 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1117.4 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2587.94 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 10583.99 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 8534.04 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 10580.4 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2895.14 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2875.86 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 10583.67 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2857.61 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 10549.66 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2853.86 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 197.65 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 253.63 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 287.34 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1204.56 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 69.4 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 175.72 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 207.61 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 776.01 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 23957.32 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6504.46 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6052.48 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 12362.99 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 32822.66 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1632.95 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 26346.65 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1475.61 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 10427.78 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 80499.1 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 7013.08 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 11190.44 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.92 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.15 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.29 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.26 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.28 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.36 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.35 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 60.51 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.72 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.14 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.7 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 265.76 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 214.32 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 257.61 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.13 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.54 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 271.04 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.01 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 244.77 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.94 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.35 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 266.68 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 220.23 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 266.3 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.86 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.28 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 258.62 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.38 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 253.93 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.6 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.51 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 383.05 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 315.02 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 383.42 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.56 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.96 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.96 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.61 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 369.12 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.25 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.62 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.79 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.9 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.75 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.22 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.55 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.65 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.42 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 565.27 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 268.7 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.21 | 245.78 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 565.73 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.72 | 837.65 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 82.83 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 58.93 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 357.07 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.63 | 1860.26 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 140.87 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 372.31 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42706.126 | 75.5891 | 203.51 | 0 | 0.0008 | 12654.4851 | 18147.8185
February | 36525.343 | 64.7317 | 174.5117 | 0 | 0.0007 | 10851.3714 | 15528.8578
March | 35426.816 | 63.7104 | 174.3738 | 0 | 0.0007 | 10843.1368 | 15146.4479
April | 31532.8406 | 57.696 | 160.6644 | 0 | 0.0007 | 9990.9942 | 13571.9789
May | 33696.807 | 63.173 | 180.0695 | 0 | 0.0007 | 11198.2364 | 14642.1292
June | 36836.9512 | 70.2582 | 203.466 | 0 | 0.0008 | 12653.6251 | 16116.1663
July | 40404.9029 | 77.5005 | 225.5873 | 0 | 0.0009 | 14029.4998 | 17717.1218
August | 40281.1408 | 77.2877 | 225.0324 | 0 | 0.0009 | 13994.9946 | 17665.1061
September | 34236.7312 | 65.1042 | 188.0291 | 0 | 0.0008 | 11693.5373 | 14960.7717
October | 33778.7632 | 62.9396 | 178.3704 | 0 | 0.0007 | 11092.447 | 14642.3524
November | 33764.8159 | 61.5222 | 170.6142 | 0 | 0.0007 | 10609.6429 | 14509.0841
December | 39874.5691 | 71.0064 | 192.3858 | 0 | 0.0008 | 11962.9282 | 16983.7918
Annual Sum or Average | 439065.8069 | 810.519 | 2276.6144 | 0 | 0.0093 | 141574.8987 | 189631.6264
Minimum of Months | 31532.8406 | 57.696 | 160.6644 | 0 | 0.0007 | 9990.9942 | 13571.9789
Maximum of Months | 42706.126 | 77.5005 | 225.5873 | 0 | 0.0009 | 14029.4998 | 18147.8185
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 200655000000 | 130612.124 | 15-JAN-08:15 | 26328.66 | 57998.833 | 7162.379 | 38769.527 | 267.948 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 172064000000 | 119594.256 | 05-FEB-08:15 | 26328.66 | 57998.833 | 6926.57 | 26608.617 | 1646.798 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 171933000000 | 112260.325 | 19-MAR-07:15 | 26328.66 | 57998.833 | 6873.096 | 17365.003 | 3609.955 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 158421000000 | 105461.629 | 05-APR-19:15 | 36517.967 | 38824.77 | 7862.976 | 0 | 19690.138 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 177564000000 | 117486.473 | 15-MAY-19:15 | 36517.967 | 38824.77 | 8576.995 | 0 | 31000.962 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 200641000000 | 135393.697 | 30-JUN-19:15 | 36517.967 | 38824.77 | 9680.996 | 0 | 50285.186 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 222457000000 | 143062.445 | 24-JUL-19:30 | 36517.967 | 38824.77 | 9938.232 | 0 | 55215.698 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 221910000000 | 143067.88 | 17-AUG-19:15 | 36517.967 | 38824.77 | 9941.759 | 0 | 55217.606 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 185417000000 | 125454.193 | 17-SEP-07:00 | 26328.66 | 57998.833 | 8347.317 | 0 | 32694.605 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 175886000000 | 119912.214 | 14-OCT-07:00 | 26328.66 | 57998.833 | 8090.453 | 0 | 27409.491 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 168231000000 | 113941.216 | 04-NOV-07:00 | 26328.66 | 57998.833 | 7754.89 | 0 | 21774.055 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 189689000000 | 122471.123 | 21-DEC-07:15 | 24311.729 | 51279.599 | 7110.027 | 36802.068 | 401.922 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2244870000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 158421000000 | 105461.629 |  | 24311.729 | 38824.77 | 6873.096 | 0 | 267.948 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 222457000000 | 143067.88 |  | 36517.967 | 57998.833 | 9941.759 | 38769.527 | 55217.606 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 42972.38 | 11820.73 | 0 | 54793.11
Cost per Total Building Area ($/m2) | 10.71 | 2.95 | 0 | 13.65
Cost per Net Conditioned Building Area ($/m2) | 10.87 | 2.99 | 0 | 13.86

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3185.8 | 793.75 | 805.84
Net Site Energy | 3185.8 | 793.75 | 805.84
Total Source Energy | 8251.83 | 2055.97 | 2087.28
Net Source Energy | 8251.83 | 2055.97 | 2087.28
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 88.36 | 270.67 | 0 | 0 | 0 | 0
Cooling | 332.78 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.98 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 240.82 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 581.48 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2144.17 | 1041.63 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.388 | 0.283
North Total or Average |  |  | 72.38 | 3.69 | 0.388 | 0.281
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.387 | 0.285
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1524.49 | 1217.54 | 306.95 | 0.8 | 3.7
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1547.76 | 1236.12 | 311.63 | 0.8 | 3.7
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1606.2 | 1282.8 | 323.4 | 0.8 | 3.7
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1490.02 | 1190.01 | 300.01 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1642.13 | 1311.5 | 330.64 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2338.42 | 1867.59 | 470.83 | 0.8 | 3.62
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7845.42 | 6265.79 | 1579.63 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6306.85 | 5037 | 1269.85 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7604.98 | 6073.76 | 1531.22 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2122.4 | 1695.06 | 427.33 | 0.8 | 3.68
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2032.07 | 1622.92 | 409.15 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8165.51 | 6521.43 | 1644.08 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2629.81 | 2100.31 | 529.5 | 0.8 | 3.53
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7324.86 | 5850.04 | 1474.82 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2040.99 | 1630.05 | 410.94 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2328.42 | 1859.6 | 468.82 | 0.8 | 3.62
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7886.01 | 6298.2 | 1587.81 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6486.35 | 5180.36 | 1305.99 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7873.59 | 6288.29 | 1585.31 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2201.13 | 1757.94 | 443.19 | 0.8 | 3.65
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2107.75 | 1683.37 | 424.38 | 0.8 | 3.68
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7766.93 | 6203.1 | 1563.83 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2074.2 | 1656.57 | 417.63 | 0.8 | 3.69
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7619.01 | 6084.96 | 1534.05 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2110.21 | 1685.33 | 424.88 | 0.8 | 3.68
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2877.07 | 2297.79 | 579.28 | 0.8 | 3.47
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10467.61 | 8360.01 | 2107.6 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8596.01 | 6865.25 | 1730.76 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10475.64 | 8366.42 | 2109.21 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2905.51 | 2320.5 | 585.01 | 0.8 | 3.46
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2769.72 | 2212.05 | 557.67 | 0.8 | 3.5
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10234.75 | 8174.04 | 2060.71 | 0.8 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2664.57 | 2128.07 | 536.5 | 0.8 | 3.53
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10147.08 | 8104.02 | 2043.06 | 0.8 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2767.65 | 2210.4 | 557.25 | 0.8 | 3.5
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8731.4 | 6973.38 | 1758.02 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4271.48 | 3411.44 | 860.04 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3851.3 | 3075.86 | 775.44 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7864.62 | 6281.12 | 1583.5 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15706.21 | 11627.99 | 4078.22 | 0.74 | 3.84
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1242.82 | 992.58 | 250.23 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10402.17 | 7203.59 | 3198.58 | 0.69 | 3.7
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 830.79 | 663.52 | 167.28 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5962.7 | 4762.14 | 1200.56 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31999.08 | 25556.23 | 6442.85 | 0.8 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2293.39 | 1809.25 | 484.13 | 0.79 | 4
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5668.3 | 4527.02 | 1141.28 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 181.9 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 254.54 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 300.36 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1071.6 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 290.93 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 844.09 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 865.21 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1069.67 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1066.73 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 860.21 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1152.93 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3097.4 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2384.27 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3039.79 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 987.39 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 958.15 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2802.92 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 572.03 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2910.98 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 880.38 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1198.15 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3235 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2598.17 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3225.67 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1032.11 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1008.32 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3170.23 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 772.07 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3169.91 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 944.75 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2170.95 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8663.99 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7001.74 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8661.27 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2412.21 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2391.75 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8658.43 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2340.77 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8626.95 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2371.12 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 88.01 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 143.13 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 174.09 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 911 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 111.72 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 141.54 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 612.48 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 21334.75 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 5815.53 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5335.55 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 9922.23 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 27740.88 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1419.7 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 21268.48 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1192.45 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9438.7 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 78233.9 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5834.45 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 9460.67 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.69 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.96 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.13 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.04 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.1 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.62 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59.52 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.76 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 57.3 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 63.15 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.92 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 301.68 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 242.52 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 292.44 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.61 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.14 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 313.99 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.12 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 281.67 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.48 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.54 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 303.24 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 249.42 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 302.77 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.64 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.05 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 298.66 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 79.76 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 292.98 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.14 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.63 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 402.51 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.54 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 402.82 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.73 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.5 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 393.56 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.46 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 390.19 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.43 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.33 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.54 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.66 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.43 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.42 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.53 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.31 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 611.81 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.26 | 299.3 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 269.86 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 551.07 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.8 | 925.98 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 87.08 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 518.44 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 58.21 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 417.81 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.93 | 2114.05 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 156.43 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 53700.9137 | 88.3539 | 214.6142 | 0 | 0.0009 | 223128.5973 | 22471.2094
February | 46530.3478 | 76.7577 | 187.0476 | 0 | 0.0007 | 194469.8713 | 19490.4394
March | 49490.974 | 82.0041 | 200.9112 | 0 | 0.0008 | 208886.1318 | 20766.1326
April | 46736.1137 | 78.3591 | 194.7055 | 0 | 0.0008 | 202440.6749 | 19700.4202
May | 51405.3624 | 87.1595 | 219.4177 | 0 | 0.0009 | 228141.4172 | 21763.9462
June | 53491.4029 | 91.27 | 231.426 | 0 | 0.0009 | 240631.0528 | 22703.39
July | 59100.8558 | 101.1869 | 257.566 | 0 | 0.001 | 267813.0453 | 25118.1236
August | 57333.6335 | 98.1106 | 249.5905 | 0 | 0.001 | 259519.9698 | 24362.0852
September | 51981.3894 | 88.6936 | 224.8931 | 0 | 0.0009 | 233838.3487 | 22062.4956
October | 49025.0975 | 82.6945 | 206.9349 | 0 | 0.0008 | 215159.4575 | 20714.0954
November | 48210.0013 | 80.1295 | 197.0526 | 0 | 0.0008 | 204876.2114 | 20252.958
December | 54182.3579 | 89.2319 | 217.003 | 0 | 0.0009 | 225612.8098 | 22681.0927
Annual Sum or Average | 621188.45 | 1043.9514 | 2601.1624 | 0 | 0.0102 | 2704520 | 262086.3883
Minimum of Months | 46530.3478 | 76.7577 | 187.0476 | 0 | 0.0007 | 194469.8713 | 19490.4394
Maximum of Months | 59100.8558 | 101.1869 | 257.566 | 0 | 0.001 | 267813.0453 | 25118.1236
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 176899000000 | 118612.989 | 08-JAN-08:15 | 26328.66 | 57998.833 | 7793.309 | 23581.779 | 2825.63 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 154178000000 | 112623.948 | 05-FEB-08:15 | 26328.66 | 57998.833 | 7600.976 | 17328.55 | 3282.151 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 165607000000 | 103337.626 | 12-MAR-07:15 | 26328.66 | 57998.833 | 7380.816 | 6461.463 | 5083.076 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 160497000000 | 107838.771 | 22-APR-19:15 | 36349.301 | 38772.136 | 8941.222 | 0 | 21210.334 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 180873000000 | 113922.959 | 30-MAY-19:15 | 36517.967 | 38824.77 | 9328.839 | 0 | 26685.605 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 190775000000 | 121051.812 | 28-JUN-19:30 | 36517.967 | 38824.77 | 9870.193 | 0 | 33273.104 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 212325000000 | 127631.106 | 30-JUL-19:15 | 36433.634 | 38807.225 | 10309.735 | 0 | 39514.734 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 205751000000 | 127115.48 | 01-AUG-19:15 | 36517.967 | 38824.77 | 10286.119 | 0 | 38920.845 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 185390000000 | 118074.328 | 03-SEP-07:00 | 26328.66 | 57998.833 | 8870.296 | 0 | 24791.761 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 170581000000 | 107324.227 | 01-OCT-19:15 | 36433.634 | 38807.225 | 9048.211 | 0 | 20469.378 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 162428000000 | 111200.731 | 23-NOV-08:15 | 26328.66 | 57998.833 | 7629.097 | 14793.749 | 4365.614 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 178869000000 | 114241.54 | 16-DEC-08:15 | 26328.66 | 57998.833 | 7644.699 | 18992.431 | 3192.138 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2144170000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 154178000000 | 103337.626 |  | 26328.66 | 38772.136 | 7380.816 | 0 | 2825.63 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 212325000000 | 127631.106 |  | 36517.967 | 57998.833 | 10309.735 | 23581.779 | 39514.734 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22186.91 | 7437.87 | 0 | 29624.78
Cost per Total Building Area ($/m2) | 5.53 | 1.85 | 0 | 7.38
Cost per Net Conditioned Building Area ($/m2) | 5.61 | 1.88 | 0 | 7.49

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3157.44 | 786.69 | 798.67
Net Site Energy | 3157.44 | 786.69 | 798.67
Total Source Energy | 4732.01 | 1179 | 1196.95
Net Source Energy | 4732.01 | 1179 | 1196.95
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 116.57 | 369.07 | 0 | 0 | 0 | 0
Cooling | 176.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.93 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 200.13 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 623.37 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1975.52 | 1181.92 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.388 | 0.283
North Total or Average |  |  | 72.38 | 3.69 | 0.388 | 0.281
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.387 | 0.285
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1473.52 | 1176.84 | 296.69 | 0.8 | 3.7
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1505.55 | 1202.42 | 303.14 | 0.8 | 3.7
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1547.89 | 1236.23 | 311.66 | 0.8 | 3.7
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1184.54 | 946.04 | 238.5 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1304.32 | 1041.7 | 262.62 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2069.47 | 1652.79 | 416.68 | 0.8 | 3.69
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7629.82 | 6093.6 | 1536.22 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6304.01 | 5034.73 | 1269.28 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7399.36 | 5909.53 | 1489.82 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2053.05 | 1639.68 | 413.37 | 0.8 | 3.69
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1678.01 | 1340.15 | 337.86 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6749.86 | 5390.81 | 1359.05 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2186.37 | 1746.15 | 440.21 | 0.8 | 3.66
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6040.61 | 4824.37 | 1216.25 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1688.2 | 1348.29 | 339.91 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2059.13 | 1644.53 | 414.59 | 0.8 | 3.69
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7651.46 | 6110.88 | 1540.58 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6476.54 | 5172.52 | 1304.02 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7641.21 | 6102.69 | 1538.52 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2123.33 | 1695.81 | 427.52 | 0.8 | 3.68
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1739.66 | 1389.39 | 350.27 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6403.19 | 5113.95 | 1289.25 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1710.92 | 1366.43 | 344.48 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6282.58 | 5017.61 | 1264.96 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1747.22 | 1395.42 | 351.79 | 0.8 | 3.7
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2478.8 | 1979.71 | 499.09 | 0.8 | 3.58
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9502.84 | 7589.49 | 1913.35 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7964.84 | 6361.17 | 1603.68 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9511.1 | 7596.09 | 1915.01 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2617.24 | 2090.28 | 526.97 | 0.8 | 3.54
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2283.24 | 1823.52 | 459.72 | 0.8 | 3.63
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8386.05 | 6697.57 | 1688.49 | 0.8 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2179.12 | 1740.36 | 438.75 | 0.8 | 3.66
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8316.71 | 6642.19 | 1674.53 | 0.8 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2277.55 | 1818.98 | 458.57 | 0.8 | 3.63
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7238.13 | 5780.77 | 1457.36 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3666.34 | 2928.14 | 738.2 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3327.27 | 2657.34 | 669.93 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6307.79 | 5037.75 | 1270.04 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15274.13 | 11170.23 | 4103.9 | 0.73 | 3.81
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1119.96 | 894.46 | 225.5 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9729.31 | 6805.89 | 2923.42 | 0.7 | 3.72
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 774.69 | 618.71 | 155.98 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5231.16 | 4056.82 | 1174.35 | 0.78 | 3.96
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26561.3 | 21213.32 | 5347.98 | 0.8 | 3.77
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1904.15 | 1490.15 | 414 | 0.78 | 3.98
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4959.89 | 3806.95 | 1152.94 | 0.77 | 3.93
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 75.03 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 184.68 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 234.22 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 951.27 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 239.91 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 772.09 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 790.92 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 967.3 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 981.95 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 786.3 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1079.24 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3050.76 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2288.07 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3050.76 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 943.8 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 916.98 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3050.76 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 685.56 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3050.76 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 837.38 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1125.13 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3091.5 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2468.95 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3084.85 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 989.47 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 967.6 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3050.76 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 762.69 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3050.76 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 903.7 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2040.96 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8304.86 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6698.32 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8304.4 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2314.44 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2293.91 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8302.97 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2232.44 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8274.35 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2277.67 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 76.2 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 109.6 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 795.86 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 43.94 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 85.24 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 509 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 21063.56 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 5973.03 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5508.85 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 9591.18 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 29962.66 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1533.29 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 22784.84 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1308.57 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9387.41 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 77321.98 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5838.55 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 9257.33 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.24 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.58 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.74 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.99 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.75 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.66 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 57.89 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59.52 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 45.55 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 50.16 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 79.58 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 293.39 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 242.41 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 284.53 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.95 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.53 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 259.55 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.07 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 232.28 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.92 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.18 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 294.22 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 249.04 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 293.83 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.65 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 66.9 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 246.22 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.79 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 241.59 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 67.19 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.32 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 365.42 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 306.27 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 365.73 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.64 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.8 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 322.47 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.79 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 319.81 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.58 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.24 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.34 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.5 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.14 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.27 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.6 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 507.18 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.22 | 256.9 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.2 | 233.14 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 441.99 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 874.23 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 78.48 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 54.28 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 343.47 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1827.91 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.11 | 127.59 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 318.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15605.6062 | 20.0613 | 37.7088 | 0 | 0.0002 | 497964.4916 | 6032.564
February | 13102.9107 | 16.9602 | 32.4032 | 0 | 0.0001 | 427921.2261 | 5077.5546
March | 14284.139 | 18.5401 | 35.6496 | 0 | 0.0002 | 470802.6671 | 5540.7524
April | 12737.9662 | 16.7605 | 33.2418 | 0 | 0.0001 | 439044.0312 | 4965.3396
May | 12239.6377 | 16.5071 | 34.5099 | 0 | 0.0001 | 455859.6116 | 4814.174
June | 11526.1636 | 15.8294 | 34.3147 | 0 | 0.0001 | 453324.6988 | 4564.0151
July | 11962.8474 | 16.7172 | 37.4545 | 0 | 0.0002 | 494846.6108 | 4767.7898
August | 11949.4149 | 16.7561 | 37.7804 | 0 | 0.0002 | 499160.235 | 4768.6083
September | 11623.4036 | 16.0053 | 34.8748 | 0 | 0.0001 | 460730.1447 | 4607.0583
October | 12354.8406 | 16.5562 | 34.1559 | 0 | 0.0001 | 451167.6365 | 4848.1004
November | 13684.0878 | 17.8458 | 34.692 | 0 | 0.0001 | 458171.6306 | 5317.0539
December | 15450.4776 | 19.9153 | 37.6754 | 0 | 0.0002 | 497532.3319 | 5978.3235
Annual Sum or Average | 156521.4953 | 208.4544 | 424.4609 | 0 | 0.0018 | 5606530 | 61281.3338
Minimum of Months | 11526.1636 | 15.8294 | 32.4032 | 0 | 0.0001 | 427921.2261 | 4564.0151
Maximum of Months | 15605.6062 | 20.0613 | 37.7804 | 0 | 0.0002 | 499160.235 | 6032.564
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 175463000000 | 110558.79 | 01-JAN-08:15 | 26328.66 | 57998.833 | 6620.262 | 16257.692 | 3268.565 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 150783000000 | 104829.027 | 12-FEB-08:15 | 26328.66 | 57998.833 | 6493.74 | 9645.725 | 4277.292 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 165892000000 | 104949.068 | 11-MAR-08:15 | 26328.66 | 57998.833 | 6525.576 | 9440.957 | 4570.265 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 154702000000 | 101536.672 | 09-APR-07:15 | 26328.66 | 57998.833 | 6414.724 | 5882.731 | 4826.946 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 160627000000 | 105869.502 | 07-MAY-07:00 | 26328.66 | 57998.833 | 7284.096 | 0 | 14173.135 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 159734000000 | 112042.255 | 18-JUN-07:00 | 26328.66 | 57998.833 | 7702.649 | 0 | 19927.334 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 174365000000 | 114290.366 | 24-JUL-19:15 | 36517.967 | 38824.77 | 8673.181 | 0 | 30189.67 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 175885000000 | 113402.894 | 06-AUG-19:45 | 36433.634 | 38807.225 | 8500.205 | 0 | 27096.052 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 162343000000 | 117723.556 | 02-SEP-19:15 | 36349.301 | 38772.136 | 8800.333 | 0 | 31236.008 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 158974000000 | 101876.137 | 29-OCT-07:15 | 26328.66 | 57998.833 | 6471.926 | 5804.419 | 5187.521 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 161442000000 | 109827.662 | 18-NOV-08:15 | 26328.66 | 57998.833 | 6621.666 | 15189.121 | 3604.604 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 175311000000 | 109899.947 | 10-DEC-08:15 | 26328.66 | 57998.833 | 6589.21 | 15675.23 | 3223.236 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1975520000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 150783000000 | 101536.672 |  | 26328.66 | 38772.136 | 6414.724 | 0 | 3223.236 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 175885000000 | 117723.556 |  | 36517.967 | 57998.833 | 8800.333 | 16257.692 | 31236.008 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 39323.89 | 9824.53 | 0 | 49148.42
Cost per Total Building Area ($/m2) | 9.8 | 2.45 | 0 | 12.25
Cost per Net Conditioned Building Area ($/m2) | 9.95 | 2.49 | 0 | 12.43

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3646.65 | 908.58 | 922.41
Net Site Energy | 3646.65 | 908.58 | 922.41
Total Source Energy | 9535.94 | 2375.92 | 2412.1
Net Source Energy | 9535.94 | 2375.92 | 2412.1
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 252.02 | 549.59 | 0 | 0 | 0 | 0
Cooling | 306.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 222.53 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 644.42 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2263.16 | 1383.49 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.388 | 0.283
North Total or Average |  |  | 72.38 | 3.69 | 0.388 | 0.281
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.387 | 0.285
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1737.1 | 1283.51 | 453.59 | 0.74 | 3.61
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1759.31 | 1303.01 | 456.29 | 0.74 | 3.61
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1831.47 | 1371.53 | 459.95 | 0.75 | 3.62
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1623.29 | 1229.29 | 394 | 0.76 | 3.63
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1679.03 | 1279.48 | 399.55 | 0.76 | 3.64
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2225.14 | 1744.71 | 480.44 | 0.78 | 3.63
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7939.43 | 6025.87 | 1913.56 | 0.76 | 3.01
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6333.61 | 4840.65 | 1492.96 | 0.76 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7767.92 | 5872.99 | 1894.93 | 0.76 | 3.01
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2135.21 | 1643.48 | 491.73 | 0.77 | 3.63
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1930.37 | 1514.66 | 415.71 | 0.78 | 3.67
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7544.68 | 5881.75 | 1662.93 | 0.78 | 3.03
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2398.94 | 1877.43 | 521.51 | 0.78 | 3.58
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7009.25 | 5394.76 | 1614.49 | 0.77 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1926.8 | 1507.52 | 419.28 | 0.78 | 3.67
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2216.76 | 1737.07 | 479.7 | 0.78 | 3.63
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7954.93 | 6039.65 | 1915.28 | 0.76 | 3.01
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6455.29 | 4949.32 | 1505.97 | 0.77 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7947.82 | 6033.32 | 1914.5 | 0.76 | 3.01
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2180.23 | 1689.37 | 490.86 | 0.77 | 3.62
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1985.7 | 1565.38 | 420.32 | 0.79 | 3.68
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7294.64 | 5653.97 | 1640.67 | 0.78 | 3.03
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1918.48 | 1499.92 | 418.56 | 0.78 | 3.67
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7199.13 | 5567.12 | 1632.01 | 0.77 | 3.03
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1980.4 | 1556.51 | 423.89 | 0.79 | 3.68
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2979.77 | 2274.77 | 705 | 0.76 | 3.39
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12065.36 | 8871.08 | 3194.28 | 0.74 | 2.99
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9817.47 | 7252.36 | 2565.11 | 0.74 | 2.99
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12073.08 | 8877.71 | 3195.36 | 0.74 | 2.99
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3284.57 | 2453.1 | 831.47 | 0.75 | 3.29
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3157.86 | 2347.25 | 810.61 | 0.74 | 3.32
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11757.19 | 8606.8 | 3150.39 | 0.73 | 2.99
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3020.21 | 2228.33 | 791.88 | 0.74 | 3.35
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11692.74 | 8551.67 | 3141.07 | 0.73 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3143.88 | 2335.17 | 808.71 | 0.74 | 3.32
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8053.94 | 6432.33 | 1621.62 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4300.86 | 3281.67 | 1019.19 | 0.76 | 3.91
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4007.31 | 3032.41 | 974.91 | 0.76 | 3.89
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15300.67 | 10566.56 | 4734.11 | 0.69 | 3.69
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18150.03 | 12270.93 | 5879.1 | 0.68 | 3.65
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1188.25 | 949 | 239.25 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1015.92 | 747.49 | 268.42 | 0.74 | 3.83
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7145.67 | 4975.91 | 2169.75 | 0.7 | 3.71
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30224.85 | 23102.25 | 7122.6 | 0.76 | 3.67
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3024.95 | 2045.12 | 979.83 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7933.26 | 5363.54 | 2569.72 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 612.43 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 627.53 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 677.53 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1959.32 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 646.46 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1274.88 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1298.36 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1516.63 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1511.24 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1296.5 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1781.23 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4858.44 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3782.11 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4782.85 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1440.13 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1410.37 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4488.86 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1030.26 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4663.86 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1340.88 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1838.94 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5031.87 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4030.2 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5016.05 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1494.86 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1471.49 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4972.49 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1261.51 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4963.6 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1414.57 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3347.07 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 13744.97 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 11088.39 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 13736.91 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 3698.04 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 3679.93 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 13744.52 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 3722.75 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 13703.51 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 3651.16 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 502.6 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 505.19 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 539.5 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1789.49 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 283.44 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 349.71 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 386.6 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1150.98 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12789.69 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6817.89 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6364.52 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 16220.06 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 37276.13 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1613.69 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 30778.32 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1544.98 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 11335.09 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 81833.01 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 8152.45 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 12103.68 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.94 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.99 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.15 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.21 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.05 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.94 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.98 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 60.89 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.4 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.13 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.17 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 272.35 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 220.78 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 264.09 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.64 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.4 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.07 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.22 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 248.27 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.82 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.75 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 273.09 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 226.66 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 272.75 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.41 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.21 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 262.52 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.4 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 257.74 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.52 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.6 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 383.94 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 315.97 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 384.29 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.51 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.15 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 370.19 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.92 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 367.33 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.52 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.59 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.6 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.71 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.67 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.9 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.11 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.23 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.65 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 564.34 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 272.16 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.21 | 248.76 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.65 | 757 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.73 | 847.78 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 83.26 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 59.01 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 361.38 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.66 | 1885.93 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 141.29 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 370.56 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 85159.3702 | 145.4775 | 409.0625 | 0 | 0.0013 | 94158.384 | 35992.3357
February | 71438.3631 | 122.1224 | 343.6597 | 0 | 0.0011 | 79104.0424 | 30201.2664
March | 71408.2463 | 122.5045 | 346.1144 | 0 | 0.0011 | 79669.7021 | 30229.9948
April | 60665.6203 | 105.1732 | 300.6284 | 0 | 0.0009 | 69201.1976 | 25787.2049
May | 63724.4157 | 112.0057 | 324.9558 | 0 | 0.001 | 74803.2854 | 27233.6571
June | 68962.2695 | 122.433 | 358.9849 | 0 | 0.0011 | 82638.3237 | 29588.8736
July | 76259.7666 | 135.8772 | 399.9009 | 0 | 0.0012 | 92057.8459 | 32766.6389
August | 73407.0521 | 130.7226 | 384.5113 | 0 | 0.0012 | 88515.033 | 31534.0481
September | 64823.244 | 114.9379 | 336.5593 | 0 | 0.001 | 77475.7356 | 27798.955
October | 62791.0802 | 110.0006 | 318.0107 | 0 | 0.001 | 73204.032 | 26799.9207
November | 66253.0262 | 114.4622 | 325.9334 | 0 | 0.001 | 75025.5516 | 28124.2374
December | 80509.8134 | 137.8617 | 388.6886 | 0 | 0.0012 | 89469.1939 | 34058.4798
Annual Sum or Average | 845402.2677 | 1473.5785 | 4237.01 | 0 | 0.0129 | 975322.3271 | 360115.6125
Minimum of Months | 60665.6203 | 105.1732 | 300.6284 | 0 | 0.0009 | 69201.1976 | 25787.2049
Maximum of Months | 85159.3702 | 145.4775 | 409.0625 | 0 | 0.0013 | 94158.384 | 35992.3357
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 218487000000 | 149437.898 | 07-JAN-08:15 | 26328.66 | 57998.833 | 7526.547 | 57495.021 | 4.06 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 183555000000 | 130996.869 | 11-FEB-08:15 | 26328.66 | 57998.833 | 7100.543 | 39428.092 | 55.963 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 184868000000 | 114489.022 | 04-MAR-08:15 | 26328.66 | 57998.833 | 6847.605 | 21435.068 | 1794.078 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 160576000000 | 105235.428 | 02-APR-07:00 | 26328.66 | 57998.833 | 6903.479 | 8092.159 | 5827.519 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 173575000000 | 116715.878 | 28-MAY-07:00 | 26328.66 | 57998.833 | 8131.524 | 0 | 24172.083 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 191756000000 | 125491.412 | 17-JUN-07:00 | 26328.66 | 57998.833 | 8669.418 | 0 | 32409.723 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 213613000000 | 137946.448 | 09-JUL-07:00 | 26328.66 | 57998.833 | 9284.192 | 0 | 44249.985 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 205392000000 | 139764.022 | 04-AUG-19:15 | 36517.967 | 38824.77 | 9997.201 | 0 | 51858.306 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 179777000000 | 120629.565 | 16-SEP-07:00 | 26328.66 | 57998.833 | 8398.727 | 0 | 27818.567 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 169864000000 | 109901.845 | 21-OCT-07:15 | 26328.66 | 57998.833 | 6937.215 | 14552.231 | 4000.128 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 174091000000 | 110756.796 | 18-NOV-08:15 | 26328.66 | 57998.833 | 6933.134 | 15630.422 | 3780.968 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 207607000000 | 147658.552 | 31-DEC-08:15 | 26328.66 | 57998.833 | 7501.02 | 55715.702 | 29.559 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2263160000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 160576000000 | 105235.428 |  | 26328.66 | 38824.77 | 6847.605 | 0 | 4.06 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 218487000000 | 149437.898 |  | 36517.967 | 57998.833 | 9997.201 | 57495.021 | 51858.306 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 61552.76 | 12117.12 | 0 | 73669.88
Cost per Total Building Area ($/m2) | 15.34 | 3.02 | 0 | 18.36
Cost per Net Conditioned Building Area ($/m2) | 15.57 | 3.06 | 0 | 18.63

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3364.84 | 838.36 | 851.13
Net Site Energy | 3364.84 | 838.36 | 851.13
Total Source Energy | 8423.54 | 2098.76 | 2130.72
Net Source Energy | 8423.54 | 2098.76 | 2130.72
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 161.01 | 400.13 | 0 | 0 | 0 | 0
Cooling | 251.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.94 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 239.23 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 641.74 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2133.49 | 1231.35 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.388 | 0.283
North Total or Average |  |  | 72.38 | 3.69 | 0.388 | 0.281
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.387 | 0.285
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1534.3 | 1225.38 | 308.92 | 0.8 | 3.7
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1557.89 | 1244.22 | 313.67 | 0.8 | 3.7
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1602.41 | 1279.77 | 322.64 | 0.8 | 3.7
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1444.13 | 1153.37 | 290.77 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1613.5 | 1288.63 | 324.87 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2319.87 | 1852.78 | 467.09 | 0.8 | 3.62
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7904.92 | 6313.3 | 1591.61 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6368.57 | 5086.29 | 1282.28 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7666.34 | 6122.77 | 1543.58 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2119.73 | 1692.93 | 426.8 | 0.8 | 3.68
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1985.26 | 1585.54 | 399.72 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8077.62 | 6451.23 | 1626.39 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2606.18 | 2081.44 | 524.74 | 0.8 | 3.54
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7234.46 | 5777.84 | 1456.62 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1999.82 | 1597.17 | 402.65 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2303.83 | 1839.96 | 463.86 | 0.8 | 3.63
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7933.7 | 6336.29 | 1597.41 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6537.08 | 5220.87 | 1316.21 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7920.99 | 6326.14 | 1594.85 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2188.76 | 1748.06 | 440.69 | 0.8 | 3.66
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2051.05 | 1638.08 | 412.97 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7659.78 | 6117.53 | 1542.26 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2041.21 | 1630.22 | 410.99 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7511.83 | 5999.37 | 1512.47 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2057.52 | 1643.25 | 414.27 | 0.8 | 3.69
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2748.45 | 2195.06 | 553.39 | 0.8 | 3.5
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10052.19 | 8028.23 | 2023.96 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8269.68 | 6604.63 | 1665.06 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10059.54 | 8034.1 | 2025.44 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2759.29 | 2203.72 | 555.57 | 0.8 | 3.5
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2575.37 | 2056.83 | 518.54 | 0.8 | 3.55
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9665.46 | 7719.37 | 1946.09 | 0.8 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2499.13 | 1995.94 | 503.19 | 0.8 | 3.57
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9576.24 | 7648.11 | 1928.12 | 0.8 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2579.46 | 2060.1 | 519.36 | 0.8 | 3.55
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8657.03 | 6913.98 | 1743.05 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4207.99 | 3360.73 | 847.26 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3742.64 | 2989.08 | 753.56 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10657.5 | 8511.67 | 2145.83 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15713.62 | 11635.56 | 4078.06 | 0.74 | 3.84
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1247.18 | 996.07 | 251.11 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10531.86 | 7262.02 | 3269.83 | 0.69 | 3.69
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 837.11 | 668.56 | 168.55 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5945.55 | 4748.45 | 1197.11 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31945.1 | 25513.12 | 6431.98 | 0.8 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2261.76 | 1789.71 | 472.05 | 0.79 | 4.01
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5550.79 | 4433.17 | 1117.62 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 462.22 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 491.96 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 541.21 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1611.94 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 508.22 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1097.4 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1120.42 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1337.41 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1333.8 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1119.73 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1525.07 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4087.68 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3177.17 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4015.03 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1245.79 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1218.1 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3723.64 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 836.47 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3903.27 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1145.73 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1578.92 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4248.18 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3412.99 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4233.42 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1297.15 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1275.5 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4195.8 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1055.2 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4188.81 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1215.63 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2870.86 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 11525.11 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 9310.33 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 11517.93 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 3141.46 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 3124.86 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 11530.37 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 3129.88 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 11491.9 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 3096.97 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 357.23 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 374.07 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 407.34 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1443.28 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 206.94 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 275.01 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 310.58 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 966.09 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 11351.23 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6031.42 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5500.83 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 13389.31 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 31742.27 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1422.06 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 25330.89 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1275.21 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 10240.97 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 79323.75 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 6854.39 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 10262.91 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.74 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.86 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.04 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.08 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.92 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59.91 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.62 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.53 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 62.04 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.21 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 303.97 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 244.89 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 294.8 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.51 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.34 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 310.61 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.22 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 278.19 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.9 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.59 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.08 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 251.37 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 304.59 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.16 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.87 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 294.54 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.49 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 288.85 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.12 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.69 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.54 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.82 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.1 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.03 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.67 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.1 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 368.24 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.19 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.35 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.41 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.54 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.45 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.78 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.04 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.17 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.65 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 606.6 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 294.85 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 262.25 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.64 | 746.77 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.8 | 926.82 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 87.39 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 518.93 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 58.66 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 416.6 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.93 | 2110.48 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 155.31 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 388.94 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 58504.0468 | 95.8222 | 231.4593 | 0 | 0.0009 | 240638.8887 | 24438.4896
February | 50527.2583 | 82.8252 | 200.2683 | 0 | 0.0008 | 208211.2976 | 21113.0606
March | 52705.412 | 86.7032 | 210.5662 | 0 | 0.0008 | 218919.9159 | 22053.3811
April | 47671.0907 | 79.2129 | 194.7372 | 0 | 0.0008 | 202468.7397 | 20024.5206
May | 49160.1339 | 82.4596 | 205.0007 | 0 | 0.0008 | 213145.209 | 20725.7683
June | 50074.562 | 84.8069 | 213.2163 | 0 | 0.0008 | 221692.8589 | 21191.0717
July | 56702.6742 | 96.6948 | 245.0247 | 0 | 0.001 | 254770.3091 | 24061.0136
August | 54681.736 | 93.1613 | 235.8198 | 0 | 0.0009 | 245198.6756 | 23194.9016
September | 49328.4347 | 83.5162 | 209.8933 | 0 | 0.0008 | 218237.5336 | 20872.6712
October | 49288.5329 | 82.5028 | 204.6038 | 0 | 0.0008 | 212731.2722 | 20763.0033
November | 50809.7836 | 83.8994 | 204.6959 | 0 | 0.0008 | 212819.0318 | 21291.0624
December | 58793.6928 | 96.363 | 232.9647 | 0 | 0.0009 | 242204.4333 | 24565.9952
Annual Sum or Average | 628247.358 | 1047.9676 | 2588.2503 | 0 | 0.0102 | 2691040 | 264294.9392
Minimum of Months | 47671.0907 | 79.2129 | 194.7372 | 0 | 0.0008 | 202468.7397 | 20024.5206
Maximum of Months | 58793.6928 | 96.6948 | 245.0247 | 0 | 0.001 | 254770.3091 | 24565.9952
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 190781000000 | 137802.804 | 08-JAN-08:15 | 26328.66 | 57998.833 | 7937.102 | 45253.733 | 199.699 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 165072000000 | 124166.682 | 16-FEB-07:15 | 24311.729 | 51279.599 | 7803.757 | 40639.99 | 46.827 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 173562000000 | 112981.462 | 07-MAR-07:15 | 24311.729 | 51279.599 | 7603.542 | 28523.91 | 1177.902 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 160520000000 | 104703.164 | 25-APR-19:30 | 36517.967 | 38824.77 | 8905.561 | 0 | 17889.088 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 168984000000 | 112196.203 | 23-MAY-19:15 | 36517.967 | 38824.77 | 9392.18 | 0 | 24895.508 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 175761000000 | 115484.866 | 27-JUN-19:30 | 36517.967 | 38824.77 | 9660.141 | 0 | 27916.21 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 201985000000 | 124133.972 | 02-JUL-07:00 | 26328.66 | 57998.833 | 9400.961 | 0 | 30320.741 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 194396000000 | 119214.912 | 29-AUG-19:15 | 36517.967 | 38824.77 | 9892.075 | 0 | 31414.321 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 173021000000 | 117847.743 | 02-SEP-07:00 | 26328.66 | 57998.833 | 9008.346 | 0 | 24427.126 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 168656000000 | 108223.461 | 21-OCT-07:15 | 26328.66 | 57998.833 | 7536.371 | 11877.123 | 4397.696 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 168725000000 | 113447.476 | 18-NOV-08:15 | 26328.66 | 57998.833 | 7445.324 | 19543.301 | 2046.58 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 192023000000 | 130625.288 | 12-DEC-07:15 | 24311.729 | 51279.599 | 7906.958 | 44537.702 | 23.522 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2133490000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 160520000000 | 104703.164 |  | 24311.729 | 38824.77 | 7445.324 | 0 | 23.522 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 201985000000 | 137802.804 |  | 36517.967 | 57998.833 | 9892.075 | 45253.733 | 31414.321 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22077.29 | 8789.6 | 0 | 30866.89
Cost per Total Building Area ($/m2) | 5.5 | 2.19 | 0 | 7.69
Cost per Net Conditioned Building Area ($/m2) | 5.58 | 2.22 | 0 | 7.81

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3960.15 | 986.68 | 1001.71
Net Site Energy | 3960.15 | 986.68 | 1001.71
Total Source Energy | 9877.88 | 2461.11 | 2498.59
Net Source Energy | 9877.88 | 2461.11 | 2498.59
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 376.22 | 713.31 | 0 | 0 | 0 | 0
Cooling | 281.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 228.05 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 689.17 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2368.19 | 1591.96 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.388 | 0.283
North Total or Average |  |  | 72.38 | 3.69 | 0.388 | 0.281
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.387 | 0.285
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1710.81 | 1284 | 426.81 | 0.75 | 3.62
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1734.44 | 1305.03 | 429.41 | 0.75 | 3.63
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1809.18 | 1371.77 | 437.41 | 0.76 | 3.64
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1556.54 | 1196.91 | 359.62 | 0.77 | 3.65
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1616.4 | 1251.27 | 365.13 | 0.77 | 3.66
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2158.86 | 1718.34 | 440.52 | 0.8 | 3.66
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7865.5 | 6064.2 | 1801.31 | 0.77 | 3.03
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6305.2 | 4896.61 | 1408.59 | 0.78 | 3.03
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7692.63 | 5908.96 | 1783.67 | 0.77 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2116.38 | 1651.09 | 465.29 | 0.78 | 3.65
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1877.28 | 1492.66 | 384.61 | 0.8 | 3.69
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7320.39 | 5792.89 | 1527.5 | 0.79 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2308.3 | 1843.53 | 464.76 | 0.8 | 3.62
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6789.73 | 5305.78 | 1483.95 | 0.78 | 3.04
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1864.71 | 1481.21 | 383.5 | 0.79 | 3.69
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2148.13 | 1708.45 | 439.68 | 0.8 | 3.66
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7874.74 | 6072.48 | 1802.26 | 0.77 | 3.03
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6424.06 | 5003.68 | 1420.38 | 0.78 | 3.03
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7867.58 | 6066.04 | 1801.53 | 0.77 | 3.03
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2168.84 | 1698.52 | 470.32 | 0.78 | 3.64
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1930.39 | 1541.64 | 388.74 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7069.38 | 5562.11 | 1507.28 | 0.79 | 3.04
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1858.19 | 1475.19 | 382.99 | 0.79 | 3.69
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6975.06 | 5475.56 | 1499.5 | 0.79 | 3.04
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1916.89 | 1529.3 | 387.59 | 0.8 | 3.69
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2827.67 | 2185.98 | 641.69 | 0.77 | 3.45
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11566.65 | 8603.78 | 2962.87 | 0.74 | 3
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9437.45 | 7055.35 | 2382.1 | 0.75 | 3
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11574.71 | 8610.77 | 2963.94 | 0.74 | 3
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3137.31 | 2371.3 | 766.01 | 0.76 | 3.34
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2991.26 | 2247.55 | 743.71 | 0.75 | 3.37
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11115.5 | 8238.05 | 2877.45 | 0.74 | 3
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2935.61 | 2189.75 | 745.85 | 0.75 | 3.38
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11052.22 | 8183.45 | 2868.77 | 0.74 | 2.99
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2970.04 | 2232.99 | 737.05 | 0.75 | 3.38
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8136.15 | 6497.98 | 1638.17 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4165.55 | 3226.92 | 938.64 | 0.77 | 3.95
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3870.56 | 2974.42 | 896.14 | 0.77 | 3.93
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17190.1 | 11987.29 | 5202.81 | 0.7 | 3.71
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18277.29 | 12356.97 | 5920.32 | 0.68 | 3.65
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1198.07 | 956.84 | 241.22 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 987.02 | 737.46 | 249.56 | 0.75 | 3.86
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6857.25 | 4860.43 | 1996.83 | 0.71 | 3.75
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29834.04 | 22989.63 | 6844.41 | 0.77 | 3.69
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3056.66 | 2066.56 | 990.1 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7783.1 | 5288.26 | 2494.84 | 0.68 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 797.59 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 781.07 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 830.63 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2314.16 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 789.28 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1444.52 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1468.95 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1693.97 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1684.8 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1465.9 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2010.38 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5467.18 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4269.52 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5383.06 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1596.93 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1566 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 5092.88 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1113.41 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5262.09 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1500.09 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2070.79 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5645.68 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4521.16 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5626.79 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1653.43 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1629.88 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5580.99 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1428.84 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5568.79 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1575.43 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3791.76 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 15601.25 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 12582.86 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 15590.8 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 4169.79 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 4151.5 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 15598.24 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 4232.3 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 15553.53 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 4119.85 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 682.74 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 649.53 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 684.54 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2140.55 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 407.58 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 452.84 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 491.15 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1376.86 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 13040.47 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6977.13 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6517.7 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 18517.6 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 39787.89 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1614.47 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 33262.32 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1593.64 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 11837.87 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 45023.77 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 8815.4 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 12605.56 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.55 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.49 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.65 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.39 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.52 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 57.17 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.31 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.92 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.02 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.01 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.4 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 279.69 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 227.91 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 271.25 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.29 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.49 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.89 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.76 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 248.86 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.86 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.85 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 280.14 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 233.75 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 279.79 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 79.88 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.22 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 263.07 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.53 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 258.27 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.54 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.17 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.47 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 312.5 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 378.83 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.59 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.23 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 360.55 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.69 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357.69 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.66 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.18 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.07 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.19 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.84 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.3 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.45 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.57 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.4 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 570.1 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.24 | 272.84 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.21 | 248.95 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 872.57 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.74 | 853.72 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 83.95 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 59.47 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 363.06 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.66 | 1896.38 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 142.78 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 368.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 70146.6468 | 115.783 | 170.0038 | 0 | 0.0013 | 111706.1049 | 29258.9483
February | 56604.9288 | 93.4433 | 137.224 | 0 | 0.001 | 90167.2473 | 23611.6996
March | 50916.1648 | 84.7447 | 125.6875 | 0 | 0.0009 | 82589.9767 | 21304.9168
April | 41835.7844 | 70.8202 | 107.1437 | 0 | 0.0008 | 70410.0149 | 17619.044
May | 43662.4029 | 75.4906 | 116.9609 | 0 | 0.0009 | 76868.2545 | 18539.1834
June | 45421.909 | 79.5428 | 124.963 | 0 | 0.0009 | 82131.4981 | 19382.82
July | 49003.1833 | 86.237 | 136.1918 | 0 | 0.001 | 89513.3212 | 20951.4506
August | 48128.8333 | 84.7299 | 133.865 | 0 | 0.001 | 87984.1163 | 20580.6493
September | 41287.9222 | 71.9752 | 112.5211 | 0 | 0.0008 | 73952.774 | 17587.3592
October | 42837.6443 | 73.1124 | 111.6508 | 0 | 0.0008 | 73374.4671 | 18097.9635
November | 48764.0892 | 81.6681 | 122.0206 | 0 | 0.0009 | 80182.6965 | 20452.727
December | 63438.2924 | 105.0275 | 154.7787 | 0 | 0.0012 | 101703.4518 | 26491.1415
Annual Sum or Average | 602047.8015 | 1022.5748 | 1553.0108 | 0 | 0.0115 | 1020580 | 253877.9031
Minimum of Months | 41287.9222 | 70.8202 | 107.1437 | 0 | 0.0008 | 70410.0149 | 17587.3592
Maximum of Months | 70146.6468 | 115.783 | 170.0038 | 0 | 0.0013 | 111706.1049 | 29258.9483
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 259206000000 | 163011.893 | 06-JAN-07:15 | 24311.729 | 51279.599 | 7933.38 | 76921.405 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 209226000000 | 159795.076 | 04-FEB-08:15 | 26328.66 | 57998.833 | 7714.435 | 67668.37 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 191644000000 | 121183.694 | 05-MAR-08:15 | 26328.66 | 57998.833 | 6916.952 | 29766.795 | 87.676 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 163381000000 | 109097.22 | 09-APR-07:15 | 26328.66 | 57998.833 | 7051.457 | 13538.817 | 4094.676 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 178367000000 | 130418.974 | 27-MAY-19:45 | 36349.301 | 38772.136 | 9801.754 | 0 | 42930.005 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 190580000000 | 131981.226 | 25-JUN-07:00 | 26328.66 | 57998.833 | 9202.166 | 0 | 38366.789 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 207709000000 | 136931.725 | 16-JUL-07:00 | 26328.66 | 57998.833 | 9478.937 | 0 | 43040.517 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 204161000000 | 135801.834 | 27-AUG-07:00 | 26328.66 | 57998.833 | 9381.74 | 0 | 42007.824 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 171602000000 | 117271.063 | 03-SEP-07:00 | 26328.66 | 57998.833 | 8386.272 | 0 | 24472.52 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 170260000000 | 110072.37 | 08-OCT-07:00 | 26328.66 | 57998.833 | 7904.194 | 0 | 17755.905 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 186058000000 | 120255.429 | 30-NOV-07:15 | 24311.729 | 51279.599 | 7028.358 | 35015.227 | 54.737 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 235995000000 | 170593.272 | 31-DEC-08:15 | 26328.66 | 57998.833 | 7947.969 | 78233.032 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2368190000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 163381000000 | 109097.22 |  | 24311.729 | 38772.136 | 6916.952 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 259206000000 | 170593.272 |  | 36349.301 | 57998.833 | 9801.754 | 78233.032 | 43040.517 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 35888.64 | 12649.15 | 0 | 48537.78
Cost per Total Building Area ($/m2) | 8.94 | 3.15 | 0 | 12.09
Cost per Net Conditioned Building Area ($/m2) | 9.08 | 3.2 | 0 | 12.28

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3644.66 | 908.08 | 921.91
Net Site Energy | 3644.66 | 908.08 | 921.91
Total Source Energy | 9165.69 | 2283.67 | 2318.44
Net Source Energy | 9165.69 | 2283.67 | 2318.44
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 276.95 | 582.66 | 0 | 0 | 0 | 0
Cooling | 183.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 232.24 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 697.3 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2175.22 | 1469.44 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.351 | 0.376 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.389 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.388 | 0.283
North Total or Average |  |  | 72.38 | 3.69 | 0.388 | 0.281
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.387 | 0.285
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1526.32 | 1219 | 307.32 | 0.8 | 3.7
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1554.68 | 1241.65 | 313.03 | 0.8 | 3.7
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1594.3 | 1273.3 | 321 | 0.8 | 3.7
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1369.2 | 1093.52 | 275.68 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1523.91 | 1217.08 | 306.83 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2260.66 | 1805.49 | 455.17 | 0.8 | 3.64
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7909.09 | 6316.64 | 1592.45 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6456.77 | 5156.74 | 1300.04 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7674.88 | 6129.58 | 1545.3 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2120.52 | 1693.56 | 426.95 | 0.8 | 3.68
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1909.53 | 1525.06 | 384.47 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7697.31 | 6147.49 | 1549.81 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2493.96 | 1991.81 | 502.15 | 0.8 | 3.57
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6897.25 | 5508.53 | 1388.73 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1913.57 | 1528.28 | 385.29 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2247.48 | 1794.96 | 452.52 | 0.8 | 3.64
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7929.07 | 6332.6 | 1596.48 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6621.43 | 5288.24 | 1333.19 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7918.6 | 6324.23 | 1594.37 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2188.34 | 1747.73 | 440.61 | 0.8 | 3.66
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1979.36 | 1580.82 | 398.53 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7316.78 | 5843.58 | 1473.19 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1951.64 | 1558.69 | 392.95 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7176.33 | 5731.41 | 1444.92 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1976.54 | 1578.57 | 397.97 | 0.8 | 3.7
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2668.37 | 2131.11 | 537.26 | 0.8 | 3.52
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9997.1 | 7984.23 | 2012.86 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8278.12 | 6611.37 | 1666.76 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10005.41 | 7990.87 | 2014.54 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2744.65 | 2192.03 | 552.62 | 0.8 | 3.5
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2651.93 | 2117.98 | 533.95 | 0.8 | 3.53
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9771.49 | 7804.05 | 1967.44 | 0.8 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2710.74 | 2164.95 | 545.79 | 0.8 | 3.51
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9734.97 | 7774.88 | 1960.08 | 0.8 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2624.32 | 2095.93 | 528.39 | 0.8 | 3.54
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8296.23 | 6625.83 | 1670.4 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4051.98 | 3236.14 | 815.85 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3631.24 | 2900.11 | 731.13 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13227.43 | 10564.16 | 2663.27 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14383.36 | 10931.5 | 3451.86 | 0.76 | 3.9
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1214.93 | 970.31 | 244.62 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8785.53 | 6416.09 | 2369.44 | 0.73 | 3.81
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 825.04 | 658.92 | 166.12 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5622.93 | 4490.78 | 1132.15 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30187.51 | 24109.42 | 6078.1 | 0.8 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2123.55 | 1695.98 | 427.57 | 0.8 | 4.04
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5231.63 | 4178.27 | 1053.36 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 766.92 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 752.08 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 802.55 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2227.5 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 756.6 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1385.69 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1410.22 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1637.35 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1628.29 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1407.68 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1928.51 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5178.93 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4046.43 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5093.01 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1526.09 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1494.97 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4800.9 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1014.58 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4970.58 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1428.31 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1989.44 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5358.44 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4298.08 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5338.81 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1582.95 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1558.31 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5287.33 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1353.87 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5275.06 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1502.96 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3661.27 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 14867.91 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 11999.28 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 14856.9 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 3989.7 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 3969.59 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 14856.37 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 4041.47 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 14811.72 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 3935.84 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 653.25 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 618.56 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 655.09 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2051.68 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 405.69 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 445.81 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 484.98 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1352.77 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 11897.57 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6468.34 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 5961.69 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 17523.9 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 36961.81 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1463.06 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 30365.61 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1406.67 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 11230.59 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 43598.91 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 8131.32 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 11367.46 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.74 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.69 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.87 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 7.96 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.7 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.69 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59.78 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.31 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 52.65 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.6 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.93 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 304.13 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 248.28 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 295.12 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.54 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.43 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 295.99 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.9 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 265.22 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.58 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.42 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 304.9 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 254.62 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 304.5 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.15 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.11 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 281.35 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.05 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.95 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.61 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 384.42 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318.32 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 384.74 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.54 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.98 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 375.75 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.24 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 374.34 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.91 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.33 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.21 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.34 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.33 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.45 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.59 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.73 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.83 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 581.32 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.24 | 283.92 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.22 | 254.44 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.8 | 926.85 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.78 | 901.91 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 85.13 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 501.15 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 57.81 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 394 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.82 | 1994.37 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 148.8 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 366.58 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 63283.2956 | 103.0922 | 165.3798 | 0 | 0.0012 | 3922060 | 26315.108
February | 52835.0755 | 86.1203 | 138.252 | 0 | 0.001 | 3278720 | 21975.1482
March | 50145.508 | 82.3361 | 133.3831 | 0 | 0.0009 | 3163350 | 20914.4718
April | 44242.2511 | 73.0752 | 119.243 | 0 | 0.0008 | 2828070 | 18494.1194
May | 43487.1657 | 72.7295 | 120.4679 | 0 | 0.0008 | 2857270 | 18265.6163
June | 44279.0635 | 75.0461 | 126.25 | 0 | 0.0009 | 2994570 | 18694.1424
July | 48474.7547 | 82.8728 | 140.801 | 0 | 0.001 | 3339820 | 20534.6945
August | 47040.1317 | 80.3202 | 136.2726 | 0 | 0.001 | 3232390 | 19917.3062
September | 42994.7453 | 72.8202 | 122.4103 | 0 | 0.0009 | 2903490 | 18147.1655
October | 44579.5888 | 74.3999 | 122.928 | 0 | 0.0009 | 2915600 | 18709.327
November | 48508.0134 | 79.9 | 129.9412 | 0 | 0.0009 | 3081770 | 20255.9347
December | 60257.6498 | 98.4265 | 158.425 | 0 | 0.0011 | 3757170 | 25082.4029
Annual Sum or Average | 590127.2431 | 981.139 | 1613.7539 | 0 | 0.0113 | 38274300 | 247305.4368
Minimum of Months | 42994.7453 | 72.7295 | 119.243 | 0 | 0.0008 | 2828070 | 18147.1655
Maximum of Months | 63283.2956 | 103.0922 | 165.3798 | 0 | 0.0012 | 3922060 | 26315.108
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 222900000000 | 161470.474 | 07-JAN-08:15 | 26328.66 | 57998.833 | 8082.834 | 66494.369 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 186338000000 | 150218.724 | 26-FEB-08:15 | 26328.66 | 57998.833 | 7858.372 | 57948.081 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 179781000000 | 133195.294 | 04-MAR-08:15 | 26328.66 | 57998.833 | 7484.261 | 41251.36 | 47.402 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 160726000000 | 105764.984 | 02-APR-07:15 | 26328.66 | 57998.833 | 7359.803 | 9560.572 | 4432.338 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 162386000000 | 103367.397 | 25-MAY-19:00 | 36517.967 | 38824.77 | 8679.748 | 0 | 16779.134 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 170189000000 | 122326.512 | 25-JUN-19:15 | 36433.634 | 38807.225 | 10199.583 | 0 | 36801.291 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 189810000000 | 121678.153 | 22-JUL-07:00 | 26328.66 | 57998.833 | 9236.857 | 0 | 28029.026 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 183705000000 | 117469.366 | 11-AUG-19:45 | 36517.967 | 38824.77 | 9661.323 | 0 | 29899.527 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 165012000000 | 113626.518 | 02-SEP-19:15 | 36349.301 | 38772.136 | 9409.068 | 0 | 26530.235 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 165700000000 | 111208.507 | 29-OCT-07:15 | 26328.66 | 57998.833 | 7404.425 | 15607.71 | 3784.101 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 175144000000 | 116904.157 | 04-NOV-07:15 | 26328.66 | 57998.833 | 7321.75 | 20228.511 | 2460.625 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 213529000000 | 156837.308 | 11-DEC-07:15 | 24311.729 | 51279.599 | 8163.875 | 70516.325 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2175220000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 160726000000 | 103367.397 |  | 24311.729 | 38772.136 | 7321.75 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 222900000000 | 161470.474 |  | 36517.967 | 57998.833 | 10199.583 | 70516.325 | 36801.291 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43347.06 | 12632.34 | 0 | 55979.4
Cost per Total Building Area ($/m2) | 10.8 | 3.15 | 0 | 13.95
Cost per Net Conditioned Building Area ($/m2) | 10.96 | 3.2 | 0 | 14.16

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4206.14 | 1047.98 | 1063.93
Net Site Energy | 4206.14 | 1047.98 | 1063.93
Total Source Energy | 10127.62 | 2523.33 | 2561.76
Net Source Energy | 10127.62 | 2523.33 | 2561.76
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 475.41 | 893.53 | 0 | 0 | 0 | 0
Cooling | 179.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 223.09 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 762.99 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2360.14 | 1846.01 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.358 | 0.384 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.363 | 0.384 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 3.241 | 0.487 | 0.409 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.487 | 0.409 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 3.241 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 3.241 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 3.808 | 0.49 | 0.378 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.487 | 0.409 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 3.241 | 0.487 | 0.409 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 3.241 | 0.487 | 0.409 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.65 | 0.489 | 0.387
North Total or Average |  |  | 72.38 | 3.69 | 0.489 | 0.384
Non-North Total or Average |  |  | 111.83 | 3.62 | 0.489 | 0.388
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1473.54 | 1164.09 | 309.46 | 0.79 | 3.68
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1497.43 | 1186.13 | 311.31 | 0.79 | 3.69
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1524.46 | 1211.33 | 313.13 | 0.79 | 3.69
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1257.86 | 1003.64 | 254.22 | 0.8 | 3.69
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1393.49 | 1112.92 | 280.57 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2128.86 | 1700.23 | 428.64 | 0.8 | 3.67
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7610.4 | 6078.08 | 1532.31 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6261.43 | 5000.72 | 1260.71 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7372 | 5887.69 | 1484.31 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2042.33 | 1631.12 | 411.21 | 0.8 | 3.7
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1802.68 | 1439.72 | 362.96 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7187.4 | 5740.25 | 1447.14 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2312.83 | 1847.15 | 465.68 | 0.8 | 3.62
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6455.02 | 5155.33 | 1299.68 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1796.45 | 1434.75 | 361.71 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2118.06 | 1691.6 | 426.46 | 0.8 | 3.68
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7636.89 | 6099.24 | 1537.65 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6438.16 | 5141.87 | 1296.29 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7625.63 | 6090.25 | 1535.38 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2115.81 | 1689.8 | 426.01 | 0.8 | 3.68
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1879.65 | 1501.19 | 378.46 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6870.1 | 5486.84 | 1383.26 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1832.76 | 1463.74 | 369.02 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6742.18 | 5384.67 | 1357.5 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1867.13 | 1491.19 | 375.94 | 0.8 | 3.7
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2501.81 | 1998.08 | 503.73 | 0.8 | 3.57
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10307.6 | 8059.17 | 2248.43 | 0.78 | 3.04
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8361.81 | 6573.45 | 1788.36 | 0.79 | 3.04
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10296.31 | 8051.09 | 2245.21 | 0.78 | 3.04
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2719.33 | 2151.34 | 567.99 | 0.79 | 3.5
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2743.87 | 2157.13 | 586.74 | 0.79 | 3.49
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10418.6 | 8106.92 | 2311.68 | 0.78 | 3.03
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2850.11 | 2230.26 | 619.85 | 0.78 | 3.45
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10403.95 | 8087.78 | 2316.17 | 0.78 | 3.03
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2718.82 | 2137.1 | 581.72 | 0.79 | 3.49
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7601.9 | 6071.3 | 1530.6 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3878.57 | 3097.64 | 780.93 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3540.78 | 2827.86 | 712.92 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17051.38 | 12299.86 | 4751.51 | 0.72 | 3.78
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18587.52 | 12566.71 | 6020.81 | 0.68 | 3.65
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1103.15 | 881.03 | 222.11 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10659.87 | 7206.96 | 3452.91 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 794.76 | 616.4 | 178.36 | 0.78 | 3.96
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5884.72 | 4426.67 | 1458.05 | 0.75 | 3.88
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27792.52 | 22118.42 | 5674.1 | 0.8 | 3.76
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2912.98 | 1969.42 | 943.56 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5800.96 | 4251.23 | 1549.73 | 0.73 | 3.82
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 890.43 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 855.41 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 905.71 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2484.66 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 858.51 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1525.19 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1550.16 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1778.56 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1768.72 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1547.45 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2118.64 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5748.19 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4498.75 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5659.14 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1669.32 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1639.58 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 5375.43 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1139.66 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5543.26 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1575.3 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2181.43 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5933.32 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4756.67 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5912.77 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1727.85 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1705.38 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5870.44 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1508.8 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5856.44 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1652.28 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 4007.86 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 16476.84 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 13294.02 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 16465.14 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 4392.96 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 4375.52 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 16476.51 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 4475.11 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 16429.78 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 4341.9 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 771.93 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 718.64 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 756.05 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2309.34 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 473.29 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 504.86 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 544.16 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1490.18 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12192.37 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 6919.2 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6473.56 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 19575.22 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 40688.55 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1455.45 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 34046.51 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1451.32 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 11841.2 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 44606.19 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 8883.88 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 12030.86 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.9 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.79 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.95 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.1 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.8 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.33 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.56 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 57.97 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 48.27 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 53.58 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.86 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 292.64 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 240.77 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 283.48 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.53 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.32 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 276.38 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.94 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 248.22 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.08 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.45 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 293.66 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 247.57 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 293.23 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.36 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.28 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 264.18 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.48 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 259.26 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.8 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.2 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.26 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 310.58 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 377.93 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.43 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.93 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.25 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.79 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 376.91 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.96 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.52 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.34 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.47 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.53 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.54 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.65 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.78 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.86 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 532.67 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.23 | 271.77 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.21 | 248.1 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.81 | 943.54 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.75 | 868.21 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 77.3 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 52.19 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 360.27 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.67 | 1898 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 136.06 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 333.72 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 71316.0475 | 117.5355 | 172.2591 | 0 | 0.0013 | 113187.2498 | 29729.7292
February | 61239.7636 | 100.9323 | 147.932 | 0 | 0.0011 | 97202.484 | 25529.5346
March | 57135.1312 | 94.3424 | 138.5869 | 0 | 0.001 | 91062.9039 | 23835.1411
April | 45349.7087 | 75.6412 | 112.4717 | 0 | 0.0008 | 73906.5269 | 18991.1524
May | 42329.3852 | 71.7116 | 108.5894 | 0 | 0.0008 | 71360.3131 | 17832.2531
June | 41315.4838 | 71.3004 | 110.2425 | 0 | 0.0008 | 72452.3283 | 17530.0073
July | 45729.4901 | 79.6852 | 124.519 | 0 | 0.0009 | 81838.1015 | 19476.1992
August | 44093.1113 | 76.5829 | 119.2465 | 0 | 0.0009 | 78371.8341 | 18755.2902
September | 40567.1442 | 69.612 | 106.9533 | 0 | 0.0008 | 70288.9733 | 17174.5494
October | 44441.7374 | 75.1056 | 113.4072 | 0 | 0.0008 | 74525.5986 | 18704.4866
November | 52617.3328 | 87.6459 | 130.1141 | 0 | 0.001 | 85498.9945 | 22023.4077
December | 67384.2201 | 111.2752 | 163.4776 | 0 | 0.0012 | 107418.1613 | 28111.6634
Annual Sum or Average | 613518.556 | 1031.3702 | 1547.7993 | 0 | 0.0115 | 1017110 | 257693.4142
Minimum of Months | 40567.1442 | 69.612 | 106.9533 | 0 | 0.0008 | 70288.9733 | 17174.5494
Maximum of Months | 71316.0475 | 117.5355 | 172.2591 | 0 | 0.0013 | 113187.2498 | 29729.7292
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 262642000000 | 168254.319 | 09-JAN-07:15 | 24311.729 | 51279.599 | 7968.74 | 82128.472 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 225551000000 | 168542.445 | 02-FEB-07:15 | 24311.729 | 51279.599 | 7979.669 | 82405.669 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 211305000000 | 148316.719 | 09-MAR-07:15 | 24311.729 | 51279.599 | 7592.69 | 65047.922 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 171495000000 | 117887.929 | 03-APR-06:15 | 24311.729 | 51279.599 | 7118.298 | 33970.052 | 1123.472 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 165586000000 | 107036.537 | 28-MAY-07:00 | 26328.66 | 57998.833 | 7739.844 | 0 | 14884.422 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 168120000000 | 119320.494 | 14-JUN-19:00 | 36517.967 | 38824.77 | 9371.707 | 0 | 32040.272 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 189899000000 | 132159.095 | 08-JUL-07:00 | 26328.66 | 57998.833 | 9449.408 | 0 | 38297.416 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 181856000000 | 126864.682 | 13-AUG-19:30 | 36433.634 | 38807.225 | 9906.913 | 0 | 39151.132 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 163100000000 | 110202.511 | 08-SEP-19:15 | 36517.967 | 38824.77 | 8749.602 | 0 | 23544.394 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 172931000000 | 111887.081 | 29-OCT-07:15 | 26328.66 | 57998.833 | 7050.32 | 16938.011 | 3486.479 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 198394000000 | 148646.407 | 25-NOV-08:15 | 26328.66 | 57998.833 | 7415.458 | 56818.678 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 249256000000 | 171289.895 | 31-DEC-08:15 | 26328.66 | 57998.833 | 7893.333 | 78984.29 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2360140000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 163100000000 | 107036.537 |  | 24311.729 | 38807.225 | 7050.32 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 262642000000 | 171289.895 |  | 36517.967 | 57998.833 | 9906.913 | 82405.669 | 39151.132 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 35972.15 | 14663.9 | 0 | 50636.04
Cost per Total Building Area ($/m2) | 8.96 | 3.65 | 0 | 12.62
Cost per Net Conditioned Building Area ($/m2) | 9.1 | 3.71 | 0 | 12.81

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5125.38 | 1277.01 | 1296.45
Net Site Energy | 5125.38 | 1277.01 | 1296.45
Total Source Energy | 12247.81 | 3051.59 | 3098.06
Net Source Energy | 12247.81 | 3051.59 | 3098.06
Area [m2]
Total Building Area | 4013.59
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 60.2
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 811.42 | 1401.77 | 0 | 0 | 0 | 0
Cooling | 151.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 628.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 38.68 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 236.81 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 852.32 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2681.81 | 2443.57 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 5.38 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 5.38 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 12.9 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 9.7 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 11.84 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 11.84 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 6.46 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 8.6 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 11.84 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 11.84 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 11.84 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 11.84 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 11.84 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 6.46 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 16.16 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 14 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 6.46 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 6.46 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.6 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 8.6 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 9.7 | 32.61 | 10.76
Total | 4013.59 |  | 11621.74 |  | 1694.58 | 184.21 | 10.415 | 16.11 | 24.162
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 10.5736 | 15.87 | 16.4078
Unconditioned Total | 60.2 |  | 174.32 |  | 21.18 | 0 | 0 |  | 533.3765
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 8.36 | 0 | 90 | N
R_CORRIDORFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 125.42 | 90 | 0
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.02 | 0 | 90 | N
R_ELEVATORCOREFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 15.05 | 90 | 0
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 270 | 90 | W
R_FRONTSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 20.07 | 90 | 0
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 4.18 | 0 | 90 | N
R_FRONTSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 12.54 | 90 | 0
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 180 | 90 | S
R_GUESTROOM401_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 32.61 | 90 | 0
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 180 | 90 | S
R_GUESTROOM402_405_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 130.45 | 90 | 0
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 35.12 | 180 | 90 | S
R_GUESTROOM406_408_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 105.36 | 90 | 0
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 180 | 90 | S
R_GUESTROOM409_412_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 130.45 | 90 | 0
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 180 | 90 | S
R_GUESTROOM413_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 32.61 | 90 | 0
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
R_GUESTROOM414_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 32.61 | 90 | 0
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 0 | 90 | N
R_GUESTROOM415_418_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 130.44 | 90 | 0
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
R_GUESTROOM419_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 32.61 | 90 | 0
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 43.48 | 0 | 90 | N
R_GUESTROOM420_423_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 130.44 | 90 | 0
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 10.87 | 0 | 90 | N
R_GUESTROOM424_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 32.61 | 90 | 0
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 0 | 90 | N
R_REARSTAIRSFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 20.07 | 90 | 0
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 6.69 | 180 | 90 | S
R_REARSTORAGEFLR4_1_0_0 | ROOF-IEAD-RES | 0.3 | 0.269 | 0.283 | 20.07 | 90 | 0
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.312 | 0.328 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 4.44 | 4.44 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.69 | 2.69 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.31 | 1.31 | 2.615 | 0.702 | 0.633 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 2.615 | 0.702 | 0.633 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 2.97 | 2.97 | 2.615 | 0.702 | 0.633 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-90.1-2004-NONRES-FIXED | 2.96 | 2.96 | 2.615 | 0.702 | 0.633 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 3.41 | 3.41 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.65 | 1.65 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-90.1-2004-RES-OPER | 1.64 | 1.64 | 2.672 | 0.702 | 0.633 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 2.615 | 0.702 | 0.633 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-90.1-2004-NONRES-FIXED | 1.64 | 1.64 | 2.615 | 0.702 | 0.633 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-90.1-2004-NONRES-FIXED | 1.65 | 1.65 | 2.615 | 0.702 | 0.633 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 2.66 | 0.702 | 0.633
North Total or Average |  |  | 72.38 | 2.66 | 0.702 | 0.633
Non-North Total or Average |  |  | 111.83 | 2.65 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1616.1 | 1290.71 | 325.39 | 0.8 | 3.7
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1669.61 | 1333.45 | 336.17 | 0.8 | 3.7
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1652.45 | 1319.73 | 332.71 | 0.8 | 3.7
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1137.16 | 908.2 | 228.96 | 0.8 | 3.7
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1310.65 | 1046.76 | 263.89 | 0.8 | 3.7
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2378.36 | 1899.49 | 478.87 | 0.8 | 3.6
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9129.3 | 7291.16 | 1838.14 | 0.8 | 3.05
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7757.64 | 6195.68 | 1561.96 | 0.8 | 3.05
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8797.85 | 7026.45 | 1771.4 | 0.8 | 3.05
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2383.01 | 1903.21 | 479.81 | 0.8 | 3.6
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1826.51 | 1458.75 | 367.76 | 0.8 | 3.7
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7263.23 | 5800.81 | 1462.41 | 0.8 | 3.05
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2341.95 | 1870.41 | 471.54 | 0.8 | 3.61
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6531.39 | 5216.33 | 1315.06 | 0.8 | 3.05
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1784.14 | 1424.91 | 359.23 | 0.8 | 3.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2357.24 | 1882.62 | 474.62 | 0.8 | 3.61
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9154.55 | 7311.33 | 1843.22 | 0.8 | 3.05
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8023.58 | 6408.08 | 1615.51 | 0.8 | 3.05
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9135.28 | 7295.94 | 1839.34 | 0.8 | 3.05
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2476.23 | 1977.65 | 498.58 | 0.8 | 3.58
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1910.51 | 1525.84 | 384.67 | 0.8 | 3.7
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6972.41 | 5568.55 | 1403.86 | 0.8 | 3.05
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1843.3 | 1472.16 | 371.14 | 0.8 | 3.7
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6843.84 | 5465.87 | 1377.97 | 0.8 | 3.05
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1859.19 | 1484.85 | 374.34 | 0.8 | 3.7
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2778.05 | 2218.7 | 559.34 | 0.8 | 3.49
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11942.65 | 9538.06 | 2404.59 | 0.8 | 3.05
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9757.3 | 7792.72 | 1964.58 | 0.8 | 3.05
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11932.76 | 9530.16 | 2402.6 | 0.8 | 3.05
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3189.31 | 2547.16 | 642.15 | 0.8 | 3.38
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3176.18 | 2536.67 | 639.51 | 0.8 | 3.38
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11943.72 | 9538.92 | 2404.81 | 0.8 | 3.05
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3319.48 | 2651.12 | 668.36 | 0.8 | 3.35
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11906.92 | 9509.52 | 2397.4 | 0.8 | 3.05
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3149.39 | 2515.28 | 634.11 | 0.8 | 3.39
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6997.23 | 5588.38 | 1408.86 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4050.83 | 3235.22 | 815.61 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3707.63 | 2961.11 | 746.51 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17096.5 | 13654.21 | 3442.29 | 0.8 | 4.01
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14845.33 | 11856.3 | 2989.03 | 0.8 | 4.01
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1102.7 | 880.68 | 222.02 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7327.42 | 5852.08 | 1475.34 | 0.8 | 4.04
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 728.32 | 581.68 | 146.64 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4956.73 | 3958.72 | 998.01 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26287.27 | 20994.47 | 5292.8 | 0.8 | 3.77
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1875.17 | 1497.61 | 377.56 | 0.8 | 4.04
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4375.64 | 3494.63 | 881.01 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1339.37 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1202.78 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1250.31 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3354.09 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1197.97 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1905.41 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1929.68 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2166.72 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2164.77 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1937.1 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2576.9 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 7000.82 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 5431.93 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 6904.85 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1987.12 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1960.24 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 6650.23 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1466.35 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 6811.37 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1905.41 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2632.81 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 7152.13 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5656.17 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 7129.04 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2038.73 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 2016.8 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 7091.49 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1845.13 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 7076.16 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1970.34 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 4939.24 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 20910.23 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 16792.95 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 20896.52 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 5510.03 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 5491.82 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 20911.72 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 5690.58 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 20860.67 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 5454.66 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1203.45 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1051.13 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1087.59 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3171.93 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 736.62 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 699.67 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 737.13 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1954 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12406.04 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7905.57 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7436.61 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 25742.95 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 52302.37 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1506.81 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 42463.84 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1611.55 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 13425.64 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 46731.78 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 10877.87 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 13538.74 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.22 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.79 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.94 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.56 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.77 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 62.14 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.2 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 63.54 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 43.73 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 50.4 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.46 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 351.05 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 298.31 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 338.31 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.63 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.24 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 279.29 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.06 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 251.15 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 68.61 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.64 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 352.02 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 308.53 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 351.28 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.22 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.47 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 268.11 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.88 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.41 | 263.17 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.49 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.83 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 459.23 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 375.2 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 458.85 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 122.64 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 122.13 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 459.28 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 127.64 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 457.86 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 121.1 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.79 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.31 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.43 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 9.99 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.32 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.2 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.32 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.15 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 490.3 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.24 | 283.84 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.22 | 259.79 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.03 | 1176.56 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.9 | 1021.64 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 77.27 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 513.43 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 51.03 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 347.32 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.59 | 1809.06 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.11 | 131.39 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.26 | 306.6 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 85178.3512 | 100.345 | 481.9191 | 0 | 0.0017 | 96705.5737 | 33023.2703
February | 71447.3685 | 84.0083 | 400.8692 | 0 | 0.0014 | 80440.8796 | 27675.091
March | 61228.5447 | 71.9731 | 343.119 | 0 | 0.0012 | 68852.2959 | 23713.7801
April | 45721.8381 | 54.0142 | 261.8489 | 0 | 0.0009 | 52545.1915 | 17749.4388
May | 38854.9375 | 46.4842 | 234.7044 | 0 | 0.0008 | 47100.2909 | 15173.2814
June | 38478.2694 | 46.4576 | 241.2995 | 0 | 0.0008 | 48425.3151 | 15091.4352
July | 40486.8046 | 49.058 | 257.5636 | 0 | 0.0009 | 51689.8936 | 15906.1799
August | 38726.539 | 46.7427 | 242.5502 | 0 | 0.0008 | 48676.2646 | 15186.5559
September | 38481.0068 | 45.982 | 231.2981 | 0 | 0.0008 | 46416.5271 | 15018.8166
October | 49670.1914 | 58.7554 | 286.0657 | 0 | 0.001 | 57405.0606 | 19294.0112
November | 66238.1515 | 77.9367 | 372.7599 | 0 | 0.0013 | 74800.4925 | 25665.5276
December | 77896.6409 | 91.6719 | 438.7383 | 0 | 0.0015 | 88040.2211 | 30185.6003
Annual Sum or Average | 652408.6437 | 773.4292 | 3792.7359 | 0 | 0.0131 | 761098.0063 | 253682.9881
Minimum of Months | 38478.2694 | 45.982 | 231.2981 | 0 | 0.0008 | 46416.5271 | 15018.8166
Maximum of Months | 85178.3512 | 100.345 | 481.9191 | 0 | 0.0017 | 96705.5737 | 33023.2703
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 340753000000 | 216852.971 | 13-JAN-09:00 | 23669.466 | 35630.216 | 10004.942 | 144944.433 | 38.136 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 283442000000 | 210705.624 | 04-FEB-08:15 | 26328.66 | 57998.833 | 8858.511 | 114953.842 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 242609000000 | 168333.9 | 25-MAR-07:15 | 26328.66 | 57998.833 | 7981.147 | 75940.482 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 185149000000 | 133613.542 | 09-APR-07:15 | 26328.66 | 57998.833 | 7449.097 | 40671.57 | 1080.604 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 165963000000 | 103587.174 | 29-MAY-19:00 | 36433.634 | 38807.225 | 8898.973 | 0 | 19362.563 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 170632000000 | 113930.863 | 24-JUN-07:00 | 26328.66 | 57998.833 | 8724.638 | 0 | 20793.954 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 182135000000 | 117489.902 | 29-JUL-19:45 | 36349.301 | 38772.136 | 9858.416 | 0 | 32425.271 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 171516000000 | 110440.392 | 15-AUG-19:15 | 36517.967 | 38824.77 | 9315.921 | 0 | 25696.955 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 163554000000 | 111879.177 | 30-SEP-07:00 | 26328.66 | 57998.833 | 7346.529 | 15306.034 | 4814.343 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 202273000000 | 138438.264 | 22-OCT-07:15 | 26328.66 | 57998.833 | 7390.058 | 44059.57 | 95.365 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 263568000000 | 165948.81 | 23-NOV-08:15 | 26328.66 | 57998.833 | 7903.08 | 71152.459 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 310219000000 | 192794.196 | 29-DEC-08:00 | 23669.466 | 40634.202 | 9155.19 | 116769.56 | 0 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2681810000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 163554000000 | 103587.174 |  | 23669.466 | 35630.216 | 7346.529 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 340753000000 | 216852.971 |  | 36517.967 | 57998.833 | 10004.942 | 144944.433 | 32425.271 | 2481 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 68067.76 | 10194.72 | 0 | 78262.48
Cost per Total Building Area ($/m2) | 16.96 | 2.54 | 0 | 19.5
Cost per Net Conditioned Building Area ($/m2) | 17.22 | 2.58 | 0 | 19.8

## Picture
DOE Commercial Building Benchmark - Small Hotel
First Floor
Upper Floors

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.19 | 49.33 | 2572.21
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.38
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | 15.19 | 90.86 | 4737.7
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | 14.91
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720