## BuildingSummary
Building Summary Small Office new construction version 1.1_3.1
|  | Value | Data Source
Program
| Building Name | Benchmark Small Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 511 | 2003 CBECS, ASHRAE Small Office 30% Advanced Energy Design Guide
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.244
| East | 0.198
| North | 0.198
| West | 0.198
| Total | 0.212
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones
| Floor to Ceiling Height (m) | 3.05
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 281.5
| Net Dimensions - Total Area (m2) | 222
| Wall to Skin Ratio | 0.32
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 598.76
| Net Dimensions - Total Area (m2) | 598.76
| Roof to Skin Ratio | 0.68
Window Dimensions (m2)
| South | 16.73
| East | 11.16
| North | 16.73
| West | 11.16
| Total Area (m2) | 55.78
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4in slab w/carpet
| Dimensions - Total Area (m2) | 511
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 0
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 1022.46
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.45 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 17.65

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 10.76 | 8.07 | 0 | 11.3562 | 10 | 0 | 80.5463 | 0 | 0
Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.45 | 20.64 | 18.5806 | 6.1058 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 61.0582 | 0 | 0.62247
Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3 | 11.16 | 18.5806 | 3.6221 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 36.2205 | 0 | 0.65537
Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.45 | 16.73 | 18.5806 | 6.1058 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 61.0582 | 0 | 0.62247
Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3 | 11.16 | 18.5806 | 3.6221 | 10.76 | 8.07 | 0 | 0 | 10 | 0 | 36.2205 | 0 | 0.65537
Attic | No | 1 | 567.98 | 720.19 | 1.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5 | 59.69 |  | 27.5104
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7A | 8A
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 200.6 | 1755.3 | 396.1 | 1969.7 | 2244.9 | 250 | 102.9 | 4464.9 | 111.5 | 561.4 | 3959.5 | 892.2 | 1126.2 | 133.5 | 153.9 | 7.93
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.38314 | 0.38314 | 0.38314 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.1682 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9531 | 2.2026
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value (m2·K / W) | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 5.1546 | 6.4935 | 6.4935 | 6.4935 | 6.4935
Window
| U-Factor (W / m2·K) | 6.49 | 6.49 | 6.49 | 3.18 | 3.18 | 3.18 | 6.49 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 2.58
| SHGC | 0.25 | 0.25 | 0.25 | 0.402 | 0.402 | 0.402 | 0.61 | 0.402 | 0.402 | 0.402 | 0.501 | 0.501 | 0.501 | 0.501 | 0.501 | 0.504
| Visible transmittance | 0.25 | 0.25 | 0.25 | 0.495 | 0.495 | 0.495 | 0.61 | 0.495 | 0.495 | 0.495 | 0.622 | 0.622 | 0.622 | 0.622 | 0.49 | 0.49
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 9.5826 | 9.1947 | 8.9397 | 8.3741 | 6.8396 | 7.9513 | 4.3568 | 7.9616 | 7.8159 | 5.252 | 7.641 | 6.9198 | 7.1234 | 6.1054 | 5.1553 | 4.7789
| PSZ-AC:2_COOLC DXCOIL | 8.1407 | 7.8168 | 9.7806 | 6.9248 | 6.3151 | 7.8782 | 8.6394 | 7.7062 | 6.5848 | 7.3275 | 8.8098 | 8.0914 | 9.3222 | 9.3604 | 9.2799 | 11.3127
| PSZ-AC:3_COOLC DXCOIL | 6.2653 | 6.7744 | 7.5859 | 5.9876 | 5.1165 | 6.9434 | 4.3602 | 5.7705 | 6.1599 | 4.2014 | 6.0021 | 6.0471 | 5.8598 | 5.7726 | 5.6233 | 6.9659
| PSZ-AC:4_COOLC DXCOIL | 8.7015 | 9.6264 | 10.2208 | 7.1992 | 5.4669 | 8.2544 | 3.6706 | 7.0065 | 7.0958 | 4.6758 | 8.3163 | 7.8836 | 8.9165 | 9.0754 | 9.1547 | 11.0448
| PSZ-AC:5_COOLC DXCOIL | 7.0827 | 7.3506 | 8.5235 | 6.5927 | 5.5272 | 7.1865 | 5.5431 | 6.4452 | 6.9008 | 4.8656 | 6.7597 | 7.019 | 6.4102 | 6.4684 | 5.6128 | 6.9659
Heating (kW)
| PSZ-AC:1_HEATC | 4.7771 | 5.8037 | 5.2717 | 5.8507 | 4.237 | 5.1038 | 3.5142 | 6.1775 | 5.0824 | 4.606 | 6.8679 | 5.5343 | 7.2045 | 6.2857 | 6.6679 | 8.0457
| PSZ-AC:2_HEATC | 3.8819 | 4.686 | 5.1989 | 4.5869 | 3.6813 | 4.5817 | 4.9122 | 5.0771 | 4.0792 | 4.8663 | 6.1566 | 5.1693 | 6.8404 | 6.4753 | 7.1266 | 9.2529
| PSZ-AC:3_HEATC | 2.9716 | 3.5387 | 3.7981 | 3.5981 | 2.7527 | 3.5919 | 2.5954 | 3.7514 | 3.1924 | 2.827 | 4.228 | 3.4933 | 4.3674 | 3.9207 | 4.3072 | 5.5936
| PSZ-AC:4_HEATC | 4.1655 | 5.3186 | 5.375 | 4.7235 | 3.3291 | 4.7266 | 2.8427 | 5.033 | 4.2543 | 3.777 | 6.0724 | 5.0982 | 6.7357 | 6.3723 | 7.0134 | 9.143
| PSZ-AC:5_HEATC | 3.3079 | 3.9281 | 4.1734 | 3.7663 | 2.9232 | 3.6855 | 3.0881 | 3.9248 | 3.4463 | 3.0999 | 4.448 | 3.8258 | 4.5889 | 4.1722 | 4.3031 | 5.5936
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 3.9 | 3.95 | 4.06 | 4 | 4.05 | 4.05 | 4.07 | 3.97 | 4.05 | 4.07 | 3.97 | 4.04 | 4 | 4.04 | 4.05 | 4.06
| PSZ-AC:2_COOLC DXCOIL | 3.87 | 3.94 | 4.05 | 3.95 | 4.07 | 4.07 | 4.06 | 3.88 | 4.06 | 4.05 | 3.89 | 4.06 | 3.94 | 4.07 | 4.03 | 4.05
| PSZ-AC:3_COOLC DXCOIL | 3.96 | 3.93 | 4.06 | 4.02 | 4.05 | 4.07 | 4.06 | 4.02 | 4.05 | 4.04 | 4.05 | 4.04 | 4.06 | 4.06 | 4.06 | 4.05
| PSZ-AC:4_COOLC DXCOIL | 3.9 | 3.92 | 4.06 | 3.99 | 4.06 | 4.04 | 4.08 | 3.95 | 4.06 | 4.04 | 3.92 | 4.07 | 3.96 | 4.06 | 4 | 4.06
| PSZ-AC:5_COOLC DXCOIL | 3.97 | 3.99 | 4.04 | 3.99 | 4.06 | 4.05 | 4.04 | 3.99 | 4.07 | 4.04 | 3.97 | 4.07 | 4.05 | 4.06 | 4.06 | 4.05
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC:1_FAN | 0.51 | 0.51 | 0.54 | 0.48 | 0.41 | 0.48 | 0.26 | 0.45 | 0.47 | 0.32 | 0.43 | 0.42 | 0.41 | 0.37 | 0.31 | 0.29
| PSZ-AC:2_FAN | 0.42 | 0.43 | 0.59 | 0.39 | 0.38 | 0.48 | 0.52 | 0.4 | 0.4 | 0.44 | 0.47 | 0.49 | 0.52 | 0.57 | 0.55 | 0.68
| PSZ-AC:3_FAN | 0.35 | 0.37 | 0.46 | 0.36 | 0.31 | 0.42 | 0.26 | 0.34 | 0.37 | 0.25 | 0.36 | 0.37 | 0.35 | 0.35 | 0.34 | 0.42
| PSZ-AC:4_FAN | 0.46 | 0.52 | 0.62 | 0.41 | 0.33 | 0.5 | 0.22 | 0.39 | 0.43 | 0.28 | 0.45 | 0.48 | 0.5 | 0.55 | 0.53 | 0.67
| PSZ-AC:5_FAN | 0.4 | 0.42 | 0.51 | 0.39 | 0.33 | 0.43 | 0.33 | 0.37 | 0.42 | 0.29 | 0.4 | 0.42 | 0.39 | 0.39 | 0.34 | 0.42
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.1025 | 0.12239 | 0.12627 | 0.11787 | 0.12863 | 0.10152 | 0.16288 | 0.075958 | 0.075399 | 0.073435 | 0.065822 | 0.075423 | 0.075045 | 0.076215 | 0.074834 | 0.10039
| Total Cost ($/m2) | 14.4 | 15.88 | 17.57 | 13.71 | 13.7 | 12.52 | 16.16 | 8.57 | 8.51 | 7.29 | 7.49 | 8.38 | 8.58 | 8.44 | 8.17 | 11.6
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011468 | 0.0080924 | 0.0083118 | 0.0097145 | 0.0085374 | 0.0077965 | 0.0086367 | 0.0096946 | 0.0069041 | 0.0084427 | 0.0083018 | 0.0068965 | 0.0079033 | 0.0080232 | 0.0078717 | 0.0041098
| Total Cost ($/m2) | 0.25 | 0.62 | 0.44 | 0.98 | 0.26 | 0.47 | 0.68 | 1.9 | 0.85 | 1.51 | 2.32 | 1.31 | 3 | 2.44 | 3.78 | 3.44
Total Utility Costs
| Cost Intensity ($/m2) | 14.65 | 16.5 | 18.01 | 14.69 | 13.96 | 12.99 | 16.84 | 10.47 | 9.37 | 8.8 | 9.81 | 9.7 | 11.59 | 10.88 | 11.95 | 15.04
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 19625 | 13213.8889 | 15358.3333 | 7486.1111 | 4191.6667 | 9716.6667 | 1138.8889 | 5605.5556 | 5186.1111 | 1080.5556 | 4605.5556 | 3297.2222 | 3994.4444 | 2208.3333 | 1427.7778 | 836.1111
| Interior Lighting | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222
| Exterior Lighting | 6619.4444 | 6616.6667 | 6613.8889 | 6613.8889 | 6608.3333 | 6605.5556 | 6611.1111 | 6605.5556 | 6608.3333 | 6594.4444 | 6608.3333 | 6602.7778 | 6602.7778 | 6602.7778 | 6597.2222 | 6558.3333
| Interior Equipment | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275 | 18275
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 11550 | 12480.5556 | 15122.2222 | 11330.5556 | 9636.1111 | 12702.7778 | 8936.1111 | 11405.5556 | 11900 | 9047.2222 | 12941.6667 | 12883.3333 | 13850 | 13758.3333 | 13763.8889 | 17633.3333
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 71816.6667 | 66333.3333 | 71122.2222 | 59452.7778 | 54458.3333 | 63050 | 50708.3333 | 57638.8889 | 57716.6667 | 50747.2222 | 58177.7778 | 56808.3333 | 58469.4444 | 56591.6667 | 55813.8889 | 59052.7778
Gas (MJ)
| Heating | 380 | 27840 | 16370 | 40050 | 4230 | 19520 | 28540 | 88400 | 51350 | 79720 | 131000 | 85380 | 181860 | 143330 | 232550 | 415020
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 10690 | 11090 | 10860 | 11480 | 11400 | 11140 | 11730 | 11780 | 11720 | 11940 | 12040 | 12030 | 12270 | 12310 | 12650 | 13110
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11070 | 38940 | 27230 | 51530 | 15630 | 30660 | 40270 | 100180 | 63070 | 91650 | 143040 | 97410 | 194140 | 155640 | 245200 | 428120
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 269610 | 277740 | 283270 | 265560 | 211680 | 257640 | 222820 | 307680 | 270850 | 274340 | 352480 | 301920 | 404630 | 359370 | 446130 | 640720
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 138.215 | 93.0628 | 108.1657 | 52.7232 | 29.5211 | 68.4326 | 8.021 | 39.4788 | 36.5248 | 7.6101 | 32.436 | 23.2217 | 28.1321 | 15.5529 | 10.0556 | 5.8886
| Interior Lighting (elec) | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046
| Exterior Lighting (elec) | 46.6195 | 46.5999 | 46.5803 | 46.5803 | 46.5412 | 46.5216 | 46.5608 | 46.5216 | 46.5412 | 46.4434 | 46.5412 | 46.5021 | 46.5021 | 46.5021 | 46.4629 | 46.1891
| Interior Equipment (elec) | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073 | 128.7073
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 81.3444 | 87.8981 | 106.5029 | 79.7989 | 67.8652 | 89.4632 | 62.9353 | 80.3271 | 83.8094 | 63.7178 | 91.1456 | 90.7348 | 97.5428 | 96.8973 | 96.9364 | 124.1881
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 505.7908 | 467.1727 | 500.8999 | 418.7143 | 383.5394 | 444.0488 | 357.1289 | 405.9394 | 406.4872 | 357.4028 | 409.7347 | 400.09 | 411.7889 | 398.5641 | 393.0863 | 415.8972
Gas (MJ/m2)
| Heating (gas) | 0.74341 | 54.4644 | 32.0252 | 78.3512 | 8.2753 | 38.1877 | 55.8338 | 172.94 | 100.4578 | 155.959 | 256.2798 | 167.0318 | 355.779 | 280.4014 | 454.9456 | 811.918
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.9132 | 21.6958 | 21.2458 | 22.4587 | 22.3022 | 21.7936 | 22.9478 | 23.0456 | 22.9282 | 23.3586 | 23.5543 | 23.5347 | 24.0042 | 24.0825 | 24.7476 | 25.6475
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 21.6566 | 76.1797 | 53.271 | 100.8099 | 30.5775 | 59.9812 | 78.7816 | 195.9856 | 123.386 | 179.2981 | 279.8341 | 190.5666 | 379.8028 | 304.4839 | 479.6932 | 837.546
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 527.4474 | 543.3524 | 554.1709 | 519.5242 | 414.1169 | 504.03 | 435.9105 | 601.925 | 529.8732 | 536.7008 | 689.5688 | 590.6565 | 791.5917 | 703.048 | 872.7796 | 1253.4627
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 16.521 | 14.1681 | 13.4284 | 11.4871 | 12.8415 | 12.9831 | 12.0384 | 12.4377 | 11.437 | 12.0211 | 12.625 | 12.6965 | 12.7003 | 12.754 | 12.5861 | 13.0543
| Feb | 16.9913 | 14.5654 | 14.1681 | 11.3256 | 12.4987 | 12.2603 | 11.8478 | 10.9628 | 11.7335 | 10.5535 | 12.625 | 11.4835 | 11.2059 | 11.4949 | 11.1062 | 13.0543
| Mar | 16.9519 | 15.2206 | 16.6169 | 12.8687 | 12.8582 | 13.4807 | 11.2765 | 11.609 | 11.9378 | 11.0412 | 11.4823 | 12.14 | 11.3748 | 12.0889 | 11.1057 | 13.0543
| Apr | 17.9277 | 16.3441 | 16.8435 | 14.6439 | 13.3205 | 15.5616 | 12.2401 | 12.9788 | 13.5655 | 10.8905 | 12.0243 | 13.4018 | 11.9418 | 11.6214 | 11.1416 | 11.6442
| May | 18.448 | 18.9481 | 20.2553 | 16.3762 | 13.6287 | 17.141 | 12.314 | 14.7008 | 14.9291 | 12.5197 | 14.835 | 14.3485 | 15.3067 | 13.1367 | 12.7909 | 13.0962
| Jun | 19.6053 | 19.204 | 23.8822 | 17.3569 | 13.8111 | 20.4667 | 13.0563 | 17.6409 | 16.3691 | 13.2305 | 17.417 | 15.4552 | 17.3245 | 16.0201 | 14.8548 | 14.8391
| Jul | 19.2639 | 20.291 | 23.4753 | 18.8634 | 14.4104 | 20.0992 | 13.959 | 18.4551 | 17.0124 | 14.1297 | 18.1035 | 16.6312 | 17.3764 | 16.2114 | 16.0705 | 14.7588
| Aug | 19.44 | 20.0041 | 22.9798 | 17.4425 | 15.0155 | 19.3487 | 13.0464 | 18.3081 | 17.0572 | 14.1032 | 17.9497 | 16.8234 | 17.2815 | 15.6808 | 15.3104 | 14.473
| Sep | 18.9956 | 18.6742 | 21.466 | 16.8362 | 15.3299 | 18.8949 | 14.9216 | 16.0141 | 15.2367 | 13.5591 | 15.8514 | 15.0272 | 15.6236 | 14.4842 | 14.1957 | 11.8537
| Oct | 18.3949 | 17.4371 | 17.8413 | 15.1302 | 14.1452 | 16.2049 | 12.8479 | 14.4625 | 13.9328 | 12.0211 | 14.6712 | 14.0145 | 12.7003 | 12.6991 | 12.5861 | 13.0543
| Nov | 17.294 | 15.6164 | 15.6069 | 12.7379 | 13.8972 | 14.212 | 12.2345 | 12.6792 | 12.5981 | 12.0211 | 14.1149 | 12.7916 | 12.7291 | 12.754 | 12.5861 | 13.0543
| Dec | 16.4262 | 14.1446 | 12.9219 | 11.3842 | 13.3065 | 13.1535 | 12.0384 | 12.4377 | 12.5981 | 12.0211 | 12.625 | 12.6965 | 12.7003 | 12.754 | 12.5861 | 13.0543
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 20-JAN-16:49 | 27-JAN-15:50 | 23-JAN-16:30 | 26-JAN-13:00 | 30-JAN-16:00 | 02-JAN-16:00 | 02-JAN-16:49 | 27-JAN-14:30 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-15:00 | 23-FEB-15:30 | 28-FEB-16:00 | 27-FEB-16:30 | 13-FEB-11:00 | 27-FEB-15:30 | 15-FEB-15:39 | 15-FEB-13:20 | 14-FEB-15:50 | 23-FEB-13:30 | 01-FEB-16:00 | 07-FEB-14:30 | 16-FEB-13:20 | 03-FEB-14:30 | 28-FEB-13:30 | 01-FEB-08:09
| Mar | 13-MAR-15:50 | 28-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-15:30 | 01-MAR-13:30 | 10-MAR-13:30 | 02-MAR-15:39 | 29-MAR-15:30 | 31-MAR-15:39 | 30-MAR-15:00 | 23-MAR-13:00 | 30-MAR-15:00 | 31-MAR-12:20 | 01-MAR-08:09
| Apr | 03-APR-14:30 | 21-APR-15:30 | 28-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:20 | 13-APR-14:00 | 05-APR-15:00 | 21-APR-15:00 | 19-APR-15:30 | 28-APR-15:00 | 26-APR-15:00 | 14-APR-15:50 | 06-APR-15:00 | 04-APR-14:00 | 25-APR-15:39
| May | 19-MAY-14:00 | 18-MAY-15:39 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-15:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 24-MAY-15:00 | 31-MAY-12:09 | 17-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 12-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-15:30 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 30-JUN-14:00 | 26-JUN-14:00 | 14-JUN-15:00 | 21-JUN-15:00
| Jul | 03-JUL-14:00 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:20 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 03-JUL-15:30 | 24-JUL-14:00 | 03-JUL-14:00 | 19-JUL-12:00 | 13-JUL-15:39 | 21-JUL-15:00 | 07-JUL-15:30 | 11-JUL-15:00
| Aug | 21-AUG-14:00 | 28-AUG-15:00 | 01-AUG-15:00 | 17-AUG-15:30 | 08-AUG-15:39 | 02-AUG-14:00 | 15-AUG-12:09 | 09-AUG-14:39 | 01-AUG-14:20 | 07-AUG-14:00 | 04-AUG-15:39 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-14:30
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:00 | 11-SEP-13:50 | 25-SEP-15:09 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 29-SEP-14:30 | 01-SEP-15:50 | 06-SEP-10:00 | 01-SEP-12:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 08-SEP-15:30
| Oct | 06-OCT-15:00 | 06-OCT-15:00 | 02-OCT-15:00 | 02-OCT-14:30 | 05-OCT-14:30 | 06-OCT-13:50 | 31-OCT-13:50 | 03-OCT-14:00 | 03-OCT-14:50 | 30-OCT-16:00 | 31-OCT-16:49 | 05-OCT-14:00 | 31-OCT-16:00 | 06-OCT-15:00 | 30-OCT-16:00 | 03-OCT-07:10
| Nov | 07-NOV-14:00 | 27-NOV-14:00 | 13-NOV-16:49 | 22-NOV-15:09 | 09-NOV-16:00 | 10-NOV-16:40 | 14-NOV-16:00 | 03-NOV-14:09 | 13-NOV-16:00 | 01-NOV-16:49 | 02-NOV-16:49 | 01-NOV-16:00 | 02-NOV-16:00 | 08-NOV-16:00 | 01-NOV-16:49 | 01-NOV-08:09
| Dec | 15-DEC-15:39 | 20-DEC-11:00 | 11-DEC-16:49 | 05-DEC-14:39 | 20-DEC-16:49 | 06-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
| Total Building | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Emissions
| Carbon Equivalent (kg) | 19895.2196 | 22828.4408 | 21960.7781 | 19243.0754 | 6646.1809 | 21818.2457 | 6652.3469 | 17361.0354 | 24714.3008 | 5348.8375 | 33596.2377 | 24962.5899 | 23514.5367 | 23486.9571 | 23526.6536 | 24337.0094
| CO2 (kg) | 46182.9764 | 57549.8352 | 51909.0866 | 44249.8418 | 17806.0167 | 51964.6807 | 17919.9456 | 40100.9077 | 58222.6246 | 13555.1074 | 79016.6602 | 59147.3832 | 56254.0227 | 56208.6547 | 56819.5064 | 63930.5577
| NOX (kg) | 80.9549 | 74.8193 | 86.6248 | 82.6995 | 15.2804 | 84.0489 | 15.4447 | 74.4808 | 99.3716 | 18.4423 | 137.0768 | 99.4793 | 93.3789 | 92.7434 | 91.9714 | 72.3988
| SO2 (kg) | 307.405 | 316.4222 | 285.999 | 208.6952 | 158.4709 | 346.8357 | 147.5678 | 210.4367 | 252.0517 | 39.2475 | 392.1021 | 248.0954 | 138.0497 | 151.1453 | 131.7981 | 300.7182
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0014 | 0.0009 | 0.0008 | 0.0008 | 0.0001 | 0.0007 | 0.0001 | 0.0009 | 0.001 | 0.0002 | 0.0012 | 0.001 | 0.001 | 0.0011 | 0.001 | 0.0011
| Water for Electricity (m3) | 38.0452 | 107.9327 | 2112.61 | 371.2031 | 956.1635 | 1729.72 | 890.336 | 13.0865 | 262.0773 | 518.4661 | 90.2575 | 257.9538 | 90.7121 | 3584.68 | 86.5936 | 60.3333

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 269.61 | 527.45 | 527.45
Net Site Energy | 269.61 | 527.45 | 527.45
Total Source Energy | 869.66 | 1701.36 | 1701.36
Net Source Energy | 869.66 | 1701.36 | 1701.36
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 0.38 | 0 | 0 | 0 | 0
Cooling | 70.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 41.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.69 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 258.54 | 11.07 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 1.627 | 2.69 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 6.49 | 0.351 | 0.351
North Total or Average |  |  | 16.73 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 42.95 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9582.59 | 7228.39 | 2354.2 | 0.75 | 3.9
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8140.73 | 6087.16 | 2053.58 | 0.75 | 3.87
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6265.33 | 4820.16 | 1445.17 | 0.77 | 3.96
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8701.54 | 6579.16 | 2122.38 | 0.76 | 3.9
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7082.74 | 5469.27 | 1613.47 | 0.77 | 3.97
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4777.15 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 3881.88 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 2971.6 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 4165.52 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3307.95 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 590.49 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 491.43 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 404 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 539.13 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 460.57 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3414.6138 | 5.9656 | 22.5717 | 0 | 0.0001 | 2793.5163 | 1468.9897
February | 3168.938 | 5.551 | 21.0627 | 0 | 0.0001 | 2606.774 | 1364.7626
March | 3733.5374 | 6.5426 | 24.8355 | 0 | 0.0001 | 3073.7074 | 1608.1742
April | 3669.2568 | 6.4318 | 24.4225 | 0 | 0.0001 | 3022.5911 | 1580.6716
May | 4109.0672 | 7.2065 | 27.3794 | 0 | 0.0001 | 3388.5462 | 1770.5124
June | 4267.652 | 7.4878 | 28.461 | 0 | 0.0001 | 3522.4099 | 1839.1606
July | 4216.5138 | 7.397 | 28.1115 | 0 | 0.0001 | 3479.1588 | 1817.0152
August | 4543.7833 | 7.9735 | 30.3124 | 0 | 0.0001 | 3751.5396 | 1958.2856
September | 4026.1315 | 7.0619 | 26.8337 | 0 | 0.0001 | 3321.0121 | 1734.8654
October | 3987.5755 | 6.9921 | 26.5593 | 0 | 0.0001 | 3287.0463 | 1718.0293
November | 3670.8916 | 6.4343 | 24.4305 | 0 | 0.0001 | 3023.5782 | 1581.3389
December | 3375.0155 | 5.911 | 22.4246 | 0 | 0.0001 | 2775.324 | 1453.4141
Annual Sum or Average | 46182.9764 | 80.9549 | 307.405 | 0 | 0.0014 | 38045.204 | 19895.2196
Minimum of Months | 3168.938 | 5.551 | 21.0627 | 0 | 0.0001 | 2606.774 | 1364.7626
Maximum of Months | 4543.7833 | 7.9735 | 30.3124 | 0 | 0.0001 | 3751.5396 | 1958.2856
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18983500000 | 16520.99 | 23-JAN-15:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 5372.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 17714500000 | 16991.267 | 22-FEB-15:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 5843.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 20887600000 | 16951.851 | 13-MAR-15:50 | 4950.048 | 3712.536 | 2485.624 | 0 | 5803.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 20540200000 | 17927.726 | 03-APR-14:30 | 4950.048 | 3712.536 | 2485.624 | 0 | 6779.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 23027100000 | 18448.022 | 19-MAY-14:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 7299.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23936700000 | 19605.342 | 28-JUN-14:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 8457.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 23642800000 | 19263.919 | 03-JUL-14:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 8115.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 25493800000 | 19439.972 | 21-AUG-14:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 8291.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 22568100000 | 18995.552 | 11-SEP-14:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 7847.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 22337300000 | 18394.945 | 06-OCT-15:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 7246.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 20546900000 | 17294 | 07-NOV-14:00 | 4950.048 | 3712.536 | 2485.624 | 0 | 6145.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 18859900000 | 16426.221 | 15-DEC-15:39 | 4950.048 | 3712.536 | 2485.624 | 0 | 5278.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 258538000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 17714500000 | 16426.221 |  | 4950.048 | 3712.536 | 2485.624 | 0 | 5278.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 25493800000 | 19605.342 |  | 4950.048 | 3712.536 | 2485.624 | 0 | 8457.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7361.05 | 126.95 | 0 | 7488.01
Cost per Total Building Area ($/m2) | 14.4 | 0.25 | 0 | 14.65
Cost per Net Conditioned Building Area ($/m2) | 14.4 | 0.25 | 0 | 14.65

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 277.74 | 543.35 | 543.35
Net Site Energy | 277.74 | 543.35 | 543.35
Total Source Energy | 42.52 | 83.18 | 83.18
Net Source Energy | 42.52 | 83.18 | 83.18
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 27.84 | 0 | 0 | 0 | 0
Cooling | 47.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 44.93 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.09 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 238.8 | 38.94 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 6.49 | 0.351 | 0.351
North Total or Average |  |  | 16.73 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 42.95 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9194.69 | 7091.9 | 2102.79 | 0.77 | 3.95
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7816.83 | 5994.42 | 1822.41 | 0.77 | 3.94
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6774.36 | 5149.16 | 1625.2 | 0.76 | 3.93
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9626.35 | 7334.58 | 2291.77 | 0.76 | 3.92
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7350.56 | 5742.35 | 1608.21 | 0.78 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 5803.67 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 4685.99 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3538.66 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 5318.65 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3928.08 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 596.34 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 500.36 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 424.89 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 607.14 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 490.62 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4442.4523 | 5.6308 | 22.3992 | 0 | 0.0001 | 7639.7845 | 1743.5485
February | 4032.4379 | 5.0926 | 20.0725 | 0 | 0.0001 | 6846.1426 | 1580.242
March | 4279.4178 | 5.5707 | 23.6285 | 0 | 0.0001 | 8059.8106 | 1698.4417
April | 4227.5722 | 5.5362 | 23.8047 | 0 | 0.0001 | 8120.0446 | 1682.1208
May | 5100.5007 | 6.6843 | 28.7899 | 0 | 0.0001 | 9820.5755 | 2030.0961
June | 5614.2395 | 7.3606 | 31.7313 | 0 | 0.0001 | 10823.9338 | 2234.9566
July | 5647.6018 | 7.4043 | 31.92 | 0 | 0.0001 | 10888.2886 | 2248.2387
August | 5931.5386 | 7.7771 | 33.5327 | 0 | 0.0001 | 11438.4125 | 2361.3433
September | 5134.3781 | 6.7299 | 28.9977 | 0 | 0.0001 | 9891.4703 | 2043.7327
October | 4705.1004 | 6.1639 | 26.5265 | 0 | 0.0001 | 9048.5014 | 1872.4291
November | 4141.4448 | 5.408 | 23.1033 | 0 | 0.0001 | 7880.7118 | 1645.8591
December | 4293.1511 | 5.4609 | 21.9159 | 0 | 0.0001 | 7475.0464 | 1687.4321
Annual Sum or Average | 57549.8352 | 74.8193 | 316.4222 | 0 | 0.0009 | 107932.7225 | 22828.4408
Minimum of Months | 4032.4379 | 5.0926 | 20.0725 | 0 | 0.0001 | 6846.1426 | 1580.242
Maximum of Months | 5931.5386 | 7.7771 | 33.5327 | 0 | 0.0001 | 11438.4125 | 2361.3433
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16903000000 | 14168.105 | 20-JAN-16:49 | 4950.048 | 3712.536 | 2619.347 | 0 | 2886.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 15147100000 | 14565.444 | 23-FEB-15:30 | 4950.048 | 3712.536 | 2619.347 | 0 | 3283.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17832300000 | 15220.577 | 28-MAR-14:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 3938.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 17965600000 | 16344.13 | 21-APR-15:30 | 4950.048 | 3712.536 | 2619.347 | 0 | 5062.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 21728000000 | 18948.123 | 18-MAY-15:39 | 4950.048 | 3712.536 | 2619.347 | 0 | 7666.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 23948000000 | 19203.996 | 12-JUN-14:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 7922.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 24090400000 | 20290.997 | 05-JUL-15:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 9009.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 25307500000 | 20004.147 | 28-AUG-15:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 8722.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 21884900000 | 18674.239 | 15-SEP-14:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 7392.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20019800000 | 17437.064 | 06-OCT-15:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 6155.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 17436100000 | 15616.403 | 27-NOV-14:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 4334.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16538600000 | 14144.647 | 20-DEC-11:00 | 4950.048 | 3712.536 | 2619.347 | 0 | 2862.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 238801000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15147100000 | 14144.647 |  | 4950.048 | 3712.536 | 2619.347 | 0 | 2862.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 25307500000 | 20290.997 |  | 4950.048 | 3712.536 | 2619.347 | 0 | 9009.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8118.66 | 315.12 | 0 | 8433.78
Cost per Total Building Area ($/m2) | 15.88 | 0.62 | 0 | 16.5
Cost per Net Conditioned Building Area ($/m2) | 15.88 | 0.62 | 0 | 16.5

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 283.27 | 554.17 | 554.17
Net Site Energy | 283.27 | 554.17 | 554.17
Total Source Energy | 839.58 | 1642.51 | 1642.51
Net Source Energy | 839.58 | 1642.51 | 1642.51
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16.37 | 0 | 0 | 0 | 0
Cooling | 55.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 54.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 10.86 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 256.04 | 27.23 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 2.61 | 4.28 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 2.61 | 4.28 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.778 | 0.96 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.25 | 0.25 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 6.49 | 0.351 | 0.351
North Total or Average |  |  | 16.73 | 6.49 | 0.61 | 0.61
Non-North Total or Average |  |  | 42.95 | 6.49 | 0.25 | 0.25
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8939.66 | 7139.71 | 1799.95 | 0.8 | 4.06
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9780.57 | 7811.31 | 1969.27 | 0.8 | 4.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7585.89 | 6058.51 | 1527.38 | 0.8 | 4.06
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10220.79 | 8162.88 | 2057.9 | 0.8 | 4.06
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8523.54 | 6807.37 | 1716.17 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 5271.73 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 5198.85 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3798.11 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 5375.05 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 4173.43 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 626.4 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 685.32 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 531.54 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.62 | 716.17 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 597.24 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3726.3151 | 6.0529 | 19.3333 | 0 | 0.0001 | 142802.2641 | 1559.7276
February | 3299.4613 | 5.403 | 17.4332 | 0 | 0 | 128769.9013 | 1385.4562
March | 3938.2248 | 6.5849 | 21.7913 | 0 | 0.0001 | 160967.6506 | 1667.4171
April | 3847.6707 | 6.4664 | 21.5285 | 0 | 0.0001 | 159027.8124 | 1632.4073
May | 4483.0196 | 7.5399 | 25.1247 | 0 | 0.0001 | 185593.3198 | 1902.5379
June | 5311.3984 | 8.9421 | 29.8319 | 0 | 0.0001 | 220365.3296 | 2254.9949
July | 5380.7616 | 9.0592 | 30.2237 | 0 | 0.0001 | 223259.4761 | 2284.4745
August | 5575.8155 | 9.3883 | 31.3248 | 0 | 0.0001 | 231393.0697 | 2367.3636
September | 4805.0762 | 8.0862 | 26.9627 | 0 | 0.0001 | 199170.6764 | 2039.6769
October | 4137.3872 | 6.9555 | 23.1649 | 0 | 0.0001 | 171115.8145 | 1755.537
November | 3590.265 | 6.0181 | 19.9742 | 0 | 0.0001 | 147545.8785 | 1521.6067
December | 3813.6913 | 6.1283 | 19.3057 | 0 | 0.0001 | 142595.1596 | 1589.5785
Annual Sum or Average | 51909.0866 | 86.6248 | 285.999 | 0 | 0.0008 | 2112610 | 21960.7781
Minimum of Months | 3299.4613 | 5.403 | 17.4332 | 0 | 0 | 128769.9013 | 1385.4562
Maximum of Months | 5575.8155 | 9.3883 | 31.3248 | 0 | 0.0001 | 231393.0697 | 2367.3636
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 17306800000 | 13428.43 | 27-JAN-15:50 | 4950.048 | 3712.536 | 3156.684 | 0 | 1609.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 15606200000 | 14168.095 | 28-FEB-16:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 2348.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 19508300000 | 16616.86 | 17-MAR-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 4797.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 19273200000 | 16843.493 | 28-APR-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 5024.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 22492800000 | 20255.32 | 30-MAY-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 8436.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 26707000000 | 23882.183 | 28-JUN-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 12062.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 27057700000 | 23475.291 | 11-JUL-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 11656.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 28043500000 | 22979.794 | 01-AUG-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 11160.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 24138300000 | 21465.983 | 11-SEP-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 9646.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 20738200000 | 17841.278 | 02-OCT-15:00 | 4950.048 | 3712.536 | 3156.684 | 0 | 6022.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 17881700000 | 15606.883 | 13-NOV-16:49 | 4950.048 | 3712.536 | 3156.684 | 0 | 3787.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 17281700000 | 12921.913 | 11-DEC-16:49 | 4950.048 | 3712.536 | 3156.684 | 0 | 1102.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 256036000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15606200000 | 12921.913 |  | 4950.048 | 3712.536 | 3156.684 | 0 | 1102.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 28043500000 | 23882.183 |  | 4950.048 | 3712.536 | 3156.684 | 0 | 12062.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8980.33 | 226.33 | 0 | 9206.66
Cost per Total Building Area ($/m2) | 17.57 | 0.44 | 0 | 18.01
Cost per Net Conditioned Building Area ($/m2) | 17.57 | 0.44 | 0 | 18.01

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 265.56 | 519.53 | 519.53
Net Site Energy | 265.56 | 519.53 | 519.53
Total Source Energy | 776.28 | 1518.66 | 1518.66
Net Source Energy | 776.28 | 1518.66 | 1518.66
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 40.05 | 0 | 0 | 0 | 0
Cooling | 26.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 40.79 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.48 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 214.03 | 51.53 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.43 | 0.531
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8374.12 | 6535.58 | 1838.54 | 0.78 | 4
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6924.78 | 5341.58 | 1583.21 | 0.77 | 3.95
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5987.61 | 4782.03 | 1205.57 | 0.8 | 4.02
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7199.21 | 5584.89 | 1614.32 | 0.78 | 3.99
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6592.68 | 5196.79 | 1395.89 | 0.79 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 5850.74 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 4586.94 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3598.12 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 4723.48 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3766.26 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 557.72 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 449.21 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 419.55 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 473.04 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 448.9 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 3973.414 | 6.89 | 16.1122 | 0 | 0.0001 | 28653.4757 | 1678.4297
February | 3377.6601 | 5.9619 | 14.2109 | 0 | 0.0001 | 25273.3688 | 1436.4664
March | 3432.7043 | 6.438 | 16.3003 | 0 | 0.0001 | 28993.3484 | 1494.8766
April | 3213.7472 | 6.1084 | 15.6579 | 0 | 0.0001 | 27851.4215 | 1407.0098
May | 3664.5323 | 7.0243 | 18.1438 | 0 | 0.0001 | 32273.8423 | 1609.8249
June | 4055.7634 | 7.7823 | 20.1201 | 0 | 0.0001 | 35789.268 | 1782.431
July | 4050.7007 | 7.7724 | 20.0942 | 0 | 0.0001 | 35743.2103 | 1780.1914
August | 4356.6708 | 8.3624 | 21.6264 | 0 | 0.0001 | 38468.6818 | 1914.9292
September | 3832.7378 | 7.3524 | 19.0044 | 0 | 0.0001 | 33804.6231 | 1684.2398
October | 3351.0416 | 6.4088 | 16.52 | 0 | 0.0001 | 29385.3061 | 1470.7588
November | 3266.571 | 6.086 | 15.3133 | 0 | 0.0001 | 27237.3175 | 1418.7957
December | 3674.2985 | 6.5126 | 15.5916 | 0 | 0.0001 | 27729.2468 | 1565.122
Annual Sum or Average | 44249.8418 | 82.6995 | 208.6952 | 0 | 0.0008 | 371203.1103 | 19243.0754
Minimum of Months | 3213.7472 | 5.9619 | 14.2109 | 0 | 0.0001 | 25273.3688 | 1407.0098
Maximum of Months | 4356.6708 | 8.3624 | 21.6264 | 0 | 0.0001 | 38468.6818 | 1914.9292
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16521300000 | 11487.057 | 23-JAN-16:30 | 4950.048 | 3712.536 | 2348.418 | 0 | 476.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14572400000 | 11325.628 | 27-FEB-16:30 | 4950.048 | 3712.536 | 2348.418 | 0 | 314.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 16717300000 | 12868.703 | 28-MAR-15:00 | 4950.048 | 3712.536 | 2348.418 | 0 | 1857.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 16058900000 | 14643.877 | 14-APR-15:00 | 4950.048 | 3712.536 | 2348.418 | 0 | 3632.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 18608800000 | 16376.204 | 15-MAY-14:00 | 4950.048 | 3712.536 | 2348.418 | 0 | 5365.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 20635800000 | 17356.913 | 19-JUN-14:00 | 4950.048 | 3712.536 | 2348.418 | 0 | 6345.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 20609200000 | 18863.395 | 03-JUL-15:00 | 4950.048 | 3712.536 | 2348.418 | 0 | 7852.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 22180700000 | 17442.458 | 17-AUG-15:30 | 4950.048 | 3712.536 | 2348.418 | 0 | 6431.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 19491400000 | 16836.249 | 11-SEP-13:50 | 4950.048 | 3712.536 | 2348.418 | 0 | 5825.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16943300000 | 15130.17 | 02-OCT-14:30 | 4950.048 | 3712.536 | 2348.418 | 0 | 4119.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15704800000 | 12737.853 | 22-NOV-15:09 | 4950.048 | 3712.536 | 2348.418 | 0 | 1726.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15988400000 | 11384.23 | 05-DEC-14:39 | 4950.048 | 3712.536 | 2348.418 | 0 | 373.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 214032000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14572400000 | 11325.628 |  | 4950.048 | 3712.536 | 2348.418 | 0 | 314.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 22180700000 | 18863.395 |  | 4950.048 | 3712.536 | 2348.418 | 0 | 7852.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7007.89 | 500.59 | 0 | 7508.49
Cost per Total Building Area ($/m2) | 13.71 | 0.98 | 0 | 14.69
Cost per Net Conditioned Building Area ($/m2) | 13.71 | 0.98 | 0 | 14.69

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 211.68 | 414.12 | 414.12
Net Site Energy | 211.68 | 414.12 | 414.12
Total Source Energy | 623.84 | 1220.45 | 1220.45
Net Source Energy | 623.84 | 1220.45 | 1220.45
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4.23 | 0 | 0 | 0 | 0
Cooling | 15.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 34.69 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.4 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 196.05 | 15.63 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.43 | 0.531
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6839.57 | 5462.46 | 1377.11 | 0.8 | 4.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6315.12 | 5043.61 | 1271.52 | 0.8 | 4.07
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5116.49 | 4086.31 | 1030.18 | 0.8 | 4.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5466.88 | 4366.15 | 1100.73 | 0.8 | 4.06
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5527.17 | 4414.3 | 1112.87 | 0.8 | 4.06
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4237.04 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 3681.26 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 2752.66 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 3329.11 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 2923.15 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 479.25 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 442.5 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 358.51 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 383.06 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 387.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1494.8032 | 1.2858 | 12.7542 | 0 | 0 | 76952.9576 | 556.2665
February | 1320.1744 | 1.1346 | 11.4547 | 0 | 0 | 69112.8746 | 491.8624
March | 1498.5779 | 1.2867 | 13.2084 | 0 | 0 | 79695.1414 | 558.9588
April | 1363.7803 | 1.1701 | 12.1758 | 0 | 0 | 73465.3075 | 509.1547
May | 1449.8155 | 1.2434 | 13.0332 | 0 | 0 | 78638.8472 | 541.5474
June | 1467.5682 | 1.2584 | 13.2323 | 0 | 0 | 79840.3254 | 548.2992
July | 1542.4772 | 1.3226 | 13.925 | 0 | 0 | 84019.4814 | 576.3385
August | 1714.617 | 1.47 | 15.5213 | 0 | 0 | 93651.4783 | 640.7867
September | 1556.5853 | 1.3346 | 14.0671 | 0 | 0 | 84877.0552 | 581.6549
October | 1522.8457 | 1.3058 | 13.7349 | 0 | 0 | 82872.9384 | 568.9642
November | 1423.2255 | 1.221 | 12.7317 | 0 | 0 | 76819.0091 | 531.4245
December | 1451.5465 | 1.2473 | 12.6323 | 0 | 0 | 76218.0419 | 540.9232
Annual Sum or Average | 17806.0167 | 15.2804 | 158.4709 | 0 | 0.0001 | 956163.4581 | 6646.1809
Minimum of Months | 1320.1744 | 1.1346 | 11.4547 | 0 | 0 | 69112.8746 | 491.8624
Maximum of Months | 1714.617 | 1.47 | 15.5213 | 0 | 0 | 93651.4783 | 640.7867
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15778200000 | 12841.462 | 26-JAN-13:00 | 4950.048 | 3712.536 | 2050.614 | 0 | 2128.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14170700000 | 12498.688 | 13-FEB-11:00 | 4950.048 | 3712.536 | 2050.614 | 0 | 1785.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 16340500000 | 12858.162 | 31-MAR-14:00 | 4950.048 | 3712.536 | 2050.614 | 0 | 2144.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15063100000 | 13320.487 | 11-APR-15:00 | 4950.048 | 3712.536 | 2050.614 | 0 | 2607.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16123900000 | 13628.719 | 30-MAY-15:00 | 4950.048 | 3712.536 | 2050.614 | 0 | 2915.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 16370300000 | 13811.133 | 30-JUN-15:30 | 4950.048 | 3712.536 | 2050.614 | 0 | 3097.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 17227200000 | 14410.398 | 10-JUL-15:20 | 4950.048 | 3712.536 | 2050.614 | 0 | 3697.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 19202100000 | 15015.517 | 08-AUG-15:39 | 4950.048 | 3712.536 | 2050.614 | 0 | 4302.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17403000000 | 15329.938 | 25-SEP-15:09 | 4950.048 | 3712.536 | 2050.614 | 0 | 4616.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16992100000 | 14145.171 | 05-OCT-14:30 | 4950.048 | 3712.536 | 2050.614 | 0 | 3431.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15750800000 | 13897.168 | 09-NOV-16:00 | 4950.048 | 3712.536 | 2050.614 | 0 | 1669.88 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15627600000 | 13306.509 | 20-DEC-16:49 | 4950.048 | 3712.536 | 2050.614 | 0 | 1079.221 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 196049000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14170700000 | 12498.688 |  | 4950.048 | 3712.536 | 2050.614 | 0 | 1079.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 19202100000 | 15329.938 |  | 4950.048 | 3712.536 | 2050.614 | 0 | 4616.74 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7004.81 | 133.44 | 0 | 7138.24
Cost per Total Building Area ($/m2) | 13.7 | 0.26 | 0 | 13.96
Cost per Net Conditioned Building Area ($/m2) | 13.7 | 0.26 | 0 | 13.96

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 257.64 | 504.04 | 504.04
Net Site Energy | 257.64 | 504.04 | 504.04
Total Source Energy | 845.4 | 1653.89 | 1653.89
Net Source Energy | 845.4 | 1653.89 | 1653.89
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 19.52 | 0 | 0 | 0 | 0
Cooling | 34.98 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 45.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.14 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 226.98 | 30.66 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.43 | 0.531
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7951.28 | 6350.33 | 1600.95 | 0.8 | 4.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7878.23 | 6291.99 | 1586.24 | 0.8 | 4.07
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6943.38 | 5545.36 | 1398.01 | 0.8 | 4.07
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8254.41 | 6592.43 | 1661.98 | 0.8 | 4.04
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7186.46 | 5739.5 | 1446.96 | 0.8 | 4.05
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 5103.8 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 4581.73 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3591.87 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 4726.55 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3685.46 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 557.15 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 552.03 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 486.52 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 578.39 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 503.55 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4176.0709 | 6.5075 | 25.5518 | 0 | 0 | 127421.6448 | 1727.7254
February | 3491.9785 | 5.6049 | 22.9023 | 0 | 0 | 114215.7633 | 1461.6903
March | 4005.2494 | 6.4476 | 26.4456 | 0 | 0 | 131887.4007 | 1678.4954
April | 3860.6678 | 6.295 | 26.2441 | 0 | 0 | 130885.1902 | 1626.2327
May | 4390.2474 | 7.1638 | 29.894 | 0 | 0.0001 | 149088.327 | 1849.8602
June | 5027.6838 | 8.2114 | 34.3047 | 0 | 0.0001 | 171085.8447 | 2119.2256
July | 5110.3775 | 8.347 | 34.874 | 0 | 0.0001 | 173925.1695 | 2154.1381
August | 5417.2906 | 8.8497 | 36.9814 | 0 | 0.0001 | 184435.1459 | 2283.6519
September | 4612.7763 | 7.5311 | 31.4484 | 0 | 0.0001 | 156840.5439 | 1944.0571
October | 4154.5885 | 6.777 | 28.2678 | 0 | 0.0001 | 140977.967 | 1750.3253
November | 3742.7137 | 6.048 | 24.9286 | 0 | 0 | 124322.688 | 1570.8669
December | 3975.0363 | 6.2657 | 24.993 | 0 | 0 | 124638.2511 | 1651.977
Annual Sum or Average | 51964.6807 | 84.0489 | 346.8357 | 0 | 0.0007 | 1729720 | 21818.2457
Minimum of Months | 3491.9785 | 5.6049 | 22.9023 | 0 | 0 | 114215.7633 | 1461.6903
Maximum of Months | 5417.2906 | 8.8497 | 36.9814 | 0 | 0.0001 | 184435.1459 | 2283.6519
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16720800000 | 12983.102 | 30-JAN-16:00 | 4950.048 | 3712.536 | 2677.636 | 0 | 128.792 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14987900000 | 12260.28 | 27-FEB-15:30 | 4950.048 | 3712.536 | 2677.636 | 0 | 920.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17306800000 | 13480.74 | 31-MAR-15:30 | 4950.048 | 3712.536 | 2677.636 | 0 | 2140.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 17175300000 | 15561.633 | 21-APR-15:20 | 4950.048 | 3712.536 | 2677.636 | 0 | 4221.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 19564000000 | 17140.957 | 31-MAY-15:00 | 4950.048 | 3712.536 | 2677.636 | 0 | 5800.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 22450600000 | 20466.696 | 27-JUN-15:00 | 4950.048 | 3712.536 | 2677.636 | 0 | 9126.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 22823200000 | 20099.196 | 24-JUL-15:00 | 4950.048 | 3712.536 | 2677.636 | 0 | 8758.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 24202300000 | 19348.737 | 02-AUG-14:00 | 4950.048 | 3712.536 | 2677.636 | 0 | 8008.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 20581200000 | 18894.907 | 01-SEP-14:00 | 4950.048 | 3712.536 | 2677.636 | 0 | 7554.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 18499700000 | 16204.903 | 06-OCT-13:50 | 4950.048 | 3712.536 | 2677.636 | 0 | 4864.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16314100000 | 14212.044 | 10-NOV-16:40 | 4950.048 | 3712.536 | 2677.636 | 0 | 1357.735 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16355500000 | 13153.538 | 06-DEC-16:30 | 4950.048 | 3712.536 | 2677.636 | 0 | 299.228 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 226981000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14987900000 | 12260.28 |  | 4950.048 | 3712.536 | 2677.636 | 0 | 128.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 24202300000 | 20466.696 |  | 4950.048 | 3712.536 | 2677.636 | 0 | 9126.475 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 6401.07 | 239.04 | 0 | 6640.11
Cost per Total Building Area ($/m2) | 12.52 | 0.47 | 0 | 12.99
Cost per Net Conditioned Building Area ($/m2) | 12.52 | 0.47 | 0 | 12.99

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 222.82 | 435.92 | 435.92
Net Site Energy | 222.82 | 435.92 | 435.92
Total Source Energy | 608.98 | 1191.37 | 1191.37
Net Source Energy | 608.98 | 1191.37 | 1191.37
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 28.54 | 0 | 0 | 0 | 0
Cooling | 4.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 32.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.73 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 182.55 | 40.27 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.82 | 0.82 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.82 | 0.82 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.82 | 0.82 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.82 | 0.82 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.82 | 0.82 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 6.49 | 0.82 | 0.82 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 6.49 | 0.61 | 0.61 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 6.49 | 0.669 | 0.668
North Total or Average |  |  | 16.73 | 6.49 | 0.82 | 0.82
Non-North Total or Average |  |  | 42.95 | 6.49 | 0.61 | 0.61
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4356.77 | 3479.56 | 877.21 | 0.8 | 4.07
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8639.41 | 6899.91 | 1739.5 | 0.8 | 4.06
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4360.19 | 3482.29 | 877.9 | 0.8 | 4.06
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3670.63 | 2931.57 | 739.06 | 0.8 | 4.08
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5543.05 | 4426.99 | 1116.06 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 3514.21 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 4912.24 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 2595.44 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 2842.66 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3088.13 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.26 | 305.28 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 605.36 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.26 | 305.52 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.22 | 257.2 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 388.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1815.5476 | 1.5784 | 12.5056 | 0 | 0 | 75442.1285 | 666.5182
February | 1414.308 | 1.2212 | 11.2477 | 0 | 0 | 67860.1773 | 523.8106
March | 1631.4735 | 1.4094 | 12.8461 | 0 | 0 | 77503.3215 | 603.8486
April | 1413.6125 | 1.218 | 11.6976 | 0 | 0 | 70576.2599 | 524.9425
May | 1423.1951 | 1.2232 | 12.3254 | 0 | 0 | 74366.503 | 530.1746
June | 1386.0412 | 1.1899 | 12.2457 | 0 | 0 | 73886.4147 | 517.0724
July | 1346.6621 | 1.1554 | 12.0296 | 0 | 0 | 72582.7822 | 502.7838
August | 1457.6747 | 1.2506 | 13.03 | 0 | 0 | 78619.1636 | 544.2577
September | 1394.3144 | 1.1961 | 12.4812 | 0 | 0 | 75307.8389 | 520.6542
October | 1439.9445 | 1.2365 | 12.6791 | 0 | 0 | 76500.9166 | 537.0505
November | 1471.2144 | 1.2676 | 12.1941 | 0 | 0 | 73572.2204 | 546.3935
December | 1725.9575 | 1.4983 | 12.2859 | 0 | 0 | 74118.2616 | 634.8405
Annual Sum or Average | 17919.9456 | 15.4447 | 147.5678 | 0 | 0.0001 | 890335.9884 | 6652.3469
Minimum of Months | 1346.6621 | 1.1554 | 11.2477 | 0 | 0 | 67860.1773 | 502.7838
Maximum of Months | 1815.5476 | 1.5784 | 13.03 | 0 | 0 | 78619.1636 | 666.5182
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15468500000 | 12038.437 | 02-JAN-16:00 | 4950.048 | 3712.536 | 1861.763 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13913900000 | 11847.81 | 15-FEB-15:39 | 4950.048 | 3712.536 | 1861.763 | 0 | 1323.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15891100000 | 11276.526 | 01-MAR-13:30 | 4950.048 | 3712.536 | 1861.763 | 0 | 752.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14470800000 | 12240.071 | 13-APR-14:00 | 4950.048 | 3712.536 | 1861.763 | 0 | 1715.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15247900000 | 12313.993 | 17-MAY-13:00 | 4950.048 | 3712.536 | 1861.763 | 0 | 1789.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 15149500000 | 13056.251 | 16-JUN-15:00 | 4950.048 | 3712.536 | 1861.763 | 0 | 2531.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 14882200000 | 13958.982 | 03-JUL-12:00 | 4950.048 | 3712.536 | 1861.763 | 0 | 3434.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 16119900000 | 13046.424 | 15-AUG-12:09 | 4950.048 | 3712.536 | 1861.763 | 0 | 2522.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 15440900000 | 14921.558 | 28-SEP-14:00 | 4950.048 | 3712.536 | 1861.763 | 0 | 4397.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15685600000 | 12847.946 | 31-OCT-13:50 | 4950.048 | 3712.536 | 1861.763 | 0 | 2323.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15085100000 | 12234.46 | 14-NOV-16:00 | 4950.048 | 3712.536 | 1861.763 | 0 | 196.023 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15197000000 | 12038.437 | 01-DEC-16:49 | 4950.048 | 3712.536 | 1861.763 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 182552000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13913900000 | 11276.526 |  | 4950.048 | 3712.536 | 1861.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 16119900000 | 14921.558 |  | 4950.048 | 3712.536 | 1861.763 | 0 | 4397.211 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8259.37 | 347.8 | 0 | 8607.17
Cost per Total Building Area ($/m2) | 16.16 | 0.68 | 0 | 16.84
Cost per Net Conditioned Building Area ($/m2) | 16.16 | 0.68 | 0 | 16.84

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 307.68 | 601.94 | 601.94
Net Site Energy | 307.68 | 601.94 | 601.94
Total Source Energy | 851.43 | 1665.7 | 1665.7
Net Source Energy | 851.43 | 1665.7 | 1665.7
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 88.4 | 0 | 0 | 0 | 0
Cooling | 20.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 41.06 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.78 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 207.5 | 100.18 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.43 | 0.531
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7961.63 | 6161.31 | 1800.32 | 0.77 | 3.97
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7706.22 | 5740.17 | 1966.05 | 0.74 | 3.88
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5770.49 | 4577.92 | 1192.57 | 0.79 | 4.02
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7006.51 | 5399.42 | 1607.1 | 0.77 | 3.95
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6445.17 | 5022.46 | 1422.71 | 0.78 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 6177.46 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 5077.14 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3751.43 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 5032.96 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3924.79 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 520.27 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 460.99 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 398.48 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 453.52 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 427.79 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 4291.3924 | 6.9928 | 17.1212 | 0 | 0.0001 | 1064.3928 | 1768.4871
February | 3586.0928 | 6.0044 | 15.1955 | 0 | 0.0001 | 944.7448 | 1492.5405
March | 3312.4832 | 6.0363 | 16.7418 | 0 | 0.0001 | 1041.0871 | 1423.4695
April | 2735.4066 | 5.2346 | 15.2048 | 0 | 0.0001 | 945.5995 | 1198.3306
May | 2837.0263 | 5.5957 | 16.6901 | 0 | 0.0001 | 1038.0209 | 1258.0899
June | 3331.6066 | 6.6071 | 19.7977 | 0 | 0.0001 | 1231.3055 | 1480.6925
July | 3435.6847 | 6.8152 | 20.4257 | 0 | 0.0001 | 1270.3646 | 1527.1066
August | 3732.7663 | 7.4084 | 22.2134 | 0 | 0.0001 | 1381.5499 | 1659.5105
September | 3000.1512 | 5.9455 | 17.8047 | 0 | 0.0001 | 1107.3524 | 1332.9946
October | 2902.8113 | 5.646 | 16.6385 | 0 | 0.0001 | 1034.7916 | 1280.0001
November | 3014.9219 | 5.6141 | 15.9009 | 0 | 0.0001 | 988.8415 | 1306.5794
December | 3920.5643 | 6.5807 | 16.7025 | 0 | 0.0001 | 1038.4452 | 1633.2341
Annual Sum or Average | 40100.9077 | 74.4808 | 210.4367 | 0 | 0.0009 | 13086.4959 | 17361.0354
Minimum of Months | 2735.4066 | 5.2346 | 15.1955 | 0 | 0.0001 | 944.7448 | 1198.3306
Maximum of Months | 4291.3924 | 7.4084 | 22.2134 | 0 | 0.0001 | 1381.5499 | 1768.4871
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16877400000 | 12437.725 | 02-JAN-16:49 | 4950.048 | 3712.536 | 2261.052 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14980300000 | 10962.771 | 15-FEB-13:20 | 4950.048 | 3712.536 | 2261.052 | 0 | 39.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 16507900000 | 11609.021 | 10-MAR-13:30 | 4950.048 | 3712.536 | 2261.052 | 0 | 685.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14993800000 | 12978.84 | 05-APR-15:00 | 4950.048 | 3712.536 | 2261.052 | 0 | 2055.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16459300000 | 14700.841 | 31-MAY-15:00 | 4950.048 | 3712.536 | 2261.052 | 0 | 3777.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 19524100000 | 17640.85 | 30-JUN-15:00 | 4950.048 | 3712.536 | 2261.052 | 0 | 6717.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 20143400000 | 18455.137 | 25-JUL-12:00 | 4950.048 | 3712.536 | 2261.052 | 0 | 7531.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 21906400000 | 18308.069 | 09-AUG-14:39 | 4950.048 | 3712.536 | 2261.052 | 0 | 7384.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17558600000 | 16014.119 | 08-SEP-14:00 | 4950.048 | 3712.536 | 2261.052 | 0 | 5090.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16408100000 | 14462.469 | 03-OCT-14:00 | 4950.048 | 3712.536 | 2261.052 | 0 | 3538.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15679500000 | 12679.188 | 03-NOV-14:09 | 4950.048 | 3712.536 | 2261.052 | 0 | 1755.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16466000000 | 12437.725 | 01-DEC-16:40 | 4950.048 | 3712.536 | 2261.052 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 207505000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14980300000 | 10962.771 |  | 4950.048 | 3712.536 | 2261.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 21906400000 | 18455.137 |  | 4950.048 | 3712.536 | 2261.052 | 0 | 7531.501 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4378.16 | 971.21 | 0 | 5349.38
Cost per Total Building Area ($/m2) | 8.57 | 1.9 | 0 | 10.47
Cost per Net Conditioned Building Area ($/m2) | 8.57 | 1.9 | 0 | 10.47

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 270.85 | 529.88 | 529.88
Net Site Energy | 270.85 | 529.88 | 529.88
Total Source Energy | 758.28 | 1483.46 | 1483.46
Net Source Energy | 758.28 | 1483.46 | 1483.46
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 51.35 | 0 | 0 | 0 | 0
Cooling | 18.67 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 42.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.72 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 207.78 | 63.07 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.43 | 0.531
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7815.95 | 6242.25 | 1573.7 | 0.8 | 4.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6584.8 | 5258.99 | 1325.82 | 0.8 | 4.06
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6159.89 | 4919.63 | 1240.26 | 0.8 | 4.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7095.79 | 5667.09 | 1428.7 | 0.8 | 4.06
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6900.76 | 5511.33 | 1389.43 | 0.8 | 4.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 5082.38 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 4079.17 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3192.36 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 4254.33 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3446.31 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 547.66 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 461.4 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 431.62 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 497.2 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 483.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5208.6341 | 8.4793 | 20.3267 | 0 | 0.0001 | 21132.5082 | 2170.6893
February | 4371.5906 | 7.2547 | 17.8075 | 0 | 0.0001 | 18514.4233 | 1835.3964
March | 4805.5157 | 8.1163 | 20.3406 | 0 | 0.0001 | 21149.0754 | 2031.4514
April | 4204.9803 | 7.2709 | 18.7125 | 0 | 0.0001 | 19457.4737 | 1794.147
May | 4733.9503 | 8.2585 | 21.4618 | 0 | 0.0001 | 22316.6763 | 2027.0079
June | 5108.947 | 8.9221 | 23.2124 | 0 | 0.0001 | 24137.0843 | 2188.4918
July | 5240.5219 | 9.1529 | 23.8162 | 0 | 0.0001 | 24764.9088 | 2244.9618
August | 5562.1181 | 9.7165 | 25.288 | 0 | 0.0001 | 26295.3939 | 2382.9157
September | 4800.5203 | 8.3819 | 21.8025 | 0 | 0.0001 | 22670.9887 | 2056.2171
October | 4462.6297 | 7.7403 | 19.9885 | 0 | 0.0001 | 20784.4053 | 1906.4242
November | 4590.7229 | 7.734 | 19.326 | 0 | 0.0001 | 20094.0641 | 1938.7415
December | 5132.4939 | 8.3441 | 19.9688 | 0 | 0.0001 | 20760.324 | 2137.8566
Annual Sum or Average | 58222.6246 | 99.3716 | 252.0517 | 0 | 0.001 | 262077.326 | 24714.3008
Minimum of Months | 4204.9803 | 7.2547 | 17.8075 | 0 | 0.0001 | 18514.4233 | 1794.147
Maximum of Months | 5562.1181 | 9.7165 | 25.288 | 0 | 0.0001 | 26295.3939 | 2382.9157
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 16754100000 | 11436.997 | 27-JAN-14:30 | 4950.048 | 3712.536 | 2421.422 | 0 | 352.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 14678500000 | 11733.525 | 14-FEB-15:50 | 4950.048 | 3712.536 | 2421.422 | 0 | 649.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 16767200000 | 11937.8 | 02-MAR-15:39 | 4950.048 | 3712.536 | 2421.422 | 0 | 853.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15426100000 | 13565.474 | 21-APR-15:00 | 4950.048 | 3712.536 | 2421.422 | 0 | 2481.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 17692900000 | 14929.118 | 31-MAY-15:00 | 4950.048 | 3712.536 | 2421.422 | 0 | 3845.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 19136200000 | 16369.053 | 29-JUN-15:30 | 4950.048 | 3712.536 | 2421.422 | 0 | 5285.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 19633900000 | 17012.388 | 03-JUL-15:30 | 4950.048 | 3712.536 | 2421.422 | 0 | 5928.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 20847300000 | 17057.246 | 01-AUG-14:20 | 4950.048 | 3712.536 | 2421.422 | 0 | 5973.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17973800000 | 15236.694 | 29-SEP-14:30 | 4950.048 | 3712.536 | 2421.422 | 0 | 4152.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16478100000 | 13932.815 | 03-OCT-14:50 | 4950.048 | 3712.536 | 2421.422 | 0 | 2848.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15930800000 | 12598.096 | 13-NOV-16:00 | 4950.048 | 3712.536 | 2421.422 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 16459000000 | 12598.096 | 01-DEC-16:00 | 4950.048 | 3712.536 | 2421.422 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 207778000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 14678500000 | 11436.997 |  | 4950.048 | 3712.536 | 2421.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20847300000 | 17057.246 |  | 4950.048 | 3712.536 | 2421.422 | 0 | 5973.239 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4351.79 | 435.44 | 0 | 4787.23
Cost per Total Building Area ($/m2) | 8.51 | 0.85 | 0 | 9.37
Cost per Net Conditioned Building Area ($/m2) | 8.51 | 0.85 | 0 | 9.37

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 274.34 | 536.71 | 536.71
Net Site Energy | 274.34 | 536.71 | 536.71
Total Source Energy | 418.33 | 818.39 | 818.39
Net Source Energy | 418.33 | 818.39 | 818.39
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 79.72 | 0 | 0 | 0 | 0
Cooling | 3.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.74 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 32.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 11.94 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 182.69 | 91.65 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.856 | 0.98 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.856 | 0.98 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.608 | 0.71 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.402 | 0.495 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.43 | 0.531
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.402 | 0.495
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5251.99 | 4194.53 | 1057.46 | 0.8 | 4.07
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7327.53 | 5852.17 | 1475.36 | 0.8 | 4.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4201.37 | 3355.44 | 845.92 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4675.82 | 3734.37 | 941.45 | 0.8 | 4.04
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4865.64 | 3885.97 | 979.67 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 4605.96 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 4866.33 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 2827.04 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 3776.98 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3099.93 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 368.01 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 513.44 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.25 | 294.39 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.28 | 327.63 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 340.94 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 1734.3192 | 2.1085 | 3.4182 | 0 | 0 | 45116.9248 | 657.4658
February | 1286.1826 | 1.6351 | 2.9909 | 0 | 0 | 39492.8922 | 495.2292
March | 1384.1622 | 1.7898 | 3.4112 | 0 | 0 | 45048.8807 | 536.1841
April | 1034.6885 | 1.4187 | 3.0657 | 0 | 0 | 40499.885 | 409.4591
May | 846.7786 | 1.2725 | 3.2209 | 0 | 0 | 42566.9315 | 347.0403
June | 785.6261 | 1.2146 | 3.2053 | 0 | 0 | 42363.8351 | 325.6169
July | 784.5855 | 1.2235 | 3.2677 | 0 | 0 | 43190.2895 | 326.3043
August | 855.1092 | 1.3374 | 3.5865 | 0 | 0 | 47404.7457 | 356.0558
September | 804.1694 | 1.2323 | 3.2108 | 0 | 0 | 42436.1125 | 332.1267
October | 973.1034 | 1.3942 | 3.266 | 0 | 0 | 43154.4425 | 391.5082
November | 1349.4992 | 1.7337 | 3.2536 | 0 | 0 | 42964.5987 | 521.5447
December | 1716.8836 | 2.0821 | 3.3508 | 0 | 0 | 44226.6062 | 650.3025
Annual Sum or Average | 13555.1074 | 18.4423 | 39.2475 | 0 | 0.0002 | 518466.1445 | 5348.8375
Minimum of Months | 784.5855 | 1.2146 | 2.9909 | 0 | 0 | 39492.8922 | 325.6169
Maximum of Months | 1734.3192 | 2.1085 | 3.5865 | 0 | 0 | 47404.7457 | 657.4658
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 15897400000 | 12021.079 | 02-JAN-16:30 | 4950.048 | 3712.536 | 1844.406 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 13915700000 | 10553.525 | 23-FEB-13:30 | 4950.048 | 3712.536 | 1844.406 | 0 | 46.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 15873500000 | 11041.202 | 29-MAR-15:30 | 4950.048 | 3712.536 | 1844.406 | 0 | 534.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 14270600000 | 10890.533 | 19-APR-15:30 | 4950.048 | 3712.536 | 1844.406 | 0 | 383.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 14998900000 | 12519.72 | 05-MAY-15:00 | 4950.048 | 3712.536 | 1844.406 | 0 | 2012.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 14927400000 | 13230.472 | 28-JUN-14:00 | 4950.048 | 3712.536 | 1844.406 | 0 | 2723.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 15218600000 | 14129.659 | 24-JUL-14:00 | 4950.048 | 3712.536 | 1844.406 | 0 | 3622.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 16703600000 | 14103.167 | 07-AUG-14:00 | 4950.048 | 3712.536 | 1844.406 | 0 | 3596.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 14952800000 | 13559.06 | 01-SEP-15:50 | 4950.048 | 3712.536 | 1844.406 | 0 | 3052.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 15205900000 | 12021.079 | 30-OCT-16:00 | 4950.048 | 3712.536 | 1844.406 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 15139000000 | 12021.079 | 01-NOV-16:49 | 4950.048 | 3712.536 | 1844.406 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 15583700000 | 12021.079 | 01-DEC-16:19 | 4950.048 | 3712.536 | 1844.406 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 182687000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 13915700000 | 10553.525 |  | 4950.048 | 3712.536 | 1844.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 16703600000 | 14129.659 |  | 4950.048 | 3712.536 | 1844.406 | 0 | 3622.669 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 3726.6 | 773.77 | 0 | 4500.37
Cost per Total Building Area ($/m2) | 7.29 | 1.51 | 0 | 8.8
Cost per Net Conditioned Building Area ($/m2) | 7.29 | 1.51 | 0 | 8.8

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 352.48 | 689.57 | 689.57
Net Site Energy | 352.48 | 689.57 | 689.57
Total Source Energy | 898.86 | 1758.48 | 1758.48
Net Source Energy | 898.86 | 1758.48 | 1758.48
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 131 | 0 | 0 | 0 | 0
Cooling | 16.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 46.59 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.04 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 209.44 | 143.04 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7641.05 | 5914.88 | 1726.17 | 0.77 | 3.97
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8809.81 | 6641.33 | 2168.48 | 0.75 | 3.89
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6002.09 | 4793.6 | 1208.49 | 0.8 | 4.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8316.32 | 6352.68 | 1963.64 | 0.76 | 3.92
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6759.67 | 5318.63 | 1441.04 | 0.79 | 3.97
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 6867.88 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 6156.58 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 4227.97 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 6072.38 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 4448.03 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 499.64 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 542.08 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 420.57 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 527.61 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.4 | 458.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7985.4977 | 12.7766 | 33.1728 | 0 | 0.0001 | 7634.4611 | 3292.3408
February | 6738.5477 | 11.0028 | 29.3192 | 0 | 0.0001 | 6747.9711 | 2799.3911
March | 6868.0733 | 11.6172 | 32.2984 | 0 | 0.0001 | 7434.2959 | 2891.7263
April | 5508.5588 | 9.7527 | 28.5131 | 0 | 0.0001 | 6563.6878 | 2360.9153
May | 5794.0865 | 10.4661 | 31.2372 | 0 | 0.0001 | 7191.0499 | 2503.1645
June | 6624.8385 | 12.0167 | 36.0155 | 0 | 0.0001 | 8291.1202 | 2866.8438
July | 6826.2422 | 12.3835 | 37.1194 | 0 | 0.0001 | 8545.2478 | 2954.1427
August | 7156.7033 | 12.9846 | 38.9263 | 0 | 0.0001 | 8961.2031 | 3097.3115
September | 5952.7612 | 10.7918 | 32.3271 | 0 | 0.0001 | 7441.9969 | 2575.4539
October | 5737.3923 | 10.2743 | 30.3958 | 0 | 0.0001 | 6997.2298 | 2470.1263
November | 6249.9353 | 10.7241 | 30.3054 | 0 | 0.0001 | 6975.7897 | 2646.0424
December | 7574.0233 | 12.2865 | 32.472 | 0 | 0.0001 | 7473.4664 | 3138.7791
Annual Sum or Average | 79016.6602 | 137.0768 | 392.1021 | 0 | 0.0012 | 90257.5197 | 33596.2377
Minimum of Months | 5508.5588 | 9.7527 | 28.5131 | 0 | 0.0001 | 6563.6878 | 2360.9153
Maximum of Months | 7985.4977 | 12.9846 | 38.9263 | 0 | 0.0001 | 8961.2031 | 3292.3408
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 17715200000 | 12624.97 | 02-JAN-16:30 | 4950.048 | 3712.536 | 2448.296 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 15658200000 | 12624.97 | 01-FEB-16:00 | 4950.048 | 3712.536 | 2448.296 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17250700000 | 11482.337 | 31-MAR-15:39 | 4950.048 | 3712.536 | 2448.296 | 0 | 371.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15230500000 | 12024.28 | 28-APR-15:00 | 4950.048 | 3712.536 | 2448.296 | 0 | 913.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16686300000 | 14834.951 | 30-MAY-15:00 | 4950.048 | 3712.536 | 2448.296 | 0 | 3724.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 19238900000 | 17417.017 | 08-JUN-12:00 | 4950.048 | 3712.536 | 2448.296 | 0 | 6306.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 19828600000 | 18103.55 | 03-JUL-14:00 | 4950.048 | 3712.536 | 2448.296 | 0 | 6992.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 20793800000 | 17949.708 | 04-AUG-15:39 | 4950.048 | 3712.536 | 2448.296 | 0 | 6838.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 17268600000 | 15851.356 | 06-SEP-10:00 | 4950.048 | 3712.536 | 2448.296 | 0 | 4740.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16236500000 | 14671.238 | 31-OCT-16:49 | 4950.048 | 3712.536 | 2448.296 | 0 | 2046.268 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16186800000 | 14114.85 | 02-NOV-16:49 | 4950.048 | 3712.536 | 2448.296 | 0 | 1489.88 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 17341600000 | 12624.97 | 01-DEC-16:19 | 4950.048 | 3712.536 | 2448.296 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 209436000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15230500000 | 11482.337 |  | 4950.048 | 3712.536 | 2448.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20793800000 | 18103.55 |  | 4950.048 | 3712.536 | 2448.296 | 0 | 6992.669 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 3829.35 | 1187.49 | 0 | 5016.85
Cost per Total Building Area ($/m2) | 7.49 | 2.32 | 0 | 9.81
Cost per Net Conditioned Building Area ($/m2) | 7.49 | 2.32 | 0 | 9.81

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 301.92 | 590.66 | 590.66
Net Site Energy | 301.92 | 590.66 | 590.66
Total Source Energy | 784.94 | 1535.61 | 1535.61
Net Source Energy | 784.94 | 1535.61 | 1535.61
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 85.38 | 0 | 0 | 0 | 0
Cooling | 11.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 46.38 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.03 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 204.51 | 97.41 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.698 | 0.78 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.698 | 0.78 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.194 | 0.2 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.194 | 0.2 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6919.79 | 5526.53 | 1393.26 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8091.44 | 6462.27 | 1629.17 | 0.8 | 4.06
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6047.08 | 4829.54 | 1217.55 | 0.8 | 4.04
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7883.55 | 6296.24 | 1587.31 | 0.8 | 4.07
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7019 | 5605.76 | 1413.24 | 0.8 | 4.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 5534.3 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 5169.33 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3493.26 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 5098.19 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 3825.83 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 484.87 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 566.97 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 423.72 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 552.4 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 491.82 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5757.9925 | 9.1111 | 21.0498 | 0 | 0.0001 | 21882.2721 | 2373.8843
February | 4851.9737 | 7.8165 | 18.4902 | 0 | 0.0001 | 19222.5525 | 2013.993
March | 5142.1064 | 8.5146 | 20.8441 | 0 | 0.0001 | 21671.3967 | 2157.0443
April | 4334.3118 | 7.402 | 18.7874 | 0 | 0.0001 | 19534.7109 | 1840.2555
May | 4496.3647 | 7.7783 | 20.029 | 0 | 0.0001 | 20826.3773 | 1918.8312
June | 4665.8814 | 8.1383 | 21.145 | 0 | 0.0001 | 21987.1844 | 1997.712
July | 5000.0692 | 8.7297 | 22.7058 | 0 | 0.0001 | 23610.209 | 2141.6351
August | 5334.267 | 9.3155 | 24.2357 | 0 | 0.0001 | 25201.0779 | 2285.0018
September | 4486.542 | 7.8194 | 20.2996 | 0 | 0.0001 | 21108.1183 | 1920.3361
October | 4535.275 | 7.8108 | 20.0136 | 0 | 0.0001 | 20810.0976 | 1932.0153
November | 4885.1661 | 8.0858 | 19.7847 | 0 | 0.0001 | 20570.0141 | 2048.9391
December | 5657.4335 | 8.9573 | 20.7106 | 0 | 0.0001 | 21529.761 | 2332.9423
Annual Sum or Average | 59147.3832 | 99.4793 | 248.0954 | 0 | 0.001 | 257953.7719 | 24962.5899
Minimum of Months | 4334.3118 | 7.402 | 18.4902 | 0 | 0.0001 | 19222.5525 | 1840.2555
Maximum of Months | 5757.9925 | 9.3155 | 24.2357 | 0 | 0.0001 | 25201.0779 | 2373.8843
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 17348500000 | 12696.45 | 02-JAN-16:49 | 4950.048 | 3712.536 | 2519.776 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 15239900000 | 11483.461 | 07-FEB-14:30 | 4950.048 | 3712.536 | 2519.776 | 0 | 301.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17181300000 | 12140.019 | 30-MAR-15:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 957.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15487400000 | 13401.792 | 26-APR-15:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 2219.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16511400000 | 14348.5 | 24-MAY-15:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 3166.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 17431700000 | 15455.196 | 28-JUN-13:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 4272.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 18718500000 | 16631.167 | 19-JUL-12:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 5448.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 19979700000 | 16823.426 | 30-AUG-13:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 5641.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 16734800000 | 15027.236 | 01-SEP-12:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 3844.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16498500000 | 14014.535 | 05-OCT-14:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 2832.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16308200000 | 12791.577 | 01-NOV-16:00 | 4950.048 | 3712.536 | 2519.776 | 0 | 95.127 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 17069100000 | 12696.45 | 01-DEC-16:40 | 4950.048 | 3712.536 | 2519.776 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 204509000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15239900000 | 11483.461 |  | 4950.048 | 3712.536 | 2519.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 19979700000 | 16823.426 |  | 4950.048 | 3712.536 | 2519.776 | 0 | 5641.066 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4284.63 | 671.79 | 0 | 4956.42
Cost per Total Building Area ($/m2) | 8.38 | 1.31 | 0 | 9.7
Cost per Net Conditioned Building Area ($/m2) | 8.38 | 1.31 | 0 | 9.7

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 404.63 | 791.59 | 791.59
Net Site Energy | 404.63 | 791.59 | 791.59
Total Source Energy | 935.45 | 1830.07 | 1830.07
Net Source Energy | 935.45 | 1830.07 | 1830.07
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 181.86 | 0 | 0 | 0 | 0
Cooling | 14.38 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 49.86 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.27 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 210.49 | 194.14 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7123.44 | 5581.89 | 1541.55 | 0.78 | 4
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9322.19 | 7175.18 | 2147.01 | 0.77 | 3.94
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5859.75 | 4679.92 | 1179.83 | 0.8 | 4.06
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8916.55 | 6905.18 | 2011.37 | 0.77 | 3.96
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6410.18 | 5118.57 | 1291.61 | 0.8 | 4.05
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 7204.5 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 6840.38 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 4367.37 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 6735.69 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 4588.93 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.41 | 478.69 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 601.74 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 410.59 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 583.6 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 448.98 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6778.0219 | 9.826 | 11.9929 | 0 | 0.0001 | 7874.1205 | 2697.0277
February | 5476.5021 | 8.216 | 10.5912 | 0 | 0.0001 | 6955.5487 | 2205.5982
March | 4979.3546 | 8.0411 | 11.4888 | 0 | 0.0001 | 7548.2848 | 2059.9516
April | 3674.724 | 6.4125 | 10.0358 | 0 | 0.0001 | 6595.8979 | 1565.9379
May | 3783.2493 | 6.8197 | 11.0414 | 0 | 0.0001 | 7257.7298 | 1633.0055
June | 4181.612 | 7.5829 | 12.3512 | 0 | 0.0001 | 8118.8096 | 1809.2736
July | 4293.1261 | 7.7869 | 12.6861 | 0 | 0.0001 | 8339.0042 | 1857.6871
August | 4605.6943 | 8.3566 | 13.6188 | 0 | 0.0001 | 8952.0766 | 1993.2038
September | 3651.3517 | 6.6075 | 10.7398 | 0 | 0.0001 | 7059.5531 | 1578.5185
October | 3867.7599 | 6.7753 | 10.6477 | 0 | 0.0001 | 6998.1706 | 1650.6847
November | 4761.8895 | 7.7063 | 11.0405 | 0 | 0.0001 | 7253.8245 | 1971.5558
December | 6200.7372 | 9.2483 | 11.8153 | 0 | 0.0001 | 7759.1176 | 2492.0925
Annual Sum or Average | 56254.0227 | 93.3789 | 138.0497 | 0 | 0.001 | 90712.138 | 23514.5367
Minimum of Months | 3651.3517 | 6.4125 | 10.0358 | 0 | 0.0001 | 6595.8979 | 1565.9379
Maximum of Months | 6778.0219 | 9.826 | 13.6188 | 0 | 0.0001 | 8952.0766 | 2697.0277
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18271300000 | 12700.282 | 02-JAN-16:40 | 4950.048 | 3712.536 | 2523.609 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 16139800000 | 11205.906 | 16-FEB-13:20 | 4950.048 | 3712.536 | 2523.609 | 0 | 19.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17515200000 | 11374.807 | 23-MAR-13:00 | 4950.048 | 3712.536 | 2523.609 | 0 | 188.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15305300000 | 11941.825 | 14-APR-15:50 | 4950.048 | 3712.536 | 2523.609 | 0 | 755.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16841000000 | 15306.704 | 31-MAY-12:09 | 4950.048 | 3712.536 | 2523.609 | 0 | 4120.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 18839100000 | 17324.522 | 30-JUN-14:00 | 4950.048 | 3712.536 | 2523.609 | 0 | 6138.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 19350000000 | 17376.381 | 13-JUL-15:39 | 4950.048 | 3712.536 | 2523.609 | 0 | 6190.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 20772600000 | 17281.487 | 25-AUG-15:00 | 4950.048 | 3712.536 | 2523.609 | 0 | 6095.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 16381200000 | 15623.598 | 14-SEP-14:00 | 4950.048 | 3712.536 | 2523.609 | 0 | 4437.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16238700000 | 12700.282 | 31-OCT-16:00 | 4950.048 | 3712.536 | 2523.609 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16832000000 | 12729.069 | 02-NOV-16:00 | 4950.048 | 3712.536 | 2523.609 | 0 | 28.787 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 18004400000 | 12700.282 | 01-DEC-16:30 | 4950.048 | 3712.536 | 2523.609 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 210491000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15305300000 | 11205.906 |  | 4950.048 | 3712.536 | 2523.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20772600000 | 17376.381 |  | 4950.048 | 3712.536 | 2523.609 | 0 | 6190.188 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4387.84 | 1534.35 | 0 | 5922.19
Cost per Total Building Area ($/m2) | 8.58 | 3 | 0 | 11.59
Cost per Net Conditioned Building Area ($/m2) | 8.58 | 3 | 0 | 11.59

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 359.37 | 703.05 | 703.05
Net Site Energy | 359.37 | 703.05 | 703.05
Total Source Energy | 878.11 | 1717.89 | 1717.89
Net Source Energy | 878.11 | 1717.89 | 1717.89
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 143.33 | 0 | 0 | 0 | 0
Cooling | 7.95 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 49.53 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.31 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 203.73 | 155.64 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.591 | 0.65 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.591 | 0.65 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.622 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.501 | 0.622
North Total or Average |  |  | 16.73 | 3.18 | 0.501 | 0.622
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.501 | 0.622
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6105.36 | 4876.07 | 1229.28 | 0.8 | 4.04
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9360.36 | 7475.7 | 1884.66 | 0.8 | 4.07
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5772.62 | 4610.34 | 1162.29 | 0.8 | 4.06
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9075.44 | 7248.15 | 1827.29 | 0.8 | 4.06
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6468.43 | 5166.05 | 1302.38 | 0.8 | 4.06
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 6285.67 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 6475.29 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 3920.73 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 6372.32 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 4172.19 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 427.8 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 655.88 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 404.49 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 635.92 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 453.24 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6319.9206 | 9.4438 | 13.4356 | 0 | 0.0001 | 318488.2029 | 2545.6801
February | 5177.5642 | 7.9514 | 11.7833 | 0 | 0.0001 | 279365.0692 | 2106.2837
March | 4976.7592 | 8.0879 | 12.9353 | 0 | 0.0001 | 306764.149 | 2067.601
April | 4035.6253 | 6.8027 | 11.3725 | 0 | 0.0001 | 269741.717 | 1700.2142
May | 3997.4767 | 6.9454 | 12.0136 | 0 | 0.0001 | 284982.4258 | 1704.1535
June | 4087.6594 | 7.1918 | 12.6092 | 0 | 0.0001 | 299123.8095 | 1751.274
July | 4304.5643 | 7.5957 | 13.3589 | 0 | 0.0001 | 316911.2236 | 1846.3564
August | 4492.1374 | 7.9279 | 13.9453 | 0 | 0.0001 | 330823.0593 | 1926.9272
September | 3901.9519 | 6.8509 | 11.9849 | 0 | 0.0001 | 284311.241 | 1670.3358
October | 4179.224 | 7.1454 | 12.1412 | 0 | 0.0001 | 287990.9658 | 1770.4435
November | 4780.0457 | 7.7625 | 12.4033 | 0 | 0.0001 | 294145.4769 | 1985.3211
December | 5955.7261 | 9.038 | 13.1622 | 0 | 0.0001 | 312034.5397 | 2412.3667
Annual Sum or Average | 56208.6547 | 92.7434 | 151.1453 | 0 | 0.0011 | 3584680 | 23486.9571
Minimum of Months | 3901.9519 | 6.8027 | 11.3725 | 0 | 0.0001 | 269741.717 | 1670.3358
Maximum of Months | 6319.9206 | 9.4438 | 13.9453 | 0 | 0.0001 | 330823.0593 | 2545.6801
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18100400000 | 12754.002 | 02-JAN-08:09 | 4950.048 | 3712.536 | 2577.328 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 15877000000 | 11494.935 | 03-FEB-14:30 | 4950.048 | 3712.536 | 2577.328 | 0 | 255.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17434100000 | 12088.864 | 30-MAR-15:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 848.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15330100000 | 11621.404 | 06-APR-15:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 381.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16196200000 | 13136.706 | 17-MAY-15:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 1896.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 16999900000 | 16020.111 | 26-JUN-14:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 4780.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 18010800000 | 16211.432 | 21-JUL-15:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 4971.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 18801500000 | 15680.779 | 09-AUG-15:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 4440.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 16158100000 | 14484.151 | 12-SEP-13:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 3244.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16367200000 | 12699.071 | 06-OCT-15:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 1459.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16717000000 | 12754.002 | 08-NOV-16:00 | 4950.048 | 3712.536 | 2577.328 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 17733700000 | 12754.002 | 01-DEC-16:40 | 4950.048 | 3712.536 | 2577.328 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 203726000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15330100000 | 11494.935 |  | 4950.048 | 3712.536 | 2577.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 18801500000 | 16211.432 |  | 4950.048 | 3712.536 | 2577.328 | 0 | 4971.519 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4313.13 | 1248.73 | 0 | 5561.87
Cost per Total Building Area ($/m2) | 8.44 | 2.44 | 0 | 10.88
Cost per Net Conditioned Building Area ($/m2) | 8.44 | 2.44 | 0 | 10.88

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 446.13 | 872.79 | 872.79
Net Site Energy | 446.13 | 872.79 | 872.79
Total Source Energy | 958.37 | 1874.89 | 1874.89
Net Source Energy | 958.37 | 1874.89 | 1874.89
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 232.55 | 0 | 0 | 0 | 0
Cooling | 5.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 49.55 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 12.65 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 200.93 | 245.2 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.512 | 0.55 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.512 | 0.55 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.493 | 0.56 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.651 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.651 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.651 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.651 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.651 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 3.18 | 0.651 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 3.18 | 0.501 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 3.18 | 0.543 | 0.532
North Total or Average |  |  | 16.73 | 3.18 | 0.651 | 0.64
Non-North Total or Average |  |  | 42.95 | 3.18 | 0.501 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5155.29 | 4117.3 | 1037.99 | 0.8 | 4.05
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9279.94 | 7360.19 | 1919.74 | 0.79 | 4.03
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5623.31 | 4491.09 | 1132.22 | 0.8 | 4.06
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9154.72 | 7201.17 | 1953.55 | 0.79 | 4
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5612.83 | 4482.72 | 1130.11 | 0.8 | 4.06
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 6667.89 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 7126.58 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 4307.22 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 7013.44 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 4303.07 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 361.23 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 640.47 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 394.03 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 620.45 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 393.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 6870.8811 | 9.9018 | 11.9656 | 0 | 0.0001 | 7855.8111 | 2728.3516
February | 5832.6351 | 8.528 | 10.5564 | 0 | 0.0001 | 6931.3698 | 2327.7841
March | 5575.7371 | 8.6329 | 11.656 | 0 | 0.0001 | 7656.3568 | 2271.1879
April | 4078.4434 | 6.8008 | 10.1089 | 0 | 0.0001 | 6642.6755 | 1707.7575
May | 3768.4413 | 6.5985 | 10.3649 | 0 | 0.0001 | 6812.2646 | 1608.0209
June | 3614.188 | 6.5369 | 10.6195 | 0 | 0.0001 | 6980.4728 | 1562.13
July | 3813.0751 | 6.908 | 11.2412 | 0 | 0.0001 | 7389.1704 | 1649.1885
August | 3956.9352 | 7.1588 | 11.633 | 0 | 0.0001 | 7646.7004 | 1710.4619
September | 3564.6016 | 6.3451 | 10.1415 | 0 | 0.0001 | 6665.9075 | 1530.9437
October | 4073.1146 | 6.9513 | 10.6147 | 0 | 0.0001 | 6975.7509 | 1720.762
November | 5172.2113 | 8.1021 | 11.1184 | 0 | 0.0001 | 7303.7228 | 2115.7998
December | 6499.2427 | 9.5073 | 11.7779 | 0 | 0.0001 | 7733.4406 | 2594.2657
Annual Sum or Average | 56819.5064 | 91.9714 | 131.7981 | 0 | 0.001 | 86593.6431 | 23526.6536
Minimum of Months | 3564.6016 | 6.3451 | 10.1089 | 0 | 0.0001 | 6642.6755 | 1530.9437
Maximum of Months | 6870.8811 | 9.9018 | 11.9656 | 0 | 0.0001 | 7855.8111 | 2728.3516
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 18228800000 | 12586.143 | 02-JAN-16:30 | 4950.048 | 3712.536 | 2409.47 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 16083700000 | 11106.202 | 28-FEB-13:30 | 4950.048 | 3712.536 | 2409.47 | 0 | 34.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 17766000000 | 11105.726 | 31-MAR-12:20 | 4950.048 | 3712.536 | 2409.47 | 0 | 33.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 15413800000 | 11141.615 | 04-APR-14:00 | 4950.048 | 3712.536 | 2409.47 | 0 | 69.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 15807300000 | 12790.919 | 31-MAY-15:00 | 4950.048 | 3712.536 | 2409.47 | 0 | 1718.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 16197700000 | 14854.812 | 14-JUN-15:00 | 4950.048 | 3712.536 | 2409.47 | 0 | 3782.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 17146000000 | 16070.45 | 07-JUL-15:30 | 4950.048 | 3712.536 | 2409.47 | 0 | 4998.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 17743600000 | 15310.426 | 11-AUG-15:30 | 4950.048 | 3712.536 | 2409.47 | 0 | 4238.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 15467700000 | 14195.656 | 07-SEP-14:00 | 4950.048 | 3712.536 | 2409.47 | 0 | 3123.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 16186700000 | 12586.143 | 30-OCT-16:00 | 4950.048 | 3712.536 | 2409.47 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 16947700000 | 12586.143 | 01-NOV-16:49 | 4950.048 | 3712.536 | 2409.47 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 17944900000 | 12586.143 | 01-DEC-16:19 | 4950.048 | 3712.536 | 2409.47 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 200934000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15413800000 | 11105.726 |  | 4950.048 | 3712.536 | 2409.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 18228800000 | 16070.45 |  | 4950.048 | 3712.536 | 2409.47 | 0 | 4998.396 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 4176.79 | 1930.14 | 0 | 6106.93
Cost per Total Building Area ($/m2) | 8.17 | 3.78 | 0 | 11.95
Cost per Net Conditioned Building Area ($/m2) | 8.17 | 3.78 | 0 | 11.95

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 640.72 | 1253.46 | 1253.46
Net Site Energy | 640.72 | 1253.46 | 1253.46
Total Source Energy | 1226.89 | 2400.21 | 2400.21
Net Source Energy | 1226.89 | 2400.21 | 2400.21
Area [m2]
Total Building Area | 511.16
Net Conditioned Building Area | 511.16
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 415.02 | 0 | 0 | 0 | 0
Cooling | 3.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 56.69 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 23.61 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 65.79 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 63.48 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 13.11 | 0 | 0 | 0 | 17.65
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 212.59 | 428.12 | 0 | 0 | 0 | 17.65
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORE_ZN | 149.66 | Yes | 456.46 | 1 | 0 | 0 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_1 | 113.45 | Yes | 346.02 | 1 | 84.45 | 20.64 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_2 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_3 | 113.45 | Yes | 346.02 | 1 | 84.45 | 16.73 | 10.76 | 18.59 | 8.07
PERIMETER_ZN_4 | 67.3 | Yes | 205.26 | 1 | 56.3 | 11.16 | 10.76 | 18.59 | 8.07
ATTIC | 567.98 | No | 720.19 | 1 | 0 | 0 | 0 |  | 0
Total | 1079.13 |  | 2279.22 |  | 281.51 | 59.68 | 5.0967 | 39.24 | 3.8225
Conditioned Total | 511.16 |  | 1559.03 |  | 281.51 | 59.68 | 10.76 | 18.59 | 8.07
Unconditioned Total | 567.98 |  | 720.19 |  | 0 | 0 | 0 |  | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
CORE_ZN_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 149.66 | 270 | 180
PERIMETER_ZN_1_WALL_SOUTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 84.45 | 180 | 90 | S
PERIMETER_ZN_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 135 | 180
PERIMETER_ZN_2_WALL_EAST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 56.3 | 90 | 90 | E
PERIMETER_ZN_2_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 270 | 180
PERIMETER_ZN_3_WALL_NORTH | EXT-WALLS | 0.08 | 0.454 | 0.49 | 84.45 | 0 | 90 | N
PERIMETER_ZN_3_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 113.45 | 180 | 180
PERIMETER_ZN_4_WALL_WEST | EXT-WALLS | 0.08 | 0.454 | 0.49 | 56.3 | 270 | 90 | W
PERIMETER_ZN_4_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.4 | 67.3 | 90 | 180
ATTIC_SOFFIT_WEST | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 11.44 | 270 | 180
ATTIC_SOFFIT_SOUTH | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 16.97 | 225 | 180
ATTIC_SOFFIT_EAST | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 11.44 | 45 | 180
ATTIC_SOFFIT_NORTH | EXPOSED-FLOOR | 0.3 | 0.363 | 0.4 | 16.97 | 315 | 180
ATTIC_ROOF_NORTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 0 | 18.45
ATTIC_ROOF_WEST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 270 | 18.45
ATTIC_ROOF_EAST | ROOFS | 0.22 | 0.154 | 0.16 | 101.87 | 90 | 18.45
ATTIC_ROOF_SOUTH | ROOFS | 0.22 | 0.154 | 0.16 | 197.51 | 180 | 18.45
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_1 | WINDOW_SOUTH | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_2 | WINDOW_SOUTH | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_3 | WINDOW_SOUTH | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_4 | WINDOW_SOUTH | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_5 | WINDOW_SOUTH | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_WINDOW_6 | WINDOW_SOUTH | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_1_WALL_SOUTH_DOOR | WINDOW_SOUTH | 3.91 | 3.91 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_ZN_2_WALL_EAST_WINDOW_4 | WINDOW_EAST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_3 | WINDOW_EAST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_2 | WINDOW_EAST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_2_WALL_EAST_WINDOW_1 | WINDOW_EAST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_2_WALL_EAST | 90 | E
PERIMETER_ZN_3_WALL_NORTH_WINDOW_1 | WINDOW_NORTH | 2.79 | 2.79 | 2.58 | 0.654 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_2 | WINDOW_NORTH | 2.79 | 2.79 | 2.58 | 0.654 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_3 | WINDOW_NORTH | 2.79 | 2.79 | 2.58 | 0.654 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_4 | WINDOW_NORTH | 2.79 | 2.79 | 2.58 | 0.654 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_5 | WINDOW_NORTH | 2.79 | 2.79 | 2.58 | 0.654 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_3_WALL_NORTH_WINDOW_6 | WINDOW_NORTH | 2.79 | 2.79 | 2.58 | 0.654 | 0.64 | No | PERIMETER_ZN_3_WALL_NORTH | 0 | N
PERIMETER_ZN_4_WALL_WEST_WINDOW_4 | WINDOW_WEST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_3 | WINDOW_WEST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_2 | WINDOW_WEST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
PERIMETER_ZN_4_WALL_WEST_WINDOW_1 | WINDOW_WEST | 2.79 | 2.79 | 2.58 | 0.504 | 0.49 | No | PERIMETER_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 59.68 | 2.58 | 0.546 | 0.532
North Total or Average |  |  | 16.73 | 2.58 | 0.654 | 0.64
Non-North Total or Average |  |  | 42.95 | 2.58 | 0.504 | 0.49
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4778.94 | 3816.73 | 962.21 | 0.8 | 4.06
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11312.66 | 9034.92 | 2277.74 | 0.8 | 4.05
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6965.94 | 5563.39 | 1402.56 | 0.8 | 4.05
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11044.76 | 8820.95 | 2223.8 | 0.8 | 4.06
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6965.94 | 5563.39 | 1402.56 | 0.8 | 4.05
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 8045.71 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 9252.92 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 5593.61 | 0.8
PSZ-AC:4_HEATC | Coil:Heating:Gas | 9143.05 | 0.8
PSZ-AC:5_HEATC | Coil:Heating:Gas | 5593.61 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 334.86 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.68 | 792.68 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 488.1 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 773.91 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 488.1 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 0 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.15 | 845000 | 0.8 | 4.51 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8354.6752 | 8.9413 | 28.4195 | 0 | 0.0001 | 5699.4411 | 3100.4239
February | 7267.5615 | 7.7962 | 25.1061 | 0 | 0.0001 | 5035.0506 | 2699.8236
March | 6611.1455 | 7.3141 | 27.4827 | 0 | 0.0001 | 5513.0725 | 2490.1327
April | 4409.0754 | 5.1074 | 23.131 | 0 | 0.0001 | 4641.3165 | 1696.0325
May | 3395.5348 | 4.1638 | 22.6342 | 0 | 0.0001 | 4542.5847 | 1341.6127
June | 3249.3314 | 4.0422 | 22.8673 | 0 | 0.0001 | 4589.5432 | 1292.7288
July | 3215.3132 | 4.0058 | 22.7513 | 0 | 0.0001 | 4566.2843 | 1280.1028
August | 3451.6961 | 4.2875 | 24.1575 | 0 | 0.0001 | 4848.47 | 1372.2532
September | 3566.8372 | 4.3104 | 22.45 | 0 | 0.0001 | 4505.3966 | 1399.5415
October | 5186.0241 | 5.9417 | 25.8326 | 0 | 0.0001 | 5183.1192 | 1984.7899
November | 7175.7292 | 7.8225 | 27.3988 | 0 | 0.0001 | 5495.6479 | 2684.9069
December | 8047.6339 | 8.6659 | 28.4872 | 0 | 0.0001 | 5713.3527 | 2994.661
Annual Sum or Average | 63930.5577 | 72.3988 | 300.7182 | 0 | 0.0011 | 60333.2793 | 24337.0094
Minimum of Months | 3215.3132 | 4.0058 | 22.45 | 0 | 0.0001 | 4505.3966 | 1280.1028
Maximum of Months | 8354.6752 | 8.9413 | 28.4872 | 0 | 0.0001 | 5713.3527 | 3100.4239
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 20082600000 | 13054.324 | 02-JAN-08:09 | 4950.048 | 3712.536 | 2877.651 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 17741500000 | 13054.324 | 01-FEB-08:09 | 4950.048 | 3712.536 | 2877.651 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 19425900000 | 13054.324 | 01-MAR-08:09 | 4950.048 | 3712.536 | 2877.651 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 16354200000 | 11644.237 | 25-APR-15:39 | 4950.048 | 3712.536 | 2877.651 | 0 | 104.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 16006300000 | 13096.185 | 24-MAY-14:00 | 4950.048 | 3712.536 | 2877.651 | 0 | 1555.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 16171800000 | 14839.118 | 21-JUN-15:00 | 4950.048 | 3712.536 | 2877.651 | 0 | 3298.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 16089800000 | 14758.813 | 11-JUL-15:00 | 4950.048 | 3712.536 | 2877.651 | 0 | 3218.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 17084100000 | 14473.01 | 15-AUG-14:30 | 4950.048 | 3712.536 | 2877.651 | 0 | 2932.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 15875300000 | 11853.723 | 08-SEP-15:30 | 4950.048 | 3712.536 | 2877.651 | 0 | 313.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 18263300000 | 13054.324 | 03-OCT-07:10 | 4950.048 | 3712.536 | 2877.651 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 19364500000 | 13054.324 | 01-NOV-08:09 | 4950.048 | 3712.536 | 2877.651 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 20131600000 | 13054.324 | 01-DEC-08:09 | 4950.048 | 3712.536 | 2877.651 | 0 | 0 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 212591000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 15875300000 | 11644.237 |  | 4950.048 | 3712.536 | 2877.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 20131600000 | 14839.118 |  | 4950.048 | 3712.536 | 2877.651 | 0 | 3298.883 | 1514.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 5928.13 | 1759.49 | 0 | 7687.61
Cost per Total Building Area ($/m2) | 11.6 | 3.44 | 0 | 15.04
Cost per Net Conditioned Building Area ($/m2) | 11.6 | 3.44 | 0 | 15.04

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_ZN Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_ZN Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_ZN Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_ZN Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  |  | Sat | 86 | 86 | 86 | 86 | 86 | 86 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 86 | 86 | 86 | 86 | 86 | 86