## BuildingSummary
Building Summary Retail new construction
|  | Value | Data Source
Program
| Building Name | Retail
| Available Fuel Types | gas, electricity
| Principal Building Activity | Retail
Form
| Total Floor Area (m2) | 2294 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.254
| East | 0
| North | 0
| West | 0
| Total | 0.071
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Back, CoreRetail, FrontRetail, PointofSale, FrontEntry
| Floor to Ceiling Height (m) | 6.1
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1177
| Net Dimensions - Total Area (m2) | 1093.1
| Wall to Skin Ratio | 0.34
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2294
| Net Dimensions - Total Area (m2) | 2294
| Roof to Skin Ratio | 0.66
Window Dimensions (m2)
| South | 83.9
| East | 0
| North | 0
| West | 0
| Total Area (m2) | 83.9
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2294
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Internal Mass | 244.23
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 7764.95
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.27 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (L ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Back_Space | Yes | 1 | 379.89 | 2317.33 | 6.1 | 416.17 | 0 | 27.8709 | 13.6303 | 8.608 | 8.07 | 0 |  | 3.8 | 0.6 | 279.7292 |  | 0.37388
Core_Retail | Yes | 1 | 1600.48 | 9762.95 | 6.1 | 356.86 | 0 | 6.1939 | 258.3982 | 18.292 | 3.228 | 0 |  | 3.8 | 0.6 | 1942.2011 |  | 0.2182
Point_of_Sale | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8 | 38.05 | 6.1939 | 24.3483 | 18.292 | 21.52 | 0 |  | 3.8 | 0.6 | 183.0097 |  | 0.40297
Front_Retail | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8 | 38.05 | 6.1939 | 24.3483 | 18.292 | 3.228 | 0 |  | 3.8 | 0.6 | 183.0097 |  | 0.40297
Front_Entry | Yes | 1 | 12 | 73.2 | 6.1 | 24.38 | 7.83 | 6.1939 | 1.9374 | 11.836 | 0 | 0 |  | 3.8 | 0.6 | 14.5621 |  | 1
Total Conditioned Zones |  |  | 2293.99 | 13993.36 |  | 1177.01 | 83.93 |  | 322.6626
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 118.8919 | 1176.8857 | 268.525 | 1264.6022 |  | 662.793 | 101.3348 | 1349.3302 | 63.1496 | 227.0515 | 1817.9529 | 420.0056 | 502.6576 | 48.3359 | 57.5322 | 7.2126
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 39.701 | 34.7308 | 32.9851 | 29.3171 | 17.6983 | 18.9139 | 11.321 | 28.5568 | 20.5353 | 16.4947 | 35.6837 | 26.5036 | 39.3556 | 28.9981 | 41.3672 | 33.9358
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 175.1315 | 165.0276 | 149.1311 | 152.8454 | 132.5795 | 111.5557 | 45.4005 | 141.1152 | 84.5551 | 73.2834 | 136.3307 | 80.6202 | 133.5927 | 66.2114 | 73.1541 | 70.1016
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 27.6189 | 24.3524 | 23.9863 | 24.4636 | 18.8738 | 17.643 | 16.7208 | 22.8721 | 14.1407 | 15.1159 | 22.212 | 13.5365 | 21.8117 | 13.6133 | 17.2159 | 17.9623
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 19.9002 | 21.0797 | 21.2641 | 16.1321 | 12.3032 | 14.2552 | 13.3468 | 16.7178 | 10.7815 | 12.0131 | 16.4849 | 12.6142 | 18.5513 | 13.6148 | 18.6614 | 15.8772
Heating (kW)
| FRONT_ENTRY UNIT HEATER COIL | 0.95403 | 2.02 | 1.5563 | 1.7423 | 0.82686 | 1.3927 | 1.2058 | 2.0401 | 1.753 | 1.5811 | 2.6275 | 2.2693 | 2.9444 | 2.853 | 3.0789 | 3.8682
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 17.0313 | 35.7828 | 28.9085 | 31.7803 | 16.5323 | 26.5768 | 20.7526 | 37.2709 | 31.9675 | 29.3491 | 46.3332 | 40.0305 | 51.0818 | 49.3654 | 52.7651 | 67.9225
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 92.9463 | 122.7019 | 103.523 | 132.3637 | 96.6681 | 111.911 | 106.8502 | 147.3445 | 117.0733 | 127.425 | 175.3247 | 144.2319 | 199.2298 | 188.1186 | 209.3484 | 277.2789
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 8.7581 | 18.5752 | 14.274 | 17.2225 | 9.1088 | 13.7235 | 11.323 | 20.3142 | 16.9453 | 15.71 | 26.0584 | 22.0221 | 29.1479 | 27.8587 | 30.3823 | 38.8004
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 8.7581 | 18.5752 | 14.2665 | 17.2227 | 9.1088 | 13.7229 | 11.3245 | 20.3152 | 16.9453 | 15.71 | 26.0591 | 22.0207 | 29.149 | 27.8605 | 30.3829 | 38.8004
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 3.21 | 3.45 | 3.51 | 3.44 | 3.7 | 3.78 | 3.95 | 3.44 | 3.77 | 3.91 | 3.44 | 3.72 | 3.44 | 3.77 | 3.21 | 3.73
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.55 | 3.45 | 3.49 | 3.95 | 3.91 | 3.49 | 3.91 | 3.49 | 4.3 | 3.19 | 4.32
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.49 | 3.54 | 3.48 | 3.76 | 3.85 | 4.01 | 3.49 | 4.04 | 3.98 | 3.49 | 4.04 | 3.49 | 4.04 | 3.78 | 4.01
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.45 | 3.51 | 3.65 | 3.75 | 3.74 | 4.02 | 3.65 | 3.95 | 3.92 | 3.65 | 3.93 | 3.65 | 4.04 | 3.69 | 4.01
Heating Efficiency (%)
| FRONT_ENTRY UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
| PSZ-AC:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| FRONT_ENTRY UNIT HEATERFAN | 0.04 | 0.09 | 0.07 | 0.08 | 0.04 | 0.06 | 0.05 | 0.09 | 0.09 | 0.07 | 0.12 | 0.12 | 0.13 | 0.14 | 0.14 | 0.17
| PSZ-AC:1_UNITARY_PACKAGE_FAN | 1.6 | 1.43 | 1.47 | 1.18 | 0.76 | 0.91 | 0.64 | 1.15 | 1.24 | 0.91 | 1.44 | 1.53 | 1.58 | 1.75 | 1.67 | 2.05
| PSZ-AC:2_UNITARY_PACKAGE_FAN | 7.05 | 6.65 | 6.01 | 6.16 | 5.34 | 4.67 | 2.74 | 5.68 | 4.6 | 3.91 | 5.49 | 4.29 | 5.38 | 3.97 | 3.43 | 4.23
| PSZ-AC:3_UNITARY_PACKAGE_FAN | 1.11 | 1.05 | 1.13 | 1.05 | 0.89 | 0.92 | 1.01 | 0.99 | 0.85 | 0.87 | 0.97 | 0.82 | 0.95 | 0.82 | 0.82 | 1.09
| PSZ-AC:4_UNITARY_PACKAGE_FAN | 0.8 | 0.85 | 0.96 | 0.65 | 0.56 | 0.64 | 0.8 | 0.67 | 0.61 | 0.66 | 0.66 | 0.7 | 0.75 | 0.82 | 0.8 | 0.96
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.085219 | 0.12168 | 0.10409 | 0.10234 | 0.13136 | 0.098887 | 0.14955 | 0.076193 | 0.03758 | 0.075203 | 0.052311 | 0.037603 | 0.061384 | 0.074977 | 0.060728 | 0.096773
| Total Cost ($/m2) | 16.71 | 21.02 | 17.67 | 15.09 | 16.67 | 14 | 15.79 | 10.63 | 4.84 | 8.77 | 7.04 | 4.67 | 8.18 | 9.1 | 6.79 | 11.96
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01145 | 0.0080414 | 0.0080788 | 0.0094655 | 0.008695 | 0.0076065 | 0.0085782 | 0.0096435 | 0.0068631 | 0.0084239 | 0.0082984 | 0.0069017 | 0.007863 | 0.0080906 | 0.0078567 | 0.0041286
| Total Cost ($/m2) | 0.02 | 0.71 | 0.57 | 1.58 | 0.4 | 0.92 | 1.56 | 3.02 | 1.56 | 2.7 | 3.64 | 2.3 | 4.56 | 4.11 | 6.1 | 4.98
Total Utility Costs
| Cost Intensity ($/m2) | 16.73 | 21.73 | 18.24 | 16.67 | 17.06 | 14.92 | 17.36 | 13.65 | 6.39 | 11.47 | 10.69 | 6.98 | 12.74 | 13.22 | 12.89 | 16.95
Energy - End Uses
Electricity (kWh)
| Heating | 13.8889 | 525 | 275 | 800 | 208.3333 | 416.6667 | 725 | 1377.7778 | 836.1111 | 1600 | 2041.6667 | 1402.7778 | 2602.7778 | 2319.4444 | 3183.3333 | 5144.4444
| Cooling | 151413.8889 | 102461.1111 | 100852.7778 | 51716.6667 | 17197.2222 | 54913.8889 | 3450 | 38036.1111 | 24283.3333 | 4486.1111 | 26327.7778 | 14588.8889 | 22069.4444 | 7788.8889 | 5586.1111 | 1963.8889
| Interior Lighting | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667
| Exterior Lighting | 13175 | 13169.4444 | 13166.6667 | 13163.8889 | 13155.5556 | 13152.7778 | 13158.3333 | 13150 | 13155.5556 | 13130.5556 | 13152.7778 | 13144.4444 | 13144.4444 | 13141.6667 | 13133.3333 | 13052.7778
| Interior Equipment | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 91036.1111 | 85947.2222 | 80858.3333 | 78344.4444 | 66350 | 62002.7778 | 30694.4444 | 73380.5556 | 62711.1111 | 54252.7778 | 73177.7778 | 61816.6667 | 73736.1111 | 61050 | 40472.2222 | 69255.5556
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 449830.5556 | 396300 | 389347.2222 | 338216.6667 | 291100 | 324677.7778 | 242222.2222 | 320136.1111 | 295177.7778 | 267661.1111 | 308894.4444 | 285147.2222 | 305744.4444 | 278491.6667 | 256569.4444 | 283611.1111
Gas (MJ)
| Heating | 4160 | 201820 | 161620 | 382080 | 104240 | 278220 | 418470 | 717440 | 520610 | 734590 | 1007320 | 765330 | 1329060 | 1166190 | 1780160 | 2768040
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4160 | 201820 | 161620 | 382080 | 104240 | 278220 | 418470 | 717440 | 520610 | 734590 | 1007320 | 765330 | 1329060 | 1166190 | 1780160 | 2768040
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1623550 | 1628500 | 1563270 | 1599670 | 1152200 | 1447070 | 1290470 | 1869930 | 1583240 | 1698170 | 2119340 | 1791860 | 2429750 | 2168760 | 2703810 | 3789030
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.021796 | 0.82389 | 0.43156 | 1.2555 | 0.32694 | 0.65388 | 1.1378 | 2.1622 | 1.3121 | 2.5109 | 3.204 | 2.2014 | 4.0846 | 3.6399 | 4.9957 | 8.0733
| Cooling (elec) | 237.6166 | 160.7941 | 158.2701 | 81.1599 | 26.9879 | 86.1774 | 5.4141 | 59.6908 | 38.1083 | 7.0401 | 41.3167 | 22.8946 | 34.634 | 12.2232 | 8.7664 | 3.082
| Interior Lighting (elec) | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829
| Exterior Lighting (elec) | 20.6758 | 20.667 | 20.6627 | 20.6583 | 20.6453 | 20.6409 | 20.6496 | 20.6365 | 20.6453 | 20.606 | 20.6409 | 20.6278 | 20.6278 | 20.6235 | 20.6104 | 20.484
| Interior Equipment (elec) | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 142.8646 | 134.8785 | 126.8924 | 122.9474 | 104.1243 | 97.3021 | 48.1693 | 115.1574 | 98.4137 | 85.1399 | 114.8392 | 97.01 | 115.7154 | 95.8069 | 63.5138 | 108.684
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 705.9272 | 621.9208 | 611.0096 | 530.7695 | 456.8285 | 509.5227 | 380.1237 | 502.3954 | 463.2278 | 420.0454 | 484.7536 | 447.4867 | 479.8103 | 437.042 | 402.6391 | 445.076
Gas (MJ/m2)
| Heating (gas) | 1.8134 | 87.9777 | 70.4537 | 166.557 | 45.4405 | 121.2821 | 182.4202 | 312.7477 | 226.9452 | 320.2237 | 439.1126 | 333.6239 | 579.3661 | 508.3675 | 776.0104 | 1206.6487
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1.8134 | 87.9777 | 70.4537 | 166.557 | 45.4405 | 121.2821 | 182.4202 | 312.7477 | 226.9452 | 320.2237 | 439.1126 | 333.6239 | 579.3661 | 508.3675 | 776.0104 | 1206.6487
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 707.7407 | 709.8985 | 681.4633 | 697.3309 | 502.269 | 630.8092 | 562.5439 | 815.143 | 690.1687 | 740.2691 | 923.8663 | 781.1106 | 1059.1807 | 945.4095 | 1178.6494 | 1651.7204
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 98.7892 | 86.5006 | 73.8237 | 64.1121 | 70.7811 | 60.4566 | 54.4843 | 63.2947 | 60.7416 | 59.2715 | 63.5613 | 60.9457 | 63.9541 | 61.2727 | 57.5438 | 64.3063
| Feb | 103.5598 | 86.9207 | 77.904 | 67.1483 | 67.4358 | 60.911 | 55.3492 | 62.8498 | 60.7613 | 59.219 | 63.1155 | 61.15 | 63.5452 | 60.9571 | 57.5176 | 64.0945
| Mar | 106.1613 | 92.557 | 92.8247 | 72.3492 | 68.4083 | 66.8228 | 53.981 | 69.8757 | 60.6012 | 59.0483 | 62.8557 | 62.2499 | 63.1557 | 58.143 | 56.935 | 61.8455
| Apr | 111.8421 | 108.3869 | 97.858 | 87.467 | 75.9513 | 84.0942 | 58.5147 | 71.3586 | 71.6041 | 58.2379 | 63.3271 | 66.9572 | 62.7913 | 57.6461 | 54.1015 | 59.352
| May | 119.0918 | 116.7674 | 115.8528 | 97.7832 | 72.9414 | 93.7372 | 59.7191 | 86.5334 | 77.8859 | 64.9222 | 85.3086 | 72.9067 | 100.595 | 65.4844 | 60.8888 | 60.732
| Jun | 125.0679 | 118.4722 | 132.7021 | 106.2953 | 76.4987 | 106.3187 | 61.5303 | 108.8504 | 86.2933 | 69.0548 | 103.8046 | 80.5795 | 102.7953 | 80.2029 | 75.2232 | 69.0132
| Jul | 122.4807 | 123.1636 | 130.2137 | 115.1088 | 83.3399 | 105.7155 | 67.6969 | 112.6353 | 88.6842 | 75.7946 | 107.1926 | 85.5945 | 106.9879 | 80.8896 | 86.0854 | 73.1778
| Aug | 123.4249 | 122.6029 | 131.0832 | 109.6023 | 89.3405 | 103.7716 | 63.2981 | 114.0358 | 87.4667 | 73.2947 | 106.135 | 85.9738 | 101.7004 | 77.5828 | 84.2851 | 68.8054
| Sep | 118.959 | 121.4047 | 121.869 | 101.0289 | 87.2221 | 101.2316 | 72.8389 | 97.281 | 79.3701 | 82.8293 | 89.3799 | 79.4544 | 86.1691 | 72.3732 | 67.7328 | 59.6806
| Oct | 116.4063 | 107.391 | 98.8121 | 90.1997 | 78.353 | 84.6531 | 59.3145 | 82.4095 | 69.4874 | 58.8635 | 72.2485 | 70.8959 | 74.2119 | 62.0368 | 62.2417 | 62.6992
| Nov | 106.5877 | 92.7984 | 87.2969 | 68.9169 | 71.545 | 64.4967 | 54.4408 | 75.2949 | 61.0453 | 59.1789 | 70.2496 | 60.7047 | 63.2293 | 60.4337 | 57.1791 | 63.2972
| Dec | 99.9183 | 89.2235 | 71.9994 | 63.717 | 71.3875 | 60.9574 | 54.3977 | 62.9766 | 60.8531 | 59.3314 | 63.1479 | 61.2046 | 63.7436 | 61.3225 | 57.4476 | 63.9644
Time of Peak Electrical Demand
| Jan | 23-JAN-15:00 | 03-JAN-13:00 | 28-JAN-16:00 | 13-JAN-17:00 | 26-JAN-13:00 | 10-JAN-17:00 | 04-JAN-17:00 | 30-JAN-17:00 | 12-JAN-17:00 | 31-JAN-17:00 | 26-JAN-17:00 | 05-JAN-17:00 | 04-JAN-17:00 | 06-JAN-17:00 | 11-JAN-17:00 | 13-JAN-09:09
| Feb | 25-FEB-13:00 | 23-FEB-15:00 | 28-FEB-16:00 | 18-FEB-16:10 | 13-FEB-11:00 | 08-FEB-17:10 | 15-FEB-17:49 | 23-FEB-17:00 | 14-FEB-17:49 | 11-FEB-17:00 | 03-FEB-17:00 | 15-FEB-17:00 | 01-FEB-17:00 | 23-FEB-17:00 | 01-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-16:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:30 | 31-MAR-15:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-17:00 | 06-MAR-17:00 | 03-MAR-17:00 | 30-MAR-15:00 | 01-MAR-17:00 | 30-MAR-14:50 | 09-MAR-17:00 | 02-MAR-17:00
| Apr | 01-APR-15:00 | 29-APR-14:00 | 01-APR-16:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-14:09 | 29-APR-15:30 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 04-APR-08:09 | 03-APR-08:09 | 10-APR-08:09
| May | 24-MAY-14:00 | 18-MAY-14:00 | 27-MAY-16:00 | 15-MAY-14:00 | 30-MAY-14:09 | 31-MAY-15:00 | 17-MAY-14:09 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-14:39 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-15:00
| Jul | 13-JUL-14:00 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-15:00
| Aug | 21-AUG-14:00 | 31-AUG-15:00 | 01-AUG-16:00 | 17-AUG-14:00 | 08-AUG-14:00 | 04-AUG-15:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-15:00
| Sep | 11-SEP-14:00 | 16-SEP-14:00 | 09-SEP-15:00 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:00 | 02-SEP-15:30 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 02-SEP-15:00 | 07-SEP-14:00 | 09-SEP-15:09
| Oct | 06-OCT-15:00 | 06-OCT-15:00 | 13-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-15:00 | 13-OCT-14:00 | 30-OCT-16:00 | 31-OCT-14:00 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 27-OCT-08:09
| Nov | 07-NOV-15:09 | 03-NOV-14:00 | 13-NOV-16:00 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-16:40 | 14-NOV-16:00 | 04-NOV-12:00 | 08-NOV-17:10 | 16-NOV-17:00 | 02-NOV-14:00 | 17-NOV-17:00 | 27-NOV-17:00 | 29-NOV-17:00 | 24-NOV-17:00 | 02-NOV-08:09
| Dec | 15-DEC-15:00 | 02-DEC-14:00 | 09-DEC-15:00 | 21-DEC-17:00 | 19-DEC-12:00 | 05-DEC-16:30 | 02-DEC-17:00 | 14-DEC-17:00 | 28-DEC-17:00 | 13-DEC-17:00 | 14-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 5376.07 | 5402.08 | 4609.91 | 4513.19 | 3357.28 | 4484.77 | 3155.81 | 4904.76 | 4094.32 | 2480.73 | 5043.21 | 4241.77 | 5234.38 | 4758.4 | 5118.53 | 6669.7
| Total Source Energy (MJ/m2) | 2343.54 | 2354.88 | 2009.56 | 1967.39 | 1463.51 | 1955 | 1375.68 | 2138.09 | 1784.8 | 1081.4 | 2198.44 | 1849.08 | 2281.78 | 2074.29 | 2231.27 | 2907.46
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 123441.1576 | 135829.3072 | 120448.8609 | 111073.4569 | 35899.4849 | 114522.9912 | 35853.6713 | 99328.0541 | 129966.8907 | 32741.5767 | 182851.1939 | 130283.0181 | 128620.9733 | 122800.6317 | 119923.1993 | 129719.5531
| CO2 (kg) | 285877.6857 | 342217.3098 | 284825.8719 | 256361.3289 | 96257.914 | 273861.4311 | 97378.5999 | 231112.5863 | 308084.229 | 84581.9892 | 432457.7458 | 311288.144 | 310513.673 | 297464.7419 | 295210.8208 | 344125.9442
| NOX (kg) | 503.9899 | 445.5386 | 474.8148 | 474.6664 | 82.658 | 438.5015 | 84.4699 | 421.2877 | 517.581 | 109.1539 | 739.5436 | 512.4073 | 503.1374 | 475.3369 | 453.6622 | 381.3787
| SO2 (kg) | 1925.459 | 1890.4002 | 1565.6873 | 1187.2463 | 847.0969 | 1786.0645 | 704.9498 | 1168.8204 | 1289.1158 | 207.0775 | 2081.9672 | 1245.3859 | 721.9632 | 743.917 | 606.0228 | 1444.4313
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0088 | 0.0053 | 0.0043 | 0.0044 | 0.0004 | 0.0034 | 0.0004 | 0.0048 | 0.0051 | 0.0009 | 0.0064 | 0.0049 | 0.0054 | 0.0053 | 0.0046 | 0.0052
| Water Environmental Factors (m3) | 238.3017 | 644.8249 | 11565.3 | 2111.7 | 5111.08 | 8907.22 | 4252.88 | 72.6831 | 1340.34 | 2734.64 | 479.2303 | 1294.8 | 474.345 | 17640.8 | 398.0527 | 289.7589

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1623.55 | 707.74 | 707.74
Net Site Energy | 1623.55 | 707.74 | 707.74
Total Source Energy | 5376.07 | 2343.54 | 2343.54
Net Source Energy | 5376.07 | 2343.54 | 2343.54
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.05 | 4.16 | 0 | 0 | 0 | 0
Cooling | 545.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.43 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 327.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1619.39 | 4.16 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.251 | 0.11 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.251 | 0.11 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.251 | 0.11 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39700.96 | 26841.15 | 12859.81 | 0.68 | 3.21
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 175131.53 | 118403.49 | 56728.04 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27618.9 | 18672.67 | 8946.22 | 0.68 | 3.44
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19900.2 | 13454.19 | 6446.01 | 0.68 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 954.03 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17031.34 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 92946.29 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 8758.13 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 8758.13 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.8 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.6 | 1821.3 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.05 | 13230.51 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1267.03 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.8 | 929.53 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20336.3746 | 35.7358 | 136.0552 | 0 | 0.0006 | 16838.5904 | 8769.5328
February | 18828.1967 | 33.183 | 126.7318 | 0 | 0.0006 | 15684.7752 | 8128.9309
March | 21844.8719 | 38.497 | 147.0163 | 0 | 0.0007 | 18195.2514 | 9431.0947
April | 22928.621 | 40.437 | 154.5472 | 0 | 0.0007 | 19127.3312 | 9902.0032
May | 25774.0299 | 45.4552 | 173.7263 | 0 | 0.0008 | 21501.0055 | 11130.8276
June | 26632.2197 | 46.9687 | 179.5108 | 0 | 0.0008 | 22216.9177 | 11501.4473
July | 27981.8105 | 49.3489 | 188.6076 | 0 | 0.0009 | 23342.7626 | 12084.2845
August | 28421.6708 | 50.1246 | 191.5724 | 0 | 0.0009 | 23709.6993 | 12274.2435
September | 26108.4672 | 46.045 | 175.9805 | 0 | 0.0008 | 21779.9971 | 11275.2584
October | 24919.8892 | 43.9489 | 167.9691 | 0 | 0.0008 | 20788.4711 | 10761.9566
November | 21860.9714 | 38.5541 | 147.3509 | 0 | 0.0007 | 18236.6851 | 9440.9258
December | 20240.5626 | 35.6916 | 136.391 | 0 | 0.0006 | 16880.2472 | 8740.6523
Annual Sum or Average | 285877.6857 | 503.9899 | 1925.459 | 0 | 0.0088 | 238301.7338 | 123441.1576
Minimum of Months | 18828.1967 | 33.183 | 126.7318 | 0 | 0.0006 | 15684.7752 | 8128.9309
Maximum of Months | 28421.6708 | 50.1246 | 191.5724 | 0 | 0.0009 | 23709.6993 | 12274.2435
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 114428000000 | 98789.175 | 23-JAN-15:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 36387.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 106587000000 | 103559.805 | 25-FEB-13:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 41158.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 123647000000 | 106161.28 | 13-MAR-14:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 43759.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 129981000000 | 111842.114 | 01-APR-15:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 49440.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 146111000000 | 119091.847 | 24-MAY-14:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 56690.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 150976000000 | 125067.928 | 27-JUN-14:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 62666.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 158627000000 | 122480.714 | 13-JUL-14:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 60079.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 161121000000 | 123424.863 | 21-AUG-14:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 61023.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 148007000000 | 118959.049 | 11-SEP-14:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 56557.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 141269000000 | 116406.298 | 06-OCT-15:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 54004.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 123928000000 | 106587.738 | 07-NOV-15:09 | 34382.155 | 10771.038 | 17248.355 | 0 | 44186.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 114711000000 | 99918.332 | 15-DEC-15:00 | 34382.155 | 10771.038 | 17248.355 | 0 | 37516.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1619390000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 106587000000 | 98789.175 |  | 34382.155 | 10771.038 | 17248.355 | 0 | 36387.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 161121000000 | 125067.928 |  | 34382.155 | 10771.038 | 17248.355 | 0 | 62666.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 38333.94 | 47.63 | 0 | 38381.57
Cost per Total Building Area ($/m2) | 16.71 | 0.02 | 0 | 16.73
Cost per Net Conditioned Building Area ($/m2) | 16.71 | 0.02 | 0 | 16.73

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1628.5 | 709.9 | 709.9
Net Site Energy | 1628.5 | 709.9 | 709.9
Total Source Energy | 5402.08 | 2354.88 | 2354.88
Net Source Energy | 5402.08 | 2354.88 | 2354.88
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.89 | 201.82 | 0 | 0 | 0 | 0
Cooling | 368.86 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.41 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 309.41 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1426.68 | 201.82 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.251 | 0.11 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.251 | 0.11 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.251 | 0.11 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34730.78 | 23657.2 | 11073.58 | 0.68 | 3.45
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 165027.61 | 111572.4 | 53455.21 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24352.38 | 16908.2 | 7444.18 | 0.69 | 3.49
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21079.74 | 14251.66 | 6828.08 | 0.68 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2019.98 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35782.85 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 122701.85 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18575.15 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18575.15 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.07 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.43 | 1626.29 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.65 | 12467.19 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1200.28 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.85 | 984.62 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 25114.4131 | 31.7228 | 125.089 | 0 | 0.0004 | 42664.1534 | 9842.593
February | 22734.7185 | 28.6457 | 112.2387 | 0 | 0.0003 | 38280.9337 | 8900.7849
March | 24088.6051 | 31.2923 | 132.0981 | 0 | 0.0004 | 45059.0023 | 9552.0987
April | 25309.5049 | 33.2357 | 143.7984 | 0 | 0.0004 | 49051.6203 | 10082.2987
May | 30630.697 | 40.26 | 174.5443 | 0 | 0.0005 | 59539.6156 | 12206.771
June | 34164.1445 | 44.9056 | 194.6989 | 0 | 0.0005 | 66414.6561 | 13615.0827
July | 36430.345 | 47.8844 | 207.6138 | 0 | 0.0006 | 70820.1207 | 14518.2081
August | 36228.2927 | 47.6188 | 206.4623 | 0 | 0.0006 | 70427.3335 | 14437.6863
September | 31656.803 | 41.61 | 180.4097 | 0 | 0.0005 | 61540.4165 | 12615.8578
October | 27955.1324 | 36.7266 | 159.0642 | 0 | 0.0004 | 54259.0781 | 11138.369
November | 23475.4259 | 30.6631 | 131.0788 | 0 | 0.0004 | 44712.0573 | 9330.5145
December | 24429.2278 | 30.9736 | 123.304 | 0 | 0.0004 | 42055.9071 | 9589.0425
Annual Sum or Average | 342217.3098 | 445.5386 | 1890.4002 | 0 | 0.0053 | 644824.8946 | 135829.3072
Minimum of Months | 22734.7185 | 28.6457 | 112.2387 | 0 | 0.0003 | 38280.9337 | 8900.7849
Maximum of Months | 36430.345 | 47.8844 | 207.6138 | 0 | 0.0006 | 70820.1207 | 14518.2081
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94394500000 | 86500.611 | 03-JAN-13:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 25069.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 84696600000 | 86920.656 | 23-FEB-15:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 25489.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 99693100000 | 92557.029 | 25-MAR-16:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 31125.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 108527000000 | 108386.896 | 29-APR-14:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 46955.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 131732000000 | 116767.44 | 18-MAY-14:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 55335.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 146943000000 | 118472.208 | 13-JUN-14:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 57040.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 156690000000 | 123163.61 | 05-JUL-15:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 61732.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 155821000000 | 122602.898 | 31-AUG-15:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 61171.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 136158000000 | 121404.727 | 16-SEP-14:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 59973.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 120048000000 | 107391.01 | 06-OCT-15:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 45959.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 98925500000 | 92798.429 | 03-NOV-14:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 31366.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 93048800000 | 89223.52 | 02-DEC-14:00 | 34382.155 | 10771.038 | 16278.379 | 0 | 27791.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1426680000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 84696600000 | 86500.611 |  | 34382.155 | 10771.038 | 16278.379 | 0 | 25069.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 156690000000 | 123163.61 |  | 34382.155 | 10771.038 | 16278.379 | 0 | 61732.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 48223.14 | 1622.92 | 0 | 49846.06
Cost per Total Building Area ($/m2) | 21.02 | 0.71 | 0 | 21.73
Cost per Net Conditioned Building Area ($/m2) | 21.02 | 0.71 | 0 | 21.73

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1563.27 | 681.46 | 681.46
Net Site Energy | 1563.27 | 681.46 | 681.46
Total Source Energy | 4609.91 | 2009.56 | 2009.56
Net Source Energy | 4609.91 | 2009.56 | 2009.56
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.99 | 161.62 | 0 | 0 | 0 | 0
Cooling | 363.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.4 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 291.09 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1401.65 | 161.62 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.251 | 0.11 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.251 | 0.11 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.251 | 0.11 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32985.08 | 23178.89 | 9806.19 | 0.7 | 3.51
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 149131.15 | 100825.07 | 48306.08 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23986.33 | 17202.96 | 6783.38 | 0.72 | 3.54
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21264.09 | 14984.2 | 6279.88 | 0.7 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1556.35 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28908.53 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 103522.96 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14274.03 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14266.52 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.45 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.47 | 1677.59 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.01 | 11266.28 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.13 | 1284.98 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.96 | 1089.29 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20049.0263 | 32.0132 | 100.0147 | 0 | 0.0003 | 738712.5303 | 8335.943
February | 18001.2273 | 28.9039 | 90.9606 | 0 | 0.0003 | 671847.401 | 7500.7474
March | 20464.0187 | 34.179 | 112.9589 | 0 | 0.0003 | 834401.6929 | 8660.4911
April | 21254.5539 | 35.8941 | 120.1782 | 0 | 0.0003 | 887748.8065 | 9034.9683
May | 24671.6646 | 41.6988 | 139.7452 | 0 | 0.0004 | 1032290 | 10490.964
June | 28981.4587 | 48.9834 | 164.1597 | 0 | 0.0004 | 1212640 | 12323.6294
July | 31055.9952 | 52.4897 | 175.9105 | 0 | 0.0005 | 1299440 | 13205.7734
August | 30950.5576 | 52.3115 | 175.3132 | 0 | 0.0005 | 1295030 | 13160.9388
September | 27305.9481 | 46.1515 | 154.6691 | 0 | 0.0004 | 1142530 | 11611.1611
October | 22496.3292 | 38.0112 | 127.3448 | 0 | 0.0003 | 940688.7511 | 9564.8578
November | 18946.612 | 31.6235 | 104.4302 | 0 | 0.0003 | 771401.249 | 8016.1802
December | 20648.4803 | 32.5552 | 100.0022 | 0 | 0.0003 | 738597.2031 | 8543.2064
Annual Sum or Average | 284825.8719 | 474.8148 | 1565.6873 | 0 | 0.0043 | 11565300 | 120448.8609
Minimum of Months | 18001.2273 | 28.9039 | 90.9606 | 0 | 0.0003 | 671847.401 | 7500.7474
Maximum of Months | 31055.9952 | 52.4897 | 175.9105 | 0 | 0.0005 | 1299440 | 13205.7734
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 89527700000 | 73823.739 | 28-JAN-16:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 13352.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 81424000000 | 77904.014 | 28-FEB-16:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 17432.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 101125000000 | 92824.726 | 17-MAR-15:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 32353.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 107590000000 | 97857.958 | 01-APR-16:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 37386.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 125108000000 | 115852.768 | 27-MAY-16:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 55381.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 146965000000 | 132702.102 | 28-JUN-15:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 72230.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 157485000000 | 130213.676 | 11-JUL-15:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 69742.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 156950000000 | 131083.246 | 01-AUG-16:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 70611.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 138468000000 | 121868.991 | 09-SEP-15:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 61397.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 114006000000 | 98812.136 | 13-OCT-15:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 38340.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 93489300000 | 87296.927 | 13-NOV-16:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 26825.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 89513700000 | 71999.361 | 09-DEC-15:00 | 34382.155 | 10771.038 | 15318.138 | 0 | 11528.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1401650000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 81424000000 | 71999.361 |  | 34382.155 | 10771.038 | 15318.138 | 0 | 11528.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 157485000000 | 132702.102 |  | 34382.155 | 10771.038 | 15318.138 | 0 | 72230.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40525.6 | 1305.69 | 0 | 41831.3
Cost per Total Building Area ($/m2) | 17.67 | 0.57 | 0 | 18.24
Cost per Net Conditioned Building Area ($/m2) | 17.67 | 0.57 | 0 | 18.24

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1599.67 | 697.33 | 697.33
Net Site Energy | 1599.67 | 697.33 | 697.33
Total Source Energy | 4513.19 | 1967.39 | 1967.39
Net Source Energy | 4513.19 | 1967.39 | 1967.39
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.88 | 382.08 | 0 | 0 | 0 | 0
Cooling | 186.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 282.04 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1217.58 | 382.08 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.252 | 0.162 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.252 | 0.162 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.252 | 0.162 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29317.09 | 19820.79 | 9496.3 | 0.68 | 3.44
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 152845.42 | 103336.23 | 49509.2 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24463.56 | 16913.05 | 7550.51 | 0.69 | 3.48
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16132.06 | 10906.62 | 5225.45 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1742.34 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31780.35 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 132363.68 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17222.53 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17222.69 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.2 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.18 | 1344.93 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.16 | 11546.88 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1192.21 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 753.52 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22580.255 | 37.9926 | 85.8663 | 0 | 0.0003 | 152689.1253 | 9430.9137
February | 19814.2713 | 33.8462 | 77.836 | 0 | 0.0003 | 138415.4743 | 8322.5394
March | 19670.8133 | 35.837 | 88.2329 | 0 | 0.0003 | 156929.7657 | 8468.7726
April | 18527.303 | 34.9635 | 89.0341 | 0 | 0.0003 | 158366.9142 | 8088.1892
May | 20837.8983 | 40.2246 | 104.5534 | 0 | 0.0004 | 185979.8603 | 9180.0794
June | 23240.0609 | 44.8765 | 116.679 | 0 | 0.0004 | 207548.9423 | 10239.7167
July | 25061.6653 | 48.394 | 125.8245 | 0 | 0.0005 | 223817.0609 | 11042.3271
August | 25245.493 | 48.749 | 126.7475 | 0 | 0.0005 | 225458.7617 | 11123.3227
September | 22286.9917 | 43.0362 | 111.894 | 0 | 0.0004 | 199037.4105 | 9819.7884
October | 18809.2269 | 35.8195 | 91.9772 | 0 | 0.0003 | 163604.7746 | 8241.1861
November | 18710.3666 | 33.8961 | 82.9882 | 0 | 0.0003 | 147599.6756 | 8037.6302
December | 21576.9835 | 37.0311 | 85.6132 | 0 | 0.0003 | 152247.4969 | 9078.9915
Annual Sum or Average | 256361.3289 | 474.6664 | 1187.2463 | 0 | 0.0044 | 2111700 | 111073.4569
Minimum of Months | 18527.303 | 33.8462 | 77.836 | 0 | 0.0003 | 138415.4743 | 8037.6302
Maximum of Months | 25245.493 | 48.749 | 126.7475 | 0 | 0.0005 | 225458.7617 | 11123.3227
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 88039100000 | 64112.078 | 13-JAN-17:00 | 34382.155 | 10771.038 | 14844.741 | 1100.144 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 79809100000 | 67148.348 | 18-FEB-16:10 | 34382.155 | 10771.038 | 14837.544 | 0 | 7157.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 90484200000 | 72349.161 | 28-MAR-15:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 12358.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 91312900000 | 87466.996 | 15-APR-15:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 27476.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 107234000000 | 97783.198 | 15-MAY-14:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 37792.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 119671000000 | 106295.348 | 19-JUN-14:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 46304.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 129051000000 | 115108.828 | 03-JUL-15:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 55118.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 129997000000 | 109602.27 | 17-AUG-14:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 49611.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 114763000000 | 101028.864 | 11-SEP-13:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 41038.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 94333000000 | 90199.742 | 12-OCT-15:00 | 34382.155 | 10771.038 | 14837.544 | 0 | 30209.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 85104600000 | 68916.859 | 22-NOV-15:09 | 34382.155 | 10771.038 | 14837.544 | 0 | 8926.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 87784500000 | 63717.039 | 21-DEC-17:00 | 34382.155 | 10771.038 | 14844.741 | 705.105 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1217580000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 79809100000 | 63717.039 |  | 34382.155 | 10771.038 | 14837.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 129997000000 | 115108.828 |  | 34382.155 | 10771.038 | 14844.741 | 1100.144 | 55118.091 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34614.23 | 3616.59 | 0 | 38230.82
Cost per Total Building Area ($/m2) | 15.09 | 1.58 | 0 | 16.67
Cost per Net Conditioned Building Area ($/m2) | 15.09 | 1.58 | 0 | 16.67

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1152.2 | 502.27 | 502.27
Net Site Energy | 1152.2 | 502.27 | 502.27
Total Source Energy | 3357.28 | 1463.51 | 1463.51
Net Source Energy | 3357.28 | 1463.51 | 1463.51
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.75 | 104.24 | 0 | 0 | 0 | 0
Cooling | 61.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 238.86 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1047.96 | 104.24 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.252 | 0.162 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.252 | 0.162 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.252 | 0.162 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17698.34 | 12258.44 | 5439.9 | 0.69 | 3.7
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 132579.46 | 89634.75 | 42944.71 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18873.75 | 13575.42 | 5298.33 | 0.72 | 3.76
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12303.17 | 8731.66 | 3571.51 | 0.71 | 3.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 826.86 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16532.3 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 96668.12 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 9108.83 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 9108.83 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.3 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.76 | 882.5 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.34 | 10015.86 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1018.43 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 653.52 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 8594.6244 | 7.4212 | 68.3207 | 0 | 0 | 412196.816 | 3183.0577
February | 7665.8522 | 6.6147 | 61.7538 | 0 | 0 | 372580.0355 | 2841.5726
March | 8317.5818 | 7.1613 | 69.8196 | 0 | 0 | 421254.8179 | 3091.746
April | 7658.2268 | 6.5818 | 66.4015 | 0 | 0 | 400639.6885 | 2853.1136
May | 7639.1452 | 6.5481 | 69.3327 | 0 | 0 | 418336.5127 | 2855.4525
June | 7431.3119 | 6.3621 | 68.8521 | 0 | 0 | 415441.19 | 2782.0545
July | 8244.26 | 7.0552 | 76.8874 | 0 | 0 | 463926.569 | 3087.9327
August | 8927.5403 | 7.64 | 83.2598 | 0 | 0 | 502376.7943 | 3343.8592
September | 8161.0316 | 6.984 | 76.1112 | 0 | 0 | 459243.2396 | 3056.7591
October | 7680.6226 | 6.5753 | 71.1986 | 0 | 0 | 429599.4609 | 2875.5004
November | 7609.6699 | 6.5359 | 66.7141 | 0 | 0 | 402528.1427 | 2837.2616
December | 8328.0474 | 7.1785 | 68.4453 | 0 | 0 | 412957.4249 | 3091.1751
Annual Sum or Average | 96257.914 | 82.658 | 847.0969 | 0 | 0.0004 | 5111080 | 35899.4849
Minimum of Months | 7431.3119 | 6.3621 | 61.7538 | 0 | 0 | 372580.0355 | 2782.0545
Maximum of Months | 8927.5403 | 7.64 | 83.2598 | 0 | 0 | 502376.7943 | 3343.8592
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 84515800000 | 70781.086 | 26-JAN-13:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 13057.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 76392900000 | 67435.84 | 13-FEB-11:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 9712.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 86373100000 | 68408.316 | 31-MAR-14:30 | 34382.155 | 10771.038 | 12570.311 | 0 | 10684.812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 82146200000 | 75951.331 | 11-APR-15:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 18227.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 85774700000 | 72941.372 | 30-MAY-14:09 | 34382.155 | 10771.038 | 12570.311 | 0 | 15217.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 85181100000 | 76498.698 | 30-JUN-14:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 18775.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 95122400000 | 83339.903 | 10-JUL-14:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 25616.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 103006000000 | 89340.45 | 08-AUG-14:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 31616.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 94162100000 | 87222.069 | 25-SEP-14:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 29498.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 88084000000 | 78352.979 | 19-OCT-10:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 20629.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 82533400000 | 71545.041 | 20-NOV-12:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 13821.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 84671800000 | 71387.501 | 19-DEC-12:00 | 34382.155 | 10771.038 | 12570.311 | 0 | 13663.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1047960000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 76392900000 | 67435.84 |  | 34382.155 | 10771.038 | 12570.311 | 0 | 9712.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 103006000000 | 89340.45 |  | 34382.155 | 10771.038 | 12570.311 | 0 | 31616.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 38239.39 | 906.37 | 0 | 39145.76
Cost per Total Building Area ($/m2) | 16.67 | 0.4 | 0 | 17.06
Cost per Net Conditioned Building Area ($/m2) | 16.67 | 0.4 | 0 | 17.06

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1447.07 | 630.81 | 630.81
Net Site Energy | 1447.07 | 630.81 | 630.81
Total Source Energy | 4484.77 | 1955 | 1955
Net Source Energy | 4484.77 | 1955 | 1955
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.5 | 278.22 | 0 | 0 | 0 | 0
Cooling | 197.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 223.21 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1168.84 | 278.22 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.252 | 0.162 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.252 | 0.162 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.252 | 0.162 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18913.95 | 13695.06 | 5218.89 | 0.72 | 3.78
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 111555.66 | 76516.87 | 35038.79 | 0.69 | 3.55
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17643.04 | 13205.37 | 4437.67 | 0.75 | 3.85
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14255.24 | 10066.18 | 4189.06 | 0.71 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1392.65 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26576.83 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 111911.03 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13723.51 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13722.85 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 6 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1037.58 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.67 | 8912.33 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.92 | 1048.45 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.64 | 747.51 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22739.7819 | 34.0994 | 126.5811 | 0 | 0.0002 | 631183.0217 | 9269.0793
February | 18665.4906 | 29.1224 | 114.5477 | 0 | 0.0002 | 571228.6657 | 7726.0617
March | 20999.9393 | 32.845 | 129.6286 | 0 | 0.0002 | 646437.7239 | 8700.6877
April | 19843.5276 | 32.3385 | 134.7297 | 0 | 0.0003 | 671926.9908 | 8356.9074
May | 22363.7364 | 36.6108 | 153.3937 | 0 | 0.0003 | 765014.2203 | 9435.439
June | 26253.5531 | 43.0539 | 180.7816 | 0 | 0.0003 | 901607.2222 | 11084.4069
July | 28024.4256 | 45.958 | 192.9758 | 0 | 0.0004 | 962423.0591 | 11832.0799
August | 28364.7436 | 46.5161 | 195.3192 | 0 | 0.0004 | 974110.3591 | 11975.7641
September | 24396.4632 | 40.0084 | 167.9937 | 0 | 0.0003 | 837830.5073 | 10300.3325
October | 20732.3707 | 33.8401 | 141.2637 | 0 | 0.0003 | 704515.3342 | 8736.754
November | 19369.5464 | 30.6045 | 122.474 | 0 | 0.0002 | 610770.8333 | 8057.3571
December | 22107.8526 | 33.5042 | 126.3757 | 0 | 0.0002 | 630173.7986 | 9048.1215
Annual Sum or Average | 273861.4311 | 438.5015 | 1786.0645 | 0 | 0.0034 | 8907220 | 114522.9912
Minimum of Months | 18665.4906 | 29.1224 | 114.5477 | 0 | 0.0002 | 571228.6657 | 7726.0617
Maximum of Months | 28364.7436 | 46.5161 | 195.3192 | 0 | 0.0004 | 974110.3591 | 11975.7641
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 82826400000 | 60456.59 | 10-JAN-17:00 | 34382.155 | 10771.038 | 11751.872 | 537.525 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 74958900000 | 60911.027 | 08-FEB-17:10 | 34382.155 | 10771.038 | 11745.873 | 0 | 997.961 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 84828200000 | 66822.801 | 31-MAR-15:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 9923.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 88173000000 | 84094.197 | 21-APR-15:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 27195.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 100388000000 | 93737.224 | 31-MAY-15:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 36838.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 118313000000 | 106318.68 | 27-JUN-15:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 49419.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 126293000000 | 105715.496 | 24-JUL-15:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 48816.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 127827000000 | 103771.563 | 04-AUG-15:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 46872.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 109944000000 | 101231.59 | 01-SEP-14:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 44332.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 92449300000 | 84653.056 | 03-OCT-14:00 | 34382.155 | 10771.038 | 11745.873 | 0 | 27753.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 80147800000 | 64496.67 | 10-NOV-16:40 | 34382.155 | 10771.038 | 11745.873 | 0 | 4583.604 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 82694000000 | 60957.446 | 05-DEC-16:30 | 34382.155 | 10771.038 | 11745.873 | 0 | 1044.38 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1168840000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 74958900000 | 60456.59 |  | 34382.155 | 10771.038 | 11745.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 127827000000 | 106318.68 |  | 34382.155 | 10771.038 | 11751.872 | 537.525 | 49419.614 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32106.54 | 2116.29 | 0 | 34222.83
Cost per Total Building Area ($/m2) | 14 | 0.92 | 0 | 14.92
Cost per Net Conditioned Building Area ($/m2) | 14 | 0.92 | 0 | 14.92

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1290.47 | 562.54 | 562.54
Net Site Energy | 1290.47 | 562.54 | 562.54
Total Source Energy | 3155.81 | 1375.68 | 1375.68
Net Source Energy | 3155.81 | 1375.68 | 1375.68
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.61 | 418.47 | 0 | 0 | 0 | 0
Cooling | 12.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 110.5 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 872 | 418.47 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.39 | 0.223 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.39 | 0.223 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.39 | 0.223 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11321.01 | 8750.93 | 2570.09 | 0.77 | 3.95
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 45400.52 | 36259.36 | 9141.16 | 0.8 | 3.45
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16720.79 | 13354.15 | 3366.64 | 0.8 | 4.01
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13346.83 | 10610.23 | 2736.61 | 0.79 | 4.02
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1205.85 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20752.58 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 106850.22 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11322.96 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11324.54 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.8 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.64 | 737.87 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.74 | 2999.43 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1150.7 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.8 | 925.82 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10532.6725 | 9.2309 | 59.3504 | 0 | 0 | 357981.6981 | 3826.4515
February | 8099.4921 | 7.0531 | 53.7481 | 0 | 0 | 324234.9871 | 2967.2312
March | 9224.9139 | 8.0367 | 60.5891 | 0 | 0 | 365500.3572 | 3377.6132
April | 8045.393 | 6.9844 | 57.251 | 0 | 0 | 345384.3341 | 2959.1946
May | 7571.0747 | 6.5425 | 59.2663 | 0 | 0 | 357565.4929 | 2801.1807
June | 7110.6708 | 6.1303 | 58.2407 | 0 | 0 | 351388.6142 | 2638.7053
July | 6903.2183 | 5.9365 | 59.2064 | 0 | 0 | 357224.7482 | 2569.8518
August | 7214.3807 | 6.2078 | 61.2229 | 0 | 0 | 369389.0589 | 2683.6979
September | 6927.9447 | 5.9568 | 59.6 | 0 | 0 | 359600.4581 | 2579.6106
October | 7462.8943 | 6.4404 | 59.9638 | 0 | 0 | 361780.0587 | 2765.8675
November | 8016.5032 | 6.9578 | 57.3132 | 0 | 0 | 345760.9165 | 2949.3857
December | 10269.4417 | 8.9928 | 59.1979 | 0 | 0 | 357068.9981 | 3734.8815
Annual Sum or Average | 97378.5999 | 84.4699 | 704.9498 | 0 | 0.0004 | 4252880 | 35853.6713
Minimum of Months | 6903.2183 | 5.9365 | 53.7481 | 0 | 0 | 324234.9871 | 2569.8518
Maximum of Months | 10532.6725 | 9.2309 | 61.2229 | 0 | 0 | 369389.0589 | 3826.4515
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73399700000 | 54484.261 | 04-JAN-17:00 | 34382.155 | 10771.038 | 5818.619 | 498.449 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66480400000 | 55349.192 | 15-FEB-17:49 | 34382.155 | 10771.038 | 5813.818 | 0 | 1368.182 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74941300000 | 53981.011 | 01-MAR-17:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 70816800000 | 58514.684 | 29-APR-13:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 7547.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 73314400000 | 59719.056 | 17-MAY-14:09 | 34382.155 | 10771.038 | 5813.818 | 0 | 8752.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 72047900000 | 61530.31 | 16-JUN-14:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 10563.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 73244500000 | 67696.911 | 03-JUL-12:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 16729.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 75738600000 | 63298.078 | 15-AUG-11:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 12331.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 73731600000 | 72838.912 | 28-SEP-14:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 21871.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 74178500000 | 59314.474 | 13-OCT-14:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 8347.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 70894000000 | 54440.806 | 14-NOV-16:00 | 34382.155 | 10771.038 | 5813.818 | 0 | 459.795 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73212600000 | 54397.659 | 02-DEC-17:00 | 34382.155 | 10771.038 | 5818.619 | 411.846 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 872000000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66480400000 | 53981.011 |  | 34382.155 | 10771.038 | 5813.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 75738600000 | 72838.912 |  | 34382.155 | 10771.038 | 5818.619 | 498.449 | 21871.901 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 36223.35 | 3589.72 | 0 | 39813.08
Cost per Total Building Area ($/m2) | 15.79 | 1.56 | 0 | 17.36
Cost per Net Conditioned Building Area ($/m2) | 15.79 | 1.56 | 0 | 17.36

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1869.93 | 815.14 | 815.14
Net Site Energy | 1869.93 | 815.14 | 815.14
Total Source Energy | 4904.76 | 2138.09 | 2138.09
Net Source Energy | 4904.76 | 2138.09 | 2138.09
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 4.96 | 717.44 | 0 | 0 | 0 | 0
Cooling | 136.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 264.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1152.49 | 717.44 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.385 | 0.305 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28556.8 | 19306.78 | 9250.03 | 0.68 | 3.44
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 141115.23 | 95405.64 | 45709.59 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22872.08 | 15899.3 | 6972.77 | 0.7 | 3.49
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16717.77 | 11302.61 | 5415.17 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2040.08 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37270.95 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 147344.5 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20314.22 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20315.19 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.16 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1310.05 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.68 | 10660.71 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1130.85 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.67 | 780.88 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 24305.1509 | 38.075 | 88.5202 | 0 | 0.0004 | 5502.4519 | 9876.2582
February | 20760.1749 | 33.2755 | 79.7716 | 0 | 0.0003 | 4959.0012 | 8504.7057
March | 19527.2227 | 33.963 | 89.7421 | 0 | 0.0004 | 5580.0471 | 8243.177
April | 16212.6874 | 30.0534 | 84.7533 | 0 | 0.0003 | 5270.5637 | 7013.6265
May | 16007.6937 | 31.4708 | 93.6059 | 0 | 0.0004 | 5821.6859 | 7089.2902
June | 18877.2755 | 37.7375 | 113.838 | 0 | 0.0005 | 7080.1858 | 8417.3024
July | 20707.4414 | 41.4026 | 124.9098 | 0 | 0.0005 | 7768.7996 | 9233.9473
August | 21216.2158 | 42.4193 | 127.976 | 0 | 0.0005 | 7959.5034 | 9460.7761
September | 16802.0272 | 33.5326 | 101.0126 | 0 | 0.0004 | 6282.4847 | 7486.8097
October | 16436.981 | 31.4376 | 91.2732 | 0 | 0.0004 | 5676.3402 | 7199.2076
November | 17573.4138 | 31.3854 | 85.2937 | 0 | 0.0004 | 5303.7654 | 7493.4302
December | 22686.302 | 36.535 | 88.124 | 0 | 0.0004 | 5478.3065 | 9309.5231
Annual Sum or Average | 231112.5863 | 421.2877 | 1168.8204 | 0 | 0.0048 | 72683.1356 | 99328.0541
Minimum of Months | 16007.6937 | 30.0534 | 79.7716 | 0 | 0.0003 | 4959.0012 | 7013.6265
Maximum of Months | 24305.1509 | 42.4193 | 127.976 | 0 | 0.0005 | 7959.5034 | 9876.2582
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 87249100000 | 63294.743 | 30-JAN-17:00 | 34382.155 | 10771.038 | 13890.653 | 1236.896 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 78631900000 | 62849.759 | 23-FEB-17:00 | 34382.155 | 10771.038 | 13890.653 | 791.912 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 88479500000 | 69875.75 | 09-MAR-15:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 10840.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 83572200000 | 71358.588 | 04-APR-15:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 12322.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 92311000000 | 86533.375 | 31-MAY-15:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 27497.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 112266000000 | 108850.442 | 30-JUN-15:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 49814.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 123185000000 | 112635.295 | 25-JUL-12:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 53599.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 126209000000 | 114035.815 | 09-AUG-14:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 55000.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 99617600000 | 97281.018 | 09-SEP-14:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 38245.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 90006300000 | 82409.541 | 20-OCT-15:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 23373.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 84098600000 | 75294.868 | 04-NOV-12:00 | 34382.155 | 10771.038 | 13882.491 | 0 | 16259.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 86866200000 | 62976.629 | 14-DEC-17:00 | 34382.155 | 10771.038 | 13890.653 | 918.783 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1152490000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 78631900000 | 62849.759 |  | 34382.155 | 10771.038 | 13882.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 126209000000 | 114035.815 |  | 34382.155 | 10771.038 | 13890.653 | 1236.896 | 55000.13 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24392.1 | 6918.64 | 0 | 31310.74
Cost per Total Building Area ($/m2) | 10.63 | 3.02 | 0 | 13.65
Cost per Net Conditioned Building Area ($/m2) | 10.63 | 3.02 | 0 | 13.65

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1583.24 | 690.17 | 690.17
Net Site Energy | 1583.24 | 690.17 | 690.17
Total Source Energy | 4094.32 | 1784.8 | 1784.8
Net Source Energy | 4094.32 | 1784.8 | 1784.8
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 3.01 | 520.61 | 0 | 0 | 0 | 0
Cooling | 87.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 225.76 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1062.64 | 520.61 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.385 | 0.305 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20535.35 | 16400.67 | 4134.69 | 0.8 | 3.77
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 84555.14 | 64411.81 | 20143.33 | 0.76 | 3.95
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14140.74 | 11293.58 | 2847.16 | 0.8 | 4.04
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10781.45 | 8330.84 | 2450.61 | 0.77 | 3.95
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1753.05 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31967.49 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 117073.3 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16945.25 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16945.25 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.48 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1413.22 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.6 | 8765.7 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.85 | 990.84 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 702.12 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 28060.4141 | 44.0949 | 100.9236 | 0 | 0.0004 | 104912.5062 | 11538.5926
February | 24145.0382 | 38.7615 | 91.2761 | 0 | 0.0004 | 94890.2697 | 10008.9383
March | 26097.075 | 42.7079 | 103.054 | 0 | 0.0004 | 107140.7937 | 10897.8385
April | 23030.2922 | 39.1039 | 98.6009 | 0 | 0.0004 | 102521.5455 | 9755.9563
May | 24459.0858 | 42.6576 | 110.8223 | 0 | 0.0004 | 115236.484 | 10471.8378
June | 25865.427 | 45.3747 | 118.6254 | 0 | 0.0005 | 123352.0412 | 11099.8786
July | 27639.7585 | 48.495 | 126.8042 | 0 | 0.0005 | 131856.8053 | 11862.0629
August | 27552.6494 | 48.342 | 126.4034 | 0 | 0.0005 | 131440.0958 | 11824.6585
September | 24424.2248 | 42.8367 | 111.9629 | 0 | 0.0004 | 116424.0076 | 10480.4451
October | 23678.0273 | 40.4197 | 102.5435 | 0 | 0.0004 | 106622.3716 | 10051.5389
November | 24898.9257 | 40.561 | 97.3154 | 0 | 0.0004 | 101173.2361 | 10379.2505
December | 28233.3108 | 44.2259 | 100.7842 | 0 | 0.0004 | 104766.4573 | 11595.8926
Annual Sum or Average | 308084.229 | 517.581 | 1289.1158 | 0 | 0.0051 | 1340340 | 129966.8907
Minimum of Months | 23030.2922 | 38.7615 | 91.2761 | 0 | 0.0004 | 94890.2697 | 9755.9563
Maximum of Months | 28233.3108 | 48.495 | 126.8042 | 0 | 0.0005 | 131856.8053 | 11862.0629
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 83175900000 | 60741.627 | 12-JAN-17:00 | 34382.155 | 10771.038 | 11880.369 | 694.065 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 75230100000 | 60761.3 | 14-FEB-17:49 | 34382.155 | 10771.038 | 11871.887 | 0 | 722.22 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 84942500000 | 60601.241 | 02-MAR-17:00 | 34382.155 | 10771.038 | 11871.887 | 0 | 562.16 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 81280300000 | 71604.052 | 22-APR-14:09 | 34382.155 | 10771.038 | 11871.887 | 0 | 14578.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 91360900000 | 77885.887 | 31-MAY-15:00 | 34382.155 | 10771.038 | 11871.887 | 0 | 20860.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 97795000000 | 86293.29 | 29-JUN-14:39 | 34382.155 | 10771.038 | 11871.887 | 0 | 29268.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 104538000000 | 88684.196 | 31-JUL-14:00 | 34382.155 | 10771.038 | 11871.887 | 0 | 31659.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 104207000000 | 87466.719 | 01-AUG-14:00 | 34382.155 | 10771.038 | 11871.887 | 0 | 30441.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 92302400000 | 79370.109 | 02-SEP-15:30 | 34382.155 | 10771.038 | 11871.887 | 0 | 22345.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 84531500000 | 69487.437 | 13-OCT-14:00 | 34382.155 | 10771.038 | 11871.887 | 0 | 12462.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 80211400000 | 61045.332 | 08-NOV-17:10 | 34382.155 | 10771.038 | 11871.887 | 0 | 1006.252 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 83060100000 | 60853.062 | 28-DEC-17:00 | 34382.155 | 10771.038 | 11880.369 | 805.499 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1062640000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 75230100000 | 60601.241 |  | 34382.155 | 10771.038 | 11871.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 104538000000 | 88684.196 |  | 34382.155 | 10771.038 | 11880.369 | 805.499 | 31659.116 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 11092.8 | 3573 | 0 | 14665.8
Cost per Total Building Area ($/m2) | 4.84 | 1.56 | 0 | 6.39
Cost per Net Conditioned Building Area ($/m2) | 4.84 | 1.56 | 0 | 6.39

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1698.17 | 740.27 | 740.27
Net Site Energy | 1698.17 | 740.27 | 740.27
Total Source Energy | 2480.73 | 1081.4 | 1081.4
Net Source Energy | 2480.73 | 1081.4 | 1081.4
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 5.76 | 734.59 | 0 | 0 | 0 | 0
Cooling | 16.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 195.31 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 963.58 | 734.59 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.857 | 0.984 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.385 | 0.305 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16494.67 | 12663.09 | 3831.58 | 0.77 | 3.91
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 73283.38 | 55388.03 | 17895.34 | 0.76 | 3.91
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15115.87 | 11832.95 | 3282.92 | 0.78 | 3.98
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12013.15 | 9171 | 2842.15 | 0.76 | 3.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1581.11 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29349.13 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 127424.99 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15709.98 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15710.04 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.38 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1039.59 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.91 | 7460.14 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.87 | 1013.54 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.66 | 761.07 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10860.3412 | 12.5924 | 17.5032 | 0 | 0.0001 | 230892.3108 | 4051.6193
February | 8456.0113 | 10.1373 | 15.7524 | 0 | 0.0001 | 207886.6531 | 3190.2782
March | 8970.809 | 10.913 | 17.7239 | 0 | 0.0001 | 233941.2169 | 3401.484
April | 6978.062 | 8.9371 | 16.6489 | 0 | 0.0001 | 219851.8866 | 2693.9007
May | 5422.7352 | 7.6263 | 17.2869 | 0 | 0.0001 | 228400.6114 | 2166.411
June | 4559.4071 | 6.8028 | 17.0293 | 0 | 0.0001 | 225050.5868 | 1863.3518
July | 4245.7302 | 6.6396 | 17.8037 | 0 | 0.0001 | 235319.7832 | 1767.7995
August | 4302.3512 | 6.7911 | 18.4432 | 0 | 0.0001 | 243778.9055 | 1798.1193
September | 4780.6984 | 7.0487 | 17.3178 | 0 | 0.0001 | 228852.8917 | 1944.7642
October | 6271.7369 | 8.3863 | 17.2229 | 0 | 0.0001 | 227495.0344 | 2459.1174
November | 8822.2764 | 10.6401 | 16.8413 | 0 | 0.0001 | 222272.1842 | 3335.2832
December | 10911.8303 | 12.6392 | 17.5039 | 0 | 0.0001 | 230898.3832 | 4069.4482
Annual Sum or Average | 84581.9892 | 109.1539 | 207.0775 | 0 | 0.0009 | 2734640 | 32741.5767
Minimum of Months | 4245.7302 | 6.6396 | 15.7524 | 0 | 0.0001 | 207886.6531 | 1767.7995
Maximum of Months | 10911.8303 | 12.6392 | 18.4432 | 0 | 0.0001 | 243778.9055 | 4069.4482
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 81357400000 | 59271.454 | 31-JAN-17:00 | 34382.155 | 10771.038 | 10280.723 | 823.538 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 73251100000 | 59219.015 | 11-FEB-17:00 | 34382.155 | 10771.038 | 10280.723 | 771.099 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 82431700000 | 59048.293 | 06-MAR-17:00 | 34382.155 | 10771.038 | 10280.723 | 600.377 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 77467200000 | 58237.912 | 29-APR-15:30 | 34382.155 | 10771.038 | 10274.34 | 0 | 2810.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 80479400000 | 64922.175 | 05-MAY-15:00 | 34382.155 | 10771.038 | 10274.34 | 0 | 9494.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 79299000000 | 69054.821 | 28-JUN-14:00 | 34382.155 | 10771.038 | 10274.34 | 0 | 13627.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 82917500000 | 75794.646 | 24-JUL-14:00 | 34382.155 | 10771.038 | 10274.34 | 0 | 20367.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 85898100000 | 73294.67 | 07-AUG-14:00 | 34382.155 | 10771.038 | 10274.34 | 0 | 17867.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 80638800000 | 82829.345 | 02-SEP-15:00 | 34382.155 | 10771.038 | 10274.34 | 0 | 27401.812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 80160300000 | 58863.477 | 30-OCT-16:00 | 34382.155 | 10771.038 | 10280.723 | 415.561 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 78320000000 | 59178.855 | 16-NOV-17:00 | 34382.155 | 10771.038 | 10280.723 | 730.939 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 81359500000 | 59331.436 | 13-DEC-17:00 | 34382.155 | 10771.038 | 10280.723 | 883.52 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 963580000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 73251100000 | 58237.912 |  | 34382.155 | 10771.038 | 10274.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 85898100000 | 82829.345 |  | 34382.155 | 10771.038 | 10280.723 | 883.52 | 27401.812 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20129.05 | 6188.13 | 0 | 26317.18
Cost per Total Building Area ($/m2) | 8.77 | 2.7 | 0 | 11.47
Cost per Net Conditioned Building Area ($/m2) | 8.77 | 2.7 | 0 | 11.47

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2119.34 | 923.86 | 923.86
Net Site Energy | 2119.34 | 923.86 | 923.86
Total Source Energy | 5043.21 | 2198.44 | 2198.44
Net Source Energy | 5043.21 | 2198.44 | 2198.44
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 7.35 | 1007.32 | 0 | 0 | 0 | 0
Cooling | 94.78 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 263.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1112.02 | 1007.32 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.385 | 0.305 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35683.74 | 24125.18 | 11558.56 | 0.68 | 3.44
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 136330.69 | 92170.89 | 44159.8 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22212.02 | 15489.43 | 6722.59 | 0.7 | 3.49
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16484.87 | 11145.14 | 5339.73 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2627.46 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46333.2 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 175324.68 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26058.36 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26059.08 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 10.69 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.44 | 1637 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.49 | 10299.25 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1107.38 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.66 | 770 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42294.7584 | 65.8155 | 164.5772 | 0 | 0.0005 | 37873.0038 | 17260.341
February | 36363.4016 | 57.6636 | 147.9597 | 0 | 0.0005 | 34050.9045 | 14942.8477
March | 37946.9325 | 62.0656 | 165.7384 | 0 | 0.0005 | 38145.7268 | 15774.3595
April | 31698.1495 | 54.7122 | 155.6331 | 0 | 0.0005 | 35824.6066 | 13450.8901
May | 31772.7161 | 57.0729 | 169.3792 | 0 | 0.0005 | 38992.0056 | 13695.9313
June | 35488.7314 | 64.589 | 194.2315 | 0 | 0.0006 | 44714.2445 | 15378.1751
July | 39491.4817 | 71.9094 | 216.3509 | 0 | 0.0007 | 49806.425 | 17116.0531
August | 38566.2669 | 70.2197 | 211.252 | 0 | 0.0006 | 48632.5981 | 16714.5735
September | 31863.9924 | 57.8421 | 173.4943 | 0 | 0.0005 | 39940.1198 | 13793.1476
October | 31702.1299 | 55.8557 | 162.4662 | 0 | 0.0005 | 37399.1277 | 13561.2487
November | 34551.3161 | 57.526 | 156.9872 | 0 | 0.0005 | 36133.2417 | 14459.7829
December | 40717.8692 | 64.2718 | 163.8976 | 0 | 0.0005 | 37718.2827 | 16703.8432
Annual Sum or Average | 432457.7458 | 739.5436 | 2081.9672 | 0 | 0.0064 | 479230.2867 | 182851.1939
Minimum of Months | 31698.1495 | 54.7122 | 147.9597 | 0 | 0.0005 | 34050.9045 | 13450.8901
Maximum of Months | 42294.7584 | 71.9094 | 216.3509 | 0 | 0.0007 | 49806.425 | 17260.341
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 87881500000 | 63561.34 | 26-JAN-17:00 | 34382.155 | 10771.038 | 13824.33 | 1569.816 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 79012600000 | 63115.452 | 03-FEB-17:00 | 34382.155 | 10771.038 | 13824.33 | 1123.929 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 88514300000 | 62855.717 | 03-MAR-17:00 | 34382.155 | 10771.038 | 13824.33 | 864.193 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 83128300000 | 63327.08 | 07-APR-14:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 4360.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 90478000000 | 85308.553 | 30-MAY-15:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 26341.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 103756000000 | 103804.635 | 08-JUN-12:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 44837.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 115572000000 | 107192.62 | 13-JUL-14:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 48225.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 112848000000 | 106135.033 | 04-AUG-15:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 47168.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 92678000000 | 89379.923 | 05-SEP-14:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 30413.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 86781900000 | 72248.521 | 31-OCT-14:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 13281.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 83844500000 | 70249.632 | 02-NOV-14:00 | 34382.155 | 10771.038 | 13813.639 | 0 | 11282.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 87522400000 | 63147.883 | 14-DEC-17:00 | 34382.155 | 10771.038 | 13824.33 | 1156.36 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1112020000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 79012600000 | 62855.717 |  | 34382.155 | 10771.038 | 13813.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 115572000000 | 107192.62 |  | 34382.155 | 10771.038 | 13824.33 | 1569.816 | 48225.788 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16158.44 | 8359.1 | 0 | 24517.54
Cost per Total Building Area ($/m2) | 7.04 | 3.64 | 0 | 10.69
Cost per Net Conditioned Building Area ($/m2) | 7.04 | 3.64 | 0 | 10.69

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1791.86 | 781.11 | 781.11
Net Site Energy | 1791.86 | 781.11 | 781.11
Total Source Energy | 4241.77 | 1849.08 | 1849.08
Net Source Energy | 4241.77 | 1849.08 | 1849.08
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 5.05 | 765.33 | 0 | 0 | 0 | 0
Cooling | 52.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 222.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1026.53 | 765.33 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.698 | 0.78 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.385 | 0.305 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26503.64 | 20715.04 | 5788.6 | 0.78 | 3.72
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 80620.17 | 60838.45 | 19781.72 | 0.75 | 3.91
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13536.53 | 10811.02 | 2725.51 | 0.8 | 4.04
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12614.16 | 9667.38 | 2946.78 | 0.77 | 3.93
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2269.32 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40030.46 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 144231.89 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22022.06 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22020.69 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.53 | 1739.3 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.29 | 8177.31 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.82 | 948.5 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 806.31 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29956.2371 | 45.8831 | 101.2963 | 0 | 0.0004 | 105290.3192 | 12201.3471
February | 26204.4253 | 40.6665 | 91.4777 | 0 | 0.0004 | 95089.1869 | 10725.1909
March | 27533.0119 | 43.9812 | 102.8972 | 0 | 0.0004 | 106969.8716 | 11391.8656
April | 23862.7395 | 39.6265 | 97.3433 | 0 | 0.0004 | 101207.818 | 10021.2104
May | 23768.1137 | 40.4994 | 102.5325 | 0 | 0.0004 | 106610.3719 | 10082.5105
June | 23614.6405 | 41.1331 | 106.7157 | 0 | 0.0004 | 110966.006 | 10105.2169
July | 25907.3671 | 45.4545 | 118.851 | 0 | 0.0005 | 123586.7391 | 11118.4806
August | 26165.8794 | 45.8953 | 119.9683 | 0 | 0.0005 | 124748.4166 | 11228.1796
September | 23372.7094 | 40.4938 | 104.4433 | 0 | 0.0004 | 108601.6428 | 9980.3198
October | 24316.5515 | 40.7866 | 101.395 | 0 | 0.0004 | 105423.2811 | 10251.6686
November | 26197.5511 | 41.7274 | 97.2539 | 0 | 0.0004 | 101102.296 | 10827.4923
December | 30388.9176 | 46.2599 | 101.2119 | 0 | 0.0004 | 105200.1587 | 12349.5358
Annual Sum or Average | 311288.144 | 512.4073 | 1245.3859 | 0 | 0.0049 | 1294800 | 130283.0181
Minimum of Months | 23372.7094 | 39.6265 | 91.4777 | 0 | 0.0004 | 95089.1869 | 9980.3198
Maximum of Months | 30388.9176 | 46.2599 | 119.9683 | 0 | 0.0005 | 124748.4166 | 12349.5358
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 83475400000 | 60945.72 | 05-JAN-17:00 | 34382.155 | 10771.038 | 11682.414 | 1096.113 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 75387900000 | 61150.029 | 15-FEB-17:00 | 34382.155 | 10771.038 | 11682.414 | 1300.423 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 84807000000 | 62249.892 | 30-MAR-15:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 5425.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 80238800000 | 66957.231 | 25-APR-14:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 10132.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 84522000000 | 72906.695 | 23-MAY-15:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 16082.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 87975200000 | 80579.53 | 27-JUN-15:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 23754.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 97981100000 | 85594.513 | 17-JUL-15:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 28769.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 98902000000 | 85973.769 | 30-AUG-13:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 29149.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 86100700000 | 79454.372 | 02-SEP-14:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 22629.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 83580800000 | 70895.922 | 05-OCT-14:00 | 34382.155 | 10771.038 | 11671.415 | 0 | 14071.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 80155100000 | 60704.722 | 17-NOV-17:00 | 34382.155 | 10771.038 | 11682.414 | 855.115 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 83404000000 | 61204.608 | 11-DEC-17:00 | 34382.155 | 10771.038 | 11682.414 | 1355.002 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1026530000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 75387900000 | 60704.722 |  | 34382.155 | 10771.038 | 11671.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 98902000000 | 85973.769 |  | 34382.155 | 10771.038 | 11682.414 | 1355.002 | 29149.161 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10722.44 | 5282.11 | 0 | 16004.56
Cost per Total Building Area ($/m2) | 4.67 | 2.3 | 0 | 6.98
Cost per Net Conditioned Building Area ($/m2) | 4.67 | 2.3 | 0 | 6.98

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2429.75 | 1059.18 | 1059.18
Net Site Energy | 2429.75 | 1059.18 | 1059.18
Total Source Energy | 5234.38 | 2281.78 | 2281.78
Net Source Energy | 5234.38 | 2281.78 | 2281.78
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 9.37 | 1329.06 | 0 | 0 | 0 | 0
Cooling | 79.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.32 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 265.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1100.68 | 1329.06 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.385 | 0.305 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39355.62 | 26607.67 | 12747.94 | 0.68 | 3.44
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 133592.74 | 90319.81 | 43272.93 | 0.68 | 3.49
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21811.72 | 15212.69 | 6599.03 | 0.7 | 3.49
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18551.29 | 12542.22 | 6009.08 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2944.45 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 51081.76 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 199229.8 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29147.93 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29148.95 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.13 | 12.07 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.58 | 1805.45 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.38 | 10092.41 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.95 | 1087.88 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.75 | 866.52 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 36726.4855 | 51.2707 | 58.565 | 0 | 0.0005 | 38439.3505 | 14425.3413
February | 30334.0622 | 43.5754 | 52.3719 | 0 | 0.0004 | 34382.9906 | 12031.9757
March | 27919.9547 | 43.183 | 58.2182 | 0 | 0.0004 | 38240.8558 | 11368.3988
April | 21681.9489 | 36.4227 | 54.6141 | 0 | 0.0004 | 35888.731 | 9104.4564
May | 21009.2897 | 37.5587 | 60.2983 | 0 | 0.0004 | 39633.9544 | 9038.6033
June | 22285.4725 | 40.6145 | 66.4823 | 0 | 0.0005 | 43701.6576 | 9661.6548
July | 23973.7714 | 43.7404 | 71.6785 | 0 | 0.0005 | 47117.4822 | 10398.2854
August | 24321.7448 | 44.382 | 72.7408 | 0 | 0.0005 | 47815.8521 | 10549.8591
September | 19562.9558 | 35.2516 | 57.0543 | 0 | 0.0004 | 37502.725 | 8442.9896
October | 22276.6641 | 37.59 | 56.66 | 0 | 0.0004 | 37233.8731 | 9370.2655
November | 26498.6412 | 40.9794 | 55.2375 | 0 | 0.0004 | 36282.94 | 10789.1716
December | 33922.6822 | 48.5691 | 58.0422 | 0 | 0.0005 | 38104.577 | 13439.9717
Annual Sum or Average | 310513.673 | 503.1374 | 721.9632 | 0 | 0.0054 | 474344.9893 | 128620.9733
Minimum of Months | 19562.9558 | 35.2516 | 52.3719 | 0 | 0.0004 | 34382.9906 | 8442.9896
Maximum of Months | 36726.4855 | 51.2707 | 72.7408 | 0 | 0.0005 | 47815.8521 | 14425.3413
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 89195600000 | 63954.073 | 04-JAN-17:00 | 34382.155 | 10771.038 | 13864.334 | 1922.546 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 79783100000 | 63545.187 | 01-FEB-17:00 | 34382.155 | 10771.038 | 13864.334 | 1513.66 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 88735000000 | 63155.723 | 01-MAR-17:00 | 34382.155 | 10771.038 | 13864.334 | 1124.195 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 83277100000 | 62791.34 | 01-APR-16:00 | 34382.155 | 10771.038 | 13852.261 | 0 | 3785.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 91967600000 | 100594.973 | 27-MAY-14:00 | 34382.155 | 10771.038 | 13852.261 | 0 | 41589.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 101406000000 | 102795.305 | 29-JUN-14:00 | 34382.155 | 10771.038 | 13852.261 | 0 | 43789.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 109333000000 | 106987.922 | 15-JUL-14:00 | 34382.155 | 10771.038 | 13852.261 | 0 | 47982.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 110953000000 | 101700.406 | 25-AUG-15:00 | 34382.155 | 10771.038 | 13852.261 | 0 | 42694.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 87022200000 | 86169.076 | 14-SEP-14:00 | 34382.155 | 10771.038 | 13852.261 | 0 | 27163.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 86398400000 | 74211.935 | 07-OCT-14:00 | 34382.155 | 10771.038 | 13852.261 | 0 | 15206.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 84191800000 | 63229.266 | 27-NOV-17:00 | 34382.155 | 10771.038 | 13864.334 | 1197.738 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 88418800000 | 63743.569 | 30-DEC-17:00 | 34382.155 | 10771.038 | 13864.334 | 1712.041 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1100680000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 79783100000 | 62791.34 |  | 34382.155 | 10771.038 | 13852.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 110953000000 | 106987.922 |  | 34382.155 | 10771.038 | 13864.334 | 1922.546 | 47982.468 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18767.91 | 10450.37 | 0 | 29218.28
Cost per Total Building Area ($/m2) | 8.18 | 4.56 | 0 | 12.74
Cost per Net Conditioned Building Area ($/m2) | 8.18 | 4.56 | 0 | 12.74

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2168.76 | 945.41 | 945.41
Net Site Energy | 2168.76 | 945.41 | 945.41
Total Source Energy | 4758.4 | 2074.29 | 2074.29
Net Source Energy | 4758.4 | 2074.29 | 2074.29
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 8.35 | 1166.19 | 0 | 0 | 0 | 0
Cooling | 28.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 219.78 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1002.57 | 1166.19 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.591 | 0.648 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.385 | 0.305 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.385 | 0.305 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28998.09 | 23159.48 | 5838.61 | 0.8 | 3.77
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 66211.35 | 52684.81 | 13526.54 | 0.8 | 4.3
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13613.31 | 10872.34 | 2740.97 | 0.8 | 4.04
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13614.8 | 10873.53 | 2741.27 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2853.04 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 49365.45 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 188118.6 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27858.73 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27860.53 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.14 | 13.09 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.75 | 1995.61 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.97 | 7568.21 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.82 | 953.88 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.82 | 953.99 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 33056.2501 | 47.3537 | 62.8907 | 0 | 0.0005 | 1490380 | 13117.7748
February | 27900.7926 | 40.8961 | 56.4375 | 0 | 0.0004 | 1337670 | 11161.6042
March | 26597.6103 | 41.4809 | 62.8244 | 0 | 0.0004 | 1489600 | 10881.4426
April | 23093.9937 | 37.2296 | 58.9347 | 0 | 0.0004 | 1397600 | 9565.2959
May | 21623.9139 | 36.4834 | 61.0554 | 0 | 0.0004 | 1448170 | 9113.3595
June | 20827.8615 | 36.3318 | 63.1168 | 0 | 0.0004 | 1497250 | 8893.0414
July | 21557.1257 | 38.2059 | 67.5039 | 0 | 0.0005 | 1601410 | 9262.6132
August | 21630.1003 | 38.209 | 67.2758 | 0 | 0.0005 | 1595980 | 9281.7639
September | 20508.3021 | 35.3786 | 60.7171 | 0 | 0.0004 | 1440270 | 8718.3403
October | 23010.0702 | 37.7319 | 61.0266 | 0 | 0.0004 | 1447320 | 9592.172
November | 25833.6122 | 39.887 | 59.5644 | 0 | 0.0004 | 1412230 | 10529.9804
December | 31825.1095 | 46.1489 | 62.5697 | 0 | 0.0005 | 1482910 | 12683.2436
Annual Sum or Average | 297464.7419 | 475.3369 | 743.917 | 0 | 0.0053 | 17640800 | 122800.6317
Minimum of Months | 20508.3021 | 35.3786 | 56.4375 | 0 | 0.0004 | 1337670 | 8718.3403
Maximum of Months | 33056.2501 | 47.3537 | 67.5039 | 0 | 0.0005 | 1601410 | 13117.7748
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 84702100000 | 61272.675 | 06-JAN-17:00 | 34382.155 | 10771.038 | 11484.782 | 1620.701 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 76023000000 | 60957.144 | 23-FEB-17:00 | 34382.155 | 10771.038 | 11484.782 | 1305.17 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 84657400000 | 58142.955 | 30-MAR-14:50 | 34382.155 | 10771.038 | 11471.69 | 0 | 1518.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 79428900000 | 57646.096 | 04-APR-08:09 | 34382.155 | 10771.038 | 11484.782 | 1008.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 82302900000 | 65484.387 | 16-MAY-16:00 | 34382.155 | 10771.038 | 11471.69 | 0 | 8859.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 85092400000 | 80202.892 | 30-JUN-15:00 | 34382.155 | 10771.038 | 11471.69 | 0 | 23578.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 91012000000 | 80889.59 | 21-JUL-16:00 | 34382.155 | 10771.038 | 11471.69 | 0 | 24264.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 90703400000 | 77582.811 | 09-AUG-16:00 | 34382.155 | 10771.038 | 11471.69 | 0 | 20957.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 81853900000 | 72373.159 | 02-SEP-15:00 | 34382.155 | 10771.038 | 11471.69 | 0 | 15748.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 82254400000 | 62036.84 | 06-OCT-15:00 | 34382.155 | 10771.038 | 11471.69 | 0 | 5411.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 80260200000 | 60433.656 | 29-NOV-17:00 | 34382.155 | 10771.038 | 11484.782 | 781.682 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 84277100000 | 61322.539 | 11-DEC-17:00 | 34382.155 | 10771.038 | 11484.782 | 1670.564 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1002570000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 76023000000 | 57646.096 |  | 34382.155 | 10771.038 | 11471.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 91012000000 | 80889.59 |  | 34382.155 | 10771.038 | 11484.782 | 1670.564 | 24264.707 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 20880.44 | 9435.22 | 0 | 30315.66
Cost per Total Building Area ($/m2) | 9.1 | 4.11 | 0 | 13.22
Cost per Net Conditioned Building Area ($/m2) | 9.1 | 4.11 | 0 | 13.22

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2703.81 | 1178.65 | 1178.65
Net Site Energy | 2703.81 | 1178.65 | 1178.65
Total Source Energy | 5118.53 | 2231.27 | 2231.27
Net Source Energy | 5118.53 | 2231.27 | 2231.27
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 11.46 | 1780.16 | 0 | 0 | 0 | 0
Cooling | 20.11 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 47.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 145.7 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 923.65 | 1780.16 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.511 | 0.553 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 3.241 | 0.487 | 0.409 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.487 | 0.409 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 3.241 | 0.487 | 0.409 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41367.18 | 27967.66 | 13399.52 | 0.68 | 3.21
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 73154.13 | 52374.33 | 20779.81 | 0.72 | 3.19
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17215.87 | 12404.35 | 4811.52 | 0.72 | 3.78
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18661.4 | 12886.06 | 5775.34 | 0.69 | 3.69
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3078.93 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 52765.08 | 0.8
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 209348.36 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30382.28 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30382.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.14 | 12.89 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.67 | 1897.73 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.43 | 3745.73 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.82 | 949.94 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.8 | 923.01 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 35797.0086 | 48.3936 | 51.9395 | 0 | 0.0004 | 34079.7569 | 13909.278
February | 30703.6287 | 42.154 | 46.6531 | 0 | 0.0004 | 30616.0109 | 11991.9532
March | 29662.0512 | 42.7796 | 51.764 | 0 | 0.0004 | 33984.9463 | 11781.6358
April | 22880.3607 | 35.5271 | 48.1615 | 0 | 0.0004 | 31635.8111 | 9329.6479
May | 19935.114 | 33.3058 | 49.6201 | 0 | 0.0004 | 32606.2414 | 8353.5097
June | 17456.1094 | 31.1308 | 49.8534 | 0 | 0.0004 | 32768.2466 | 7502.7055
July | 18537.8577 | 33.6072 | 54.7246 | 0 | 0.0004 | 35972.173 | 8019.9517
August | 18788.0843 | 33.6791 | 54.2204 | 0 | 0.0004 | 35639.3112 | 8091.7202
September | 18532.3793 | 31.6768 | 48.4553 | 0 | 0.0004 | 31843.9903 | 7834.0169
October | 22104.8627 | 35.3457 | 49.8593 | 0 | 0.0004 | 32756.3693 | 9111.1903
November | 26813.266 | 39.3849 | 49.1168 | 0 | 0.0004 | 32251.5145 | 10718.3435
December | 34000.0981 | 46.6776 | 51.6547 | 0 | 0.0004 | 33898.3049 | 13279.2467
Annual Sum or Average | 295210.8208 | 453.6622 | 606.0228 | 0 | 0.0046 | 398052.6764 | 119923.1993
Minimum of Months | 17456.1094 | 31.1308 | 46.6531 | 0 | 0.0004 | 30616.0109 | 7502.7055
Maximum of Months | 35797.0086 | 48.3936 | 54.7246 | 0 | 0.0004 | 35972.173 | 13909.278
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 79079500000 | 57543.802 | 11-JAN-17:00 | 34382.155 | 10771.038 | 7529.308 | 1847.301 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 71042100000 | 57517.61 | 01-FEB-17:00 | 34382.155 | 10771.038 | 7529.308 | 1821.108 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 78859500000 | 56935.009 | 09-MAR-17:00 | 34382.155 | 10771.038 | 7529.308 | 1238.508 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 73408500000 | 54101.497 | 03-APR-08:09 | 34382.155 | 10771.038 | 7529.308 | 1418.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 75660300000 | 60888.841 | 31-MAY-15:00 | 34382.155 | 10771.038 | 7516.413 | 0 | 8219.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 76036200000 | 75223.249 | 14-JUN-14:00 | 34382.155 | 10771.038 | 7516.413 | 0 | 22553.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 83470700000 | 86085.376 | 08-JUL-15:00 | 34382.155 | 10771.038 | 7516.413 | 0 | 33415.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 82698300000 | 84285.148 | 12-AUG-14:00 | 34382.155 | 10771.038 | 7516.413 | 0 | 31615.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 73891600000 | 67732.834 | 07-SEP-14:00 | 34382.155 | 10771.038 | 7516.413 | 0 | 15063.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 76008700000 | 62241.676 | 07-OCT-14:00 | 34382.155 | 10771.038 | 7516.413 | 0 | 9572.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 74837200000 | 57179.126 | 24-NOV-17:00 | 34382.155 | 10771.038 | 7529.308 | 1482.625 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 78658500000 | 57447.622 | 30-DEC-17:00 | 34382.155 | 10771.038 | 7529.308 | 1751.121 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 923651000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 71042100000 | 54101.497 |  | 34382.155 | 10771.038 | 7516.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 83470700000 | 86085.376 |  | 34382.155 | 10771.038 | 7529.308 | 1847.301 | 33415.769 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15581.04 | 13986.11 | 0 | 29567.15
Cost per Total Building Area ($/m2) | 6.79 | 6.1 | 0 | 12.89
Cost per Net Conditioned Building Area ($/m2) | 6.79 | 6.1 | 0 | 12.89

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3789.03 | 1651.72 | 1651.72
Net Site Energy | 3789.03 | 1651.72 | 1651.72
Total Source Energy | 6669.7 | 2907.46 | 2907.46
Net Source Energy | 6669.7 | 2907.46 | 2907.46
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 18.52 | 2768.04 | 0 | 0 | 0 | 0
Cooling | 7.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 500.28 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 46.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 249.32 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1021 | 2768.04 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 8.61 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 18.29 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 11.84 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 18.29 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 16.6532 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.454 | 0.487 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 7.83 | 7.83 | 2.615 | 0.702 | 0.633 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 2.615 | 0.702 | 0.633 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-90.1-2004-NONRES-FIXED | 38.05 | 38.05 | 2.615 | 0.702 | 0.633 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33935.77 | 27102.98 | 6832.79 | 0.8 | 3.73
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70101.6 | 55987.01 | 14114.59 | 0.8 | 4.32
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17962.31 | 14345.7 | 3616.62 | 0.8 | 4.01
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15877.22 | 12680.43 | 3196.8 | 0.8 | 4.01
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3868.2 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 67922.49 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 277278.92 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38800.38 | 0.8
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38800.38 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.17 | 15.64 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.05 | 2242 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.23 | 8077.66 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1236.14 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.96 | 1092.65 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 45220.9563 | 47.2631 | 130.1194 | 0 | 0.0005 | 26087.8052 | 16607.1496
February | 38749.2847 | 40.6836 | 115.3562 | 0 | 0.0004 | 23129.2828 | 14258.8442
March | 34830.5959 | 37.59 | 125.0437 | 0 | 0.0005 | 25079.0728 | 12973.9233
April | 25571.4009 | 28.6971 | 114.8137 | 0 | 0.0004 | 23033.9459 | 9694.2581
May | 19420.2725 | 23.2238 | 117.1048 | 0 | 0.0004 | 23500.4712 | 7582.3308
June | 17093.7125 | 21.0356 | 115.5039 | 0 | 0.0004 | 23181.3283 | 6765.3802
July | 17070.2589 | 21.1524 | 118.3923 | 0 | 0.0004 | 23761.4953 | 6778.5095
August | 18310.0143 | 22.3914 | 120.7732 | 0 | 0.0004 | 24238.4204 | 7225.0764
September | 20519.4957 | 24.1278 | 115.1464 | 0 | 0.0004 | 23105.9867 | 7948.3442
October | 27867.2471 | 31.0696 | 120.8538 | 0 | 0.0004 | 24244.7289 | 10533.2318
November | 36927.5347 | 39.3542 | 122.1349 | 0 | 0.0005 | 24492.6739 | 13678.2351
December | 42545.1706 | 44.7901 | 129.1889 | 0 | 0.0005 | 25903.6692 | 15674.2701
Annual Sum or Average | 344125.9442 | 381.3787 | 1444.4313 | 0 | 0.0052 | 289758.8806 | 129719.5531
Minimum of Months | 17070.2589 | 21.0356 | 114.8137 | 0 | 0.0004 | 23033.9459 | 6765.3802
Maximum of Months | 45220.9563 | 47.2631 | 130.1194 | 0 | 0.0005 | 26087.8052 | 16607.1496
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 91923200000 | 64306.317 | 13-JAN-09:09 | 34382.155 | 10771.038 | 12664.094 | 3475.029 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 81498500000 | 64094.502 | 03-FEB-09:09 | 34382.155 | 10771.038 | 12664.094 | 3263.215 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 88368800000 | 61845.521 | 02-MAR-17:00 | 34382.155 | 10771.038 | 12664.094 | 1014.234 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 81162600000 | 59352.034 | 10-APR-08:09 | 34382.155 | 10771.038 | 12664.094 | 1534.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 82806500000 | 60732.02 | 24-MAY-14:00 | 34382.155 | 10771.038 | 12648.453 | 0 | 2930.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 81681900000 | 69013.185 | 20-JUN-15:00 | 34382.155 | 10771.038 | 12648.453 | 0 | 11211.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 83726200000 | 73177.807 | 29-JUL-15:00 | 34382.155 | 10771.038 | 12648.453 | 0 | 15376.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 85406700000 | 68805.352 | 15-AUG-15:00 | 34382.155 | 10771.038 | 12648.453 | 0 | 11003.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 81416400000 | 59680.617 | 09-SEP-15:09 | 34382.155 | 10771.038 | 12648.453 | 0 | 1878.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 85428900000 | 62699.171 | 27-OCT-08:09 | 34382.155 | 10771.038 | 12664.094 | 1867.883 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 86302600000 | 63297.245 | 02-NOV-08:09 | 34382.155 | 10771.038 | 12664.094 | 2465.958 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 91274400000 | 63964.386 | 29-DEC-09:09 | 34382.155 | 10771.038 | 12664.094 | 3133.098 | 0 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1021000000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 81162600000 | 59352.034 |  | 34382.155 | 10771.038 | 12648.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 91923200000 | 73177.807 |  | 34382.155 | 10771.038 | 12664.094 | 3475.029 | 15376.16 | 3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27445.81 | 11428.12 | 0 | 38873.93
Cost per Total Building Area ($/m2) | 11.96 | 4.98 | 0 | 16.95
Cost per Net Conditioned Building Area ($/m2) | 11.96 | 4.98 | 0 | 16.95

## Picture
DOE Commercial Building Benchmark - Retail
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400 | 16800 | 876000