## BuildingSummary
Building Summary Strip Mall new construction
|  | Value | Data Source
Program
| Building Name | Benchmark Strip Mall
| Available Fuel Types | gas, electricity
| Principal Building Activity | Strip Mall
Form
| Total Floor Area (m2) | 2090 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 4
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 10 stores
| Floor to Ceiling Height (m) | 5.1816
| Roof type | Insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1184.13
| Net Dimensions - Total Area (m2) | 1059.67
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | Insulation entirely above deck | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2090
| Net Dimensions - Total Area (m2) | 2090
| Roof to Skin Ratio | 0.64
Window
| Dimensions - Total Area (m2) | South: 124 East: 0.00 North: 0.00 West: 0.00 Total: 124
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2090
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.33 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
LGStore1 | Yes | 1 | 348.3864 | 1805.1988 | 5.1816 | 276.3 | 20.75 | 6.1938 | 56.2472 | 23.9948 | 4.304 | 0 | 0 | 3.8 | 0.6 | 422.7712 | 0 | 0.37663
SMStore1 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 23.9948 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore2 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 18.292 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore3 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 18.292 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore4 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 18.292 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
LGStore2 | Yes | 1 | 348.3864 | 1805.1988 | 5.1816 | 157.89 | 20.75 | 6.1938 | 56.2472 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 422.7712 | 0 | 0.30524
SMStore5 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore6 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore7 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 78.94 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.30523
SMStore8 | Yes | 1 | 174.1932 | 902.5994 | 5.1816 | 197.36 | 10.37 | 6.1938 | 28.1236 | 13.7728 | 4.304 | 0 | 0 | 3.8 | 0.6 | 211.3856 | 0 | 0.44802
Total Conditioned Zones |  |  | 2090.3185 | 10831.1928 |  | 1184.13 | 124.46 |  | 337.4831
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 80.8338 | 582.608 | 149.0862 | 600.2213 |  | 367.8693 | 60.7796 | 592.9458 | 13.2453 | 62.7627 | 601.4542 | 118.36 | 89.7707 | 9.3991 | 4.0338 | 0.78933
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 16.7982 | 17.2681 | 17.4244 | 16.8472 | 12.6127 | 14.9823 | 9.0434 | 16.1681 | 11.3968 | 10.4795 | 14.9664 | 11.4695 | 16.9358 | 12.8263 | 17.5966 | 14.9181
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 39.8329 | 40.5977 | 39.2808 | 40.0403 | 28.9115 | 32.558 | 20.986 | 38.1213 | 25.9874 | 23.2774 | 34.2777 | 23.1512 | 33.3934 | 21.301 | 28.7058 | 24.9597
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 19.3879 | 17.3676 | 17.3617 | 17.6984 | 14.3669 | 15.0456 | 10.1446 | 16.2435 | 12.1639 | 11.2067 | 16.1171 | 11.5565 | 15.9308 | 10.166 | 13.5187 | 10.2976
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 17.2224 | 15.237 | 15.7244 | 15.5051 | 12.5974 | 14.0357 | 9.2205 | 15.462 | 11.1714 | 10.2584 | 13.9858 | 10.5824 | 13.7848 | 9.1482 | 12.1887 | 10.2378
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 16.9068 | 14.9639 | 15.555 | 15.1994 | 12.495 | 13.9214 | 9.1158 | 15.3014 | 11.0642 | 10.1526 | 13.7002 | 10.4736 | 13.4935 | 9.0432 | 12.1854 | 10.2353
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 16.6613 | 16.1349 | 15.4699 | 14.9487 | 12.4434 | 13.8595 | 9.0526 | 15.2268 | 11.0042 | 10.093 | 13.4533 | 10.3568 | 13.2434 | 8.9824 | 12.2033 | 10.2485
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 27.4713 | 28.6436 | 27.3891 | 27.9602 | 22.6533 | 25.0039 | 15.9767 | 26.9014 | 19.8035 | 17.9841 | 25.3798 | 18.5285 | 24.7517 | 17.2784 | 24.0431 | 20.2348
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 14.7558 | 14.8935 | 14.1962 | 14.5565 | 11.6658 | 12.9439 | 8.2713 | 14.0058 | 10.192 | 9.2987 | 13.2033 | 9.5341 | 12.88 | 8.725 | 12.2036 | 10.2488
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 14.6843 | 14.8348 | 14.1475 | 14.4988 | 11.6303 | 12.9061 | 8.2416 | 13.9496 | 10.1598 | 9.2674 | 13.1472 | 9.5018 | 12.8245 | 8.7228 | 12.1913 | 10.2398
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 14.5904 | 14.9458 | 14.3022 | 14.6105 | 11.6747 | 13.0015 | 8.2815 | 14.0555 | 10.2105 | 9.3299 | 13.2292 | 9.5362 | 12.907 | 8.8072 | 12.2916 | 10.3192
Heating (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 10.251 | 14.5082 | 11.4175 | 17.5058 | 10.6614 | 13.9788 | 11.7844 | 20.7942 | 17.1283 | 16.0049 | 26.0809 | 21.7906 | 29.8251 | 28.3819 | 30.6953 | 40.4043
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 27.0653 | 22.8349 | 31.3739 | 21.3229 | 25.051 | 23.5688 | 37.3814 | 30.5906 | 28.6938 | 47.556 | 39.5577 | 54.403 | 51.652 | 56.3912 | 74.1424
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.8442 | 13.7282 | 14.0536 | 21.7534 | 18.0514 | 24.8909 | 23.6011 | 26.006 | 34.0881
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7716 | 13.6587 | 14.0536 | 21.6838 | 17.9842 | 24.8137 | 23.522 | 25.9375 | 34.0064
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.768 | 13.6553 | 14.0536 | 21.6806 | 17.9812 | 24.8102 | 23.5186 | 25.9346 | 34.003
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7793 | 13.6672 | 14.0536 | 21.6939 | 17.9947 | 24.8255 | 23.5348 | 25.9503 | 34.0211
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 27.0653 | 22.8349 | 29.1965 | 21.3229 | 24.6851 | 23.5688 | 33.3132 | 27.076 | 28.1072 | 43.1101 | 35.7055 | 49.3381 | 46.7382 | 51.581 | 67.6838
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7797 | 13.6676 | 14.0536 | 21.6943 | 17.995 | 24.8258 | 23.5352 | 25.9506 | 34.0214
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7746 | 13.6615 | 14.0536 | 21.6864 | 17.9866 | 24.8164 | 23.5248 | 25.9398 | 34.0092
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.8823 | 13.7629 | 14.0536 | 21.7828 | 18.0789 | 24.9227 | 23.6329 | 26.028 | 34.1177
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.72 | 3.69 | 3.9 | 3.65 | 3.9 | 3.85 | 3.65 | 3.87 | 3.65 | 4 | 3.65 | 4.01
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.21 | 3.21 | 3.45 | 3.21 | 3.55 | 3.54 | 3.7 | 3.44 | 3.77 | 3.67 | 3.44 | 3.74 | 3.44 | 3.77 | 3.46 | 3.77
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.65 | 3.65 | 3.65 | 3.68 | 3.71 | 3.93 | 3.65 | 3.96 | 3.86 | 3.65 | 3.94 | 3.65 | 4.04 | 3.65 | 4.04
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.72 | 3.68 | 3.91 | 3.65 | 3.92 | 3.83 | 3.65 | 3.9 | 3.65 | 4.02 | 3.65 | 4.04
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.72 | 3.68 | 3.91 | 3.65 | 3.92 | 3.83 | 3.65 | 3.9 | 3.65 | 4.01 | 3.65 | 4.04
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.72 | 3.67 | 3.91 | 3.65 | 3.92 | 3.83 | 3.65 | 3.9 | 3.65 | 4.01 | 3.65 | 4.04
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.44 | 3.44 | 3.47 | 3.44 | 3.88 | 3.44 | 3.63 | 3.8 | 3.44 | 3.84 | 3.44 | 3.96 | 3.44 | 3.77
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.7 | 3.65 | 3.89 | 3.65 | 3.89 | 3.81 | 3.65 | 3.87 | 3.65 | 3.99 | 3.65 | 4.04
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.69 | 3.65 | 3.89 | 3.65 | 3.89 | 3.81 | 3.65 | 3.87 | 3.65 | 3.99 | 3.65 | 4.04
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.7 | 3.66 | 3.89 | 3.65 | 3.89 | 3.81 | 3.65 | 3.87 | 3.65 | 3.99 | 3.65 | 4.04
Heating Efficiency (%)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 0.68 | 0.7 | 0.7 | 0.68 | 0.56 | 0.64 | 0.49 | 0.65 | 0.62 | 0.54 | 0.6 | 0.6 | 0.68 | 0.75 | 0.71 | 0.9
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 1.6 | 1.63 | 1.61 | 1.61 | 1.37 | 1.53 | 1.19 | 1.54 | 1.57 | 1.28 | 1.38 | 1.36 | 1.34 | 1.29 | 1.19 | 1.51
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 0.78 | 0.7 | 0.7 | 0.71 | 0.6 | 0.65 | 0.56 | 0.65 | 0.69 | 0.58 | 0.65 | 0.64 | 0.64 | 0.61 | 0.54 | 0.62
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 0.69 | 0.61 | 0.63 | 0.62 | 0.56 | 0.59 | 0.5 | 0.62 | 0.61 | 0.52 | 0.56 | 0.57 | 0.56 | 0.54 | 0.49 | 0.62
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 0.68 | 0.6 | 0.63 | 0.61 | 0.55 | 0.58 | 0.49 | 0.62 | 0.61 | 0.51 | 0.55 | 0.56 | 0.54 | 0.54 | 0.49 | 0.62
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 0.67 | 0.65 | 0.62 | 0.6 | 0.55 | 0.57 | 0.49 | 0.61 | 0.6 | 0.51 | 0.54 | 0.56 | 0.53 | 0.53 | 0.49 | 0.62
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.11 | 1.15 | 1.1 | 1.13 | 0.95 | 1.01 | 0.84 | 1.08 | 1.04 | 0.87 | 1.02 | 0.96 | 1 | 1 | 0.97 | 1.22
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 0.59 | 0.6 | 0.57 | 0.59 | 0.5 | 0.52 | 0.44 | 0.56 | 0.54 | 0.46 | 0.53 | 0.5 | 0.52 | 0.51 | 0.49 | 0.62
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 0.59 | 0.6 | 0.57 | 0.58 | 0.5 | 0.52 | 0.44 | 0.56 | 0.54 | 0.45 | 0.53 | 0.5 | 0.52 | 0.51 | 0.49 | 0.62
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 0.59 | 0.6 | 0.58 | 0.59 | 0.5 | 0.53 | 0.44 | 0.57 | 0.54 | 0.46 | 0.53 | 0.5 | 0.52 | 0.51 | 0.49 | 0.62
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.085737 | 0.12252 | 0.1057 | 0.10311 | 0.13207 | 0.099319 | 0.14995 | 0.077154 | 0.037652 | 0.075472 | 0.052869 | 0.037693 | 0.062155 | 0.075359 | 0.06094 | 0.097178
| Total Cost ($/m2) | 15.02 | 19.23 | 16.43 | 14.3 | 15.98 | 13.97 | 16.9 | 10.2 | 4.79 | 8.63 | 6.63 | 4.54 | 7.69 | 8.87 | 7.05 | 11.54
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011424 | 0.0080374 | 0.0081335 | 0.0095156 | 0.0086321 | 0.007634 | 0.0085555 | 0.0096546 | 0.0068796 | 0.0084117 | 0.0083157 | 0.0069174 | 0.0078597 | 0.0081233 | 0.0078582 | 0.0041297
| Total Cost ($/m2) | 0.05 | 0.79 | 0.71 | 1.99 | 0.6 | 1.11 | 1.68 | 3.57 | 1.83 | 3.16 | 4.25 | 2.67 | 5.32 | 4.78 | 6.64 | 5.57
Total Utility Costs
| Cost Intensity ($/m2) | 15.07 | 20.02 | 17.15 | 16.29 | 16.58 | 15.07 | 18.59 | 13.77 | 6.62 | 11.78 | 10.88 | 7.21 | 13.01 | 13.65 | 13.69 | 17.11
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 121147.2222 | 84047.2222 | 81752.7778 | 46450 | 16225 | 54227.7778 | 3441.6667 | 34394.4444 | 24738.8889 | 5002.7778 | 23650 | 14211.1111 | 20022.2222 | 7941.6667 | 5855.5556 | 1722.2222
| Interior Lighting | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725
| Exterior Lighting | 22155.5556 | 22147.2222 | 22144.4444 | 22141.6667 | 22125 | 22119.4444 | 22130.5556 | 22116.6667 | 22125 | 22080.5556 | 22119.4444 | 22108.3333 | 22105.5556 | 22100 | 22088.8889 | 21952.7778
| Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 48594.4444 | 47747.2222 | 46908.3333 | 47030.5556 | 40355.5556 | 43394.4444 | 35880.5556 | 45552.7778 | 44872.2222 | 37647.2222 | 42241.6667 | 41219.4444 | 42294.4444 | 41794.4444 | 39541.6667 | 50444.4444
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 366100 | 328147.2222 | 325008.3333 | 289822.2222 | 252905.5556 | 293944.4444 | 235655.5556 | 276266.6667 | 265938.8889 | 238933.3333 | 262213.8889 | 251741.6667 | 258625 | 246038.8889 | 241688.8889 | 248322.2222
Gas (MJ)
| Heating | 9650 | 205640 | 182980 | 437980 | 144360 | 303340 | 411160 | 773910 | 554560 | 784670 | 1068000 | 807800 | 1414040 | 1230450 | 1766090 | 2817030
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 9650 | 205640 | 182980 | 437980 | 144360 | 303340 | 411160 | 773910 | 554560 | 784670 | 1068000 | 807800 | 1414040 | 1230450 | 1766090 | 2817030
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1327610 | 1386970 | 1353010 | 1481340 | 1054820 | 1361540 | 1259510 | 1768480 | 1511950 | 1644830 | 2011970 | 1714070 | 2345090 | 2116190 | 2636170 | 3710990
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 208.6427 | 144.7482 | 140.7966 | 79.9973 | 27.9431 | 93.3924 | 5.9273 | 59.2349 | 42.6059 | 8.6159 | 40.7306 | 24.4747 | 34.4828 | 13.6773 | 10.0846 | 2.9661
| Interior Lighting (elec) | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822
| Exterior Lighting (elec) | 38.1568 | 38.1425 | 38.1377 | 38.1329 | 38.1042 | 38.0946 | 38.1138 | 38.0899 | 38.1042 | 38.0277 | 38.0946 | 38.0755 | 38.0707 | 38.0612 | 38.042 | 37.8076
| Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 83.6905 | 82.2314 | 80.7867 | 80.9972 | 69.5013 | 74.735 | 61.7944 | 78.4521 | 77.28 | 64.837 | 72.7496 | 70.9891 | 72.8405 | 71.9794 | 68.0996 | 86.8767
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 630.5063 | 565.1431 | 559.7373 | 499.1389 | 435.5601 | 506.2383 | 405.8517 | 475.7932 | 458.0064 | 411.4968 | 451.5911 | 433.5556 | 445.4103 | 423.7342 | 416.2425 | 427.6666
Gas (MJ/m2)
| Heating (gas) | 4.6165 | 98.3773 | 87.5368 | 209.5277 | 69.0612 | 145.1165 | 196.6972 | 370.2352 | 265.2991 | 375.3827 | 510.9266 | 386.448 | 676.4706 | 588.6419 | 844.8898 | 1347.6549
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4.6165 | 98.3773 | 87.5368 | 209.5277 | 69.0612 | 145.1165 | 196.6972 | 370.2352 | 265.2991 | 375.3827 | 510.9266 | 386.448 | 676.4706 | 588.6419 | 844.8898 | 1347.6549
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 635.1229 | 663.5204 | 647.2741 | 708.6666 | 504.6213 | 651.3548 | 602.5441 | 846.0331 | 723.3103 | 786.8795 | 962.5177 | 820.0036 | 1121.8809 | 1012.3761 | 1261.1323 | 1775.3215
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 83.529 | 74.7669 | 63.6557 | 55.3754 | 62.8882 | 54.2159 | 52.7946 | 54.6037 | 54.4829 | 53.1284 | 53.9554 | 53.7674 | 53.8953 | 53.8272 | 53.329 | 55.1662
| Feb | 87.6763 | 75.52 | 67.5023 | 58.2815 | 59.3707 | 55.0588 | 55.8893 | 54.6037 | 54.9778 | 53.1284 | 53.9554 | 53.7674 | 53.8953 | 53.8272 | 53.329 | 55.1662
| Mar | 89.4473 | 78.9255 | 80.2376 | 63.5942 | 59.6992 | 60.2851 | 52.7946 | 62.9879 | 54.9074 | 53.1284 | 53.9554 | 55.1598 | 53.8953 | 51.0575 | 53.329 | 55.1662
| Apr | 93.6436 | 92.4234 | 84.1461 | 77.0367 | 66.7466 | 77.8585 | 58.2164 | 63.5488 | 65.9238 | 54.3484 | 55.6579 | 59.336 | 53.8089 | 48.9977 | 48.26 | 50.0972
| May | 99.8225 | 99.0268 | 97.9355 | 86.1694 | 63.1606 | 86.9233 | 59.2107 | 77.6105 | 71.7104 | 59.0835 | 73.9919 | 65.0304 | 88.6056 | 58.6769 | 57.207 | 53.673
| Jun | 103.158 | 100.0484 | 109.9042 | 93.9884 | 65.8007 | 100.3275 | 59.9521 | 97.7765 | 80.3135 | 63.4458 | 91.3471 | 72.8419 | 89.5613 | 73.965 | 71.8966 | 63.0836
| Jul | 100.9173 | 103.4567 | 108.9281 | 102.5432 | 72.205 | 99.6657 | 66.3862 | 100.7667 | 82.7614 | 71.0359 | 93.758 | 77.7803 | 93.6509 | 74.6222 | 82.0538 | 67.5758
| Aug | 103.5691 | 103.4929 | 109.4283 | 97.2252 | 78.4792 | 97.4615 | 63.5192 | 100.7425 | 82.0786 | 68.135 | 93.3489 | 78.6636 | 89.6749 | 71.1219 | 81.6221 | 62.7077
| Sep | 99.866 | 102.3485 | 103.078 | 90.8187 | 77.4289 | 95.4196 | 74.852 | 87.4533 | 73.6824 | 78.7693 | 78.2536 | 72.0251 | 75.3764 | 66.1989 | 65.8026 | 50.0972
| Oct | 98.5763 | 91.0518 | 85.5499 | 81.1507 | 69.5805 | 79.033 | 60.0588 | 74.462 | 64.3662 | 54.1516 | 62.3726 | 64.4229 | 65.2606 | 55.6869 | 61.142 | 55.1662
| Nov | 90.7949 | 80.6188 | 76.1751 | 59.6475 | 64.2246 | 58.8867 | 52.7946 | 66.9282 | 55.1106 | 53.1284 | 60.6893 | 53.7674 | 53.8953 | 53.8272 | 53.329 | 55.1662
| Dec | 83.96 | 76.7517 | 62.7403 | 54.9016 | 63.7908 | 55.6902 | 52.7946 | 54.6037 | 54.4829 | 53.1284 | 53.9554 | 53.7674 | 53.8953 | 53.8272 | 53.329 | 55.1662
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-13:00 | 28-JAN-14:00 | 23-JAN-17:00 | 26-JAN-13:00 | 02-JAN-16:40 | 02-JAN-16:00 | 02-JAN-16:49 | 02-JAN-17:10 | 02-JAN-17:19 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 25-FEB-13:39 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-15:00 | 13-FEB-11:00 | 08-FEB-17:10 | 15-FEB-15:00 | 01-FEB-17:30 | 14-FEB-17:49 | 01-FEB-17:10 | 01-FEB-16:00 | 01-FEB-17:19 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 01-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-12:30 | 17-MAR-14:00 | 28-MAR-15:00 | 31-MAR-14:09 | 31-MAR-15:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-15:09 | 01-MAR-17:49 | 01-MAR-17:40 | 30-MAR-15:00 | 01-MAR-17:00 | 30-MAR-15:00 | 01-MAR-17:49 | 01-MAR-17:00
| Apr | 01-APR-15:39 | 29-APR-14:39 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-14:09 | 29-APR-15:09 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 01-APR-09:09 | 01-APR-09:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:00 | 15-MAY-14:00 | 30-MAY-14:09 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 06-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-14:00 | 29-JUN-14:00 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 20-JUN-15:00
| Jul | 13-JUL-14:00 | 01-JUL-15:00 | 11-JUL-15:00 | 03-JUL-14:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:50 | 29-JUL-15:00
| Aug | 21-AUG-14:00 | 31-AUG-14:09 | 01-AUG-16:00 | 17-AUG-14:39 | 08-AUG-14:00 | 04-AUG-14:00 | 26-AUG-12:00 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-14:50
| Sep | 11-SEP-14:00 | 15-SEP-14:00 | 09-SEP-15:30 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:30 | 02-SEP-15:20 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 01-SEP-08:09
| Oct | 06-OCT-14:39 | 06-OCT-15:00 | 14-OCT-13:00 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-14:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 23-OCT-08:09
| Nov | 07-NOV-15:09 | 03-NOV-14:30 | 13-NOV-15:30 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-16:40 | 06-NOV-17:10 | 04-NOV-13:00 | 08-NOV-17:10 | 01-NOV-16:49 | 02-NOV-14:00 | 01-NOV-16:00 | 01-NOV-16:00 | 06-NOV-17:10 | 01-NOV-16:49 | 01-NOV-08:09
| Dec | 15-DEC-15:30 | 02-DEC-12:00 | 09-DEC-15:30 | 01-DEC-17:30 | 19-DEC-12:00 | 05-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 4382.22 | 4515.14 | 3900.61 | 3988.14 | 2975.52 | 4116.42 | 3074.65 | 4401.66 | 3782.18 | 2355.26 | 4513.57 | 3889.13 | 4744.14 | 4422.48 | 4919.03 | 6269.43
| Total Source Energy (MJ/m2) | 2096.44 | 2160.02 | 1866.04 | 1907.91 | 1423.48 | 1969.28 | 1470.9 | 2105.74 | 1809.38 | 1126.75 | 2159.27 | 1860.54 | 2269.58 | 2115.69 | 2353.24 | 2999.27
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 100577.0099 | 113164.9779 | 101411.5026 | 97173.81 | 32159.3289 | 104609.787 | 34954.2829 | 88507.8699 | 118636.1803 | 31552.2056 | 159057.7782 | 117403.0519 | 114024.1629 | 112099.9431 | 114575.5895 | 120673.5252
| CO2 (kg) | 232991.2898 | 285372.1612 | 240262.8108 | 225439.1812 | 86431.0345 | 250617.7267 | 94948.4505 | 207506.5435 | 282024.9345 | 82220.5379 | 378196.6754 | 281704.7942 | 277756.8947 | 273229.1015 | 282734.3129 | 321804.8852
| NOX (kg) | 410.4745 | 370.74 | 398.6253 | 411.9764 | 74.3573 | 399.4255 | 82.3704 | 370.8779 | 470.3611 | 103.5364 | 637.8532 | 458.6286 | 439.3026 | 429.4129 | 431.5672 | 352.5342
| SO2 (kg) | 1567.0598 | 1565.3117 | 1306.97 | 1017.3935 | 735.9658 | 1617.0041 | 685.8379 | 1008.6915 | 1161.4549 | 184.8867 | 1767.3938 | 1099.5243 | 610.7727 | 657.2814 | 570.8964 | 1264.8167
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0071 | 0.0044 | 0.0036 | 0.0038 | 0.0003 | 0.0031 | 0.0004 | 0.0041 | 0.0046 | 0.0008 | 0.0054 | 0.0044 | 0.0046 | 0.0047 | 0.0044 | 0.0046
| Water for Electricity (m3) | 193.9448 | 533.9321 | 9654.16 | 1809.53 | 4440.47 | 8064.04 | 4137.57 | 62.7229 | 1207.58 | 2441.13 | 406.8082 | 1143.11 | 401.2395 | 15585.1 | 374.965 | 253.7063

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1327.61 | 635.12 | 635.12
Net Site Energy | 1327.61 | 635.12 | 635.12
Total Source Energy | 4382.22 | 2096.44 | 2096.44
Net Source Energy | 4382.22 | 2096.44 | 2096.44
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9.65 | 0 | 0 | 0 | 0
Cooling | 436.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 174.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1317.96 | 9.65 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16798.17 | 11356.96 | 5441.21 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39832.85 | 26930.32 | 12902.53 | 0.68 | 3.21
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19387.93 | 13107.85 | 6280.08 | 0.68 | 3.45
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17222.42 | 11643.79 | 5578.63 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16906.79 | 11430.4 | 5476.39 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16661.32 | 11264.44 | 5396.88 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27471.31 | 18572.89 | 8898.42 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14755.77 | 9976.13 | 4779.64 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14684.33 | 9927.83 | 4756.5 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14590.36 | 9864.3 | 4726.06 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20501.92 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20501.92 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 784.63 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.6 | 1827.35 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.78 | 905.6 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 804.45 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 789.71 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.67 | 778.24 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1260.26 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 689.23 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 685.9 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 681.51 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16873.4329 | 29.5511 | 112.1037 | 0 | 0.0005 | 13874.2095 | 7266.2536
February | 15487.5501 | 27.2353 | 103.7731 | 0 | 0.0005 | 12843.2772 | 6680.6107
March | 17795.7238 | 31.2909 | 119.2121 | 0 | 0.0005 | 14754.059 | 7675.9101
April | 18494.0433 | 32.6118 | 124.622 | 0 | 0.0006 | 15423.6681 | 7986.4366
May | 20821.8685 | 36.7216 | 140.3469 | 0 | 0.0006 | 17369.8529 | 8992.1766
June | 21544.8815 | 37.9967 | 145.2203 | 0 | 0.0007 | 17972.9991 | 9304.4186
July | 22672.8487 | 39.986 | 152.8232 | 0 | 0.0007 | 18913.9629 | 9791.5449
August | 23008.728 | 40.5783 | 155.0872 | 0 | 0.0007 | 19194.1574 | 9936.5984
September | 21325.7905 | 37.6103 | 143.7436 | 0 | 0.0007 | 17790.2307 | 9209.8015
October | 20286.0064 | 35.7765 | 136.735 | 0 | 0.0006 | 16922.8303 | 8760.758
November | 17979.4311 | 31.707 | 121.1755 | 0 | 0.0006 | 14997.1222 | 7764.4777
December | 16700.985 | 29.409 | 112.2172 | 0 | 0.0005 | 13888.3826 | 7208.0232
Annual Sum or Average | 232991.2898 | 410.4745 | 1567.0598 | 0 | 0.0071 | 193944.7521 | 100577.0099
Minimum of Months | 15487.5501 | 27.2353 | 103.7731 | 0 | 0.0005 | 12843.2772 | 6680.6107
Maximum of Months | 23008.728 | 40.5783 | 155.0872 | 0 | 0.0007 | 19194.1574 | 9936.5984
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 94283000000 | 83529.021 | 06-JAN-13:00 | 32837.857 | 8089.532 | 9206.87 | 0 | 33394.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 87277200000 | 87676.268 | 25-FEB-13:39 | 32837.857 | 8089.532 | 9206.87 | 0 | 37542.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 100262000000 | 89447.281 | 13-MAR-14:00 | 32837.857 | 8089.532 | 9206.87 | 0 | 39313.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 104812000000 | 93643.643 | 01-APR-15:39 | 32837.857 | 8089.532 | 9206.87 | 0 | 43509.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 118038000000 | 99822.471 | 24-MAY-14:00 | 32837.857 | 8089.532 | 9206.87 | 0 | 49688.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 122137000000 | 103157.958 | 27-JUN-14:00 | 32837.857 | 8089.532 | 9206.87 | 0 | 53023.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 128531000000 | 100917.328 | 13-JUL-14:00 | 32837.857 | 8089.532 | 9206.87 | 0 | 50783.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 130435000000 | 103569.115 | 21-AUG-14:00 | 32837.857 | 8089.532 | 9206.87 | 0 | 53434.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 120895000000 | 99866.023 | 11-SEP-14:00 | 32837.857 | 8089.532 | 9206.87 | 0 | 49731.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 115000000000 | 98576.332 | 06-OCT-14:39 | 32837.857 | 8089.532 | 9206.87 | 0 | 48442.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 101914000000 | 90794.935 | 07-NOV-15:09 | 32837.857 | 8089.532 | 9206.87 | 0 | 40660.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 94379300000 | 83959.966 | 15-DEC-15:30 | 32837.857 | 8089.532 | 9206.87 | 0 | 33825.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1317960000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 87277200000 | 83529.021 |  | 32837.857 | 8089.532 | 9206.87 | 0 | 33394.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 130435000000 | 103569.115 |  | 32837.857 | 8089.532 | 9206.87 | 0 | 53434.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 31388.28 | 110.24 | 0 | 31498.52
Cost per Total Building Area ($/m2) | 15.02 | 0.05 | 0 | 15.07
Cost per Net Conditioned Building Area ($/m2) | 15.02 | 0.05 | 0 | 15.07

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1386.97 | 663.52 | 663.52
Net Site Energy | 1386.97 | 663.52 | 663.52
Total Source Energy | 4515.14 | 2160.02 | 2160.02
Net Source Energy | 4515.14 | 2160.02 | 2160.02
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 205.64 | 0 | 0 | 0 | 0
Cooling | 302.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 171.89 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1181.33 | 205.64 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17268.08 | 11674.66 | 5593.42 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40597.68 | 27447.41 | 13150.27 | 0.68 | 3.21
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17367.61 | 11741.95 | 5625.66 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15237.02 | 10301.49 | 4935.52 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14963.9 | 10116.84 | 4847.06 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16134.9 | 10908.54 | 5226.36 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28643.56 | 19365.43 | 9278.13 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14893.47 | 10069.23 | 4824.25 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14834.82 | 10029.58 | 4805.25 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14945.75 | 10104.57 | 4841.18 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14508.23 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27065.35 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13532.67 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13532.67 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13532.67 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13532.67 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27065.35 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13532.67 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13532.67 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13532.67 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 806.58 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.63 | 1862.43 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 811.23 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 711.71 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 698.96 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 753.65 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1314.03 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 695.67 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 692.93 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 698.11 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 21251.1476 | 26.7151 | 104.0563 | 0 | 0.0003 | 35489.8655 | 8312.059
February | 19355.6714 | 24.2404 | 93.4878 | 0 | 0.0003 | 31884.8693 | 7558.8252
March | 20366.9029 | 26.322 | 109.7886 | 0 | 0.0003 | 37448.5573 | 8058.8052
April | 21100.8075 | 27.6607 | 119.2107 | 0 | 0.0003 | 40664.2069 | 8399.5036
May | 25248.1926 | 33.1751 | 143.7287 | 0 | 0.0004 | 49027.9153 | 10060.4384
June | 27988.0815 | 36.7878 | 159.502 | 0 | 0.0004 | 54408.4693 | 11153.8002
July | 29880.709 | 39.2755 | 170.2879 | 0 | 0.0005 | 58087.7127 | 11908.0495
August | 29822.1419 | 39.1985 | 169.9541 | 0 | 0.0005 | 57973.8591 | 11884.7094
September | 26171.0091 | 34.3994 | 149.1466 | 0 | 0.0004 | 50876.1041 | 10429.6612
October | 23514.1367 | 30.8587 | 133.3262 | 0 | 0.0004 | 45479.3028 | 9364.5949
November | 19898.6367 | 25.9037 | 109.8823 | 0 | 0.0003 | 37481.3929 | 7897.6153
December | 20774.7242 | 26.2031 | 102.9407 | 0 | 0.0003 | 35109.8154 | 8136.9159
Annual Sum or Average | 285372.1612 | 370.74 | 1565.3117 | 0 | 0.0044 | 533932.0705 | 113164.9779
Minimum of Months | 19355.6714 | 24.2404 | 93.4878 | 0 | 0.0003 | 31884.8693 | 7558.8252
Maximum of Months | 29880.709 | 39.2755 | 170.2879 | 0 | 0.0005 | 58087.7127 | 11908.0495
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 78521400000 | 74766.869 | 03-JAN-13:00 | 32837.857 | 8089.532 | 9045.3 | 0 | 24794.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 70545300000 | 75520.018 | 23-FEB-15:09 | 32837.857 | 8089.532 | 9045.3 | 0 | 25547.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 82855000000 | 78925.458 | 25-MAR-12:30 | 32837.857 | 8089.532 | 9045.3 | 0 | 28952.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 89969600000 | 92423.411 | 29-APR-14:39 | 32837.857 | 8089.532 | 9045.3 | 0 | 42450.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 108474000000 | 99026.751 | 26-MAY-14:00 | 32837.857 | 8089.532 | 9045.3 | 0 | 49054.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 120379000000 | 100048.354 | 13-JUN-14:00 | 32837.857 | 8089.532 | 9045.3 | 0 | 50075.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 128519000000 | 103456.721 | 01-JUL-15:00 | 32837.857 | 8089.532 | 9045.3 | 0 | 53484.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 128267000000 | 103492.854 | 31-AUG-14:09 | 32837.857 | 8089.532 | 9045.3 | 0 | 53520.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 112563000000 | 102348.465 | 15-SEP-14:00 | 32837.857 | 8089.532 | 9045.3 | 0 | 52375.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 100623000000 | 91051.787 | 06-OCT-15:00 | 32837.857 | 8089.532 | 9045.3 | 0 | 41079.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 82927700000 | 80618.783 | 03-NOV-14:30 | 32837.857 | 8089.532 | 9045.3 | 0 | 30646.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 77680500000 | 76751.714 | 02-DEC-12:00 | 32837.857 | 8089.532 | 9045.3 | 0 | 26779.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1181330000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 70545300000 | 74766.869 |  | 32837.857 | 8089.532 | 9045.3 | 0 | 24794.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 128519000000 | 103492.854 |  | 32837.857 | 8089.532 | 9045.3 | 0 | 53520.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40204.45 | 1652.82 | 0 | 41857.27
Cost per Total Building Area ($/m2) | 19.23 | 0.79 | 0 | 20.02
Cost per Net Conditioned Building Area ($/m2) | 19.23 | 0.79 | 0 | 20.02

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1353.01 | 647.27 | 647.27
Net Site Energy | 1353.01 | 647.27 | 647.27
Total Source Energy | 3900.61 | 1866.04 | 1866.04
Net Source Energy | 3900.61 | 1866.04 | 1866.04
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 182.98 | 0 | 0 | 0 | 0
Cooling | 294.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.72 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 168.87 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1170.03 | 182.98 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17424.4 | 11780.35 | 5644.06 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39280.8 | 26708.18 | 12572.62 | 0.68 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17361.74 | 11737.98 | 5623.76 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15724.41 | 10631.01 | 5093.4 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15555.01 | 10516.48 | 5038.53 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15469.9 | 10458.94 | 5010.96 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27389.1 | 18517.31 | 8871.79 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14196.17 | 9597.79 | 4598.38 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14147.52 | 9564.9 | 4582.62 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14302.17 | 9669.46 | 4632.71 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22834.9 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22834.9 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11417.45 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 813.88 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.61 | 1830.3 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 810.96 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.63 | 734.48 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.63 | 726.57 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 722.59 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.1 | 1256.48 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.57 | 663.1 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.57 | 660.82 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 668.05 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17386.4438 | 27.4717 | 84.6344 | 0 | 0.0002 | 625096.6556 | 7199.5722
February | 15656.511 | 24.8232 | 76.8274 | 0 | 0.0002 | 567440.491 | 6491.8063
March | 17787.1664 | 29.4047 | 95.9882 | 0 | 0.0003 | 709027.8256 | 7496.9514
April | 18148.2115 | 30.4638 | 101.2807 | 0 | 0.0003 | 748145.2011 | 7695.8715
May | 20449.5892 | 34.5424 | 115.6829 | 0 | 0.0003 | 854542.4543 | 8693.5754
June | 23705.4715 | 40.066 | 134.2741 | 0 | 0.0004 | 991876.0353 | 10080.1388
July | 25372.3463 | 42.8834 | 143.7166 | 0 | 0.0004 | 1061630 | 10788.946
August | 25326.097 | 42.8052 | 143.4546 | 0 | 0.0004 | 1059690 | 10769.2797
September | 22675.0473 | 38.3245 | 128.4383 | 0 | 0.0003 | 948766.9149 | 9641.988
October | 19337.8287 | 32.5585 | 108.6265 | 0 | 0.0003 | 802412.5994 | 8210.2179
November | 16592.9072 | 27.3979 | 89.3081 | 0 | 0.0002 | 659682.9947 | 6990.305
December | 17825.1909 | 27.884 | 84.7382 | 0 | 0.0002 | 625847.8995 | 7352.8505
Annual Sum or Average | 240262.8108 | 398.6253 | 1306.97 | 0 | 0.0036 | 9654160 | 101411.5026
Minimum of Months | 15656.511 | 24.8232 | 76.8274 | 0 | 0.0002 | 567440.491 | 6491.8063
Maximum of Months | 25372.3463 | 42.8834 | 143.7166 | 0 | 0.0004 | 1061630 | 10788.946
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 75758100000 | 63655.747 | 28-JAN-14:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 13841.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 68770500000 | 67502.327 | 28-FEB-15:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 17687.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 85930000000 | 80237.638 | 17-MAR-14:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 30423.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 90670800000 | 84146.067 | 01-APR-15:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 34331.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 103566000000 | 97935.453 | 27-MAY-15:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 48120.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 120210000000 | 109904.194 | 28-JUN-15:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 60089.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 128663000000 | 108928.054 | 11-JUL-15:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 59113.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 128428000000 | 109428.271 | 01-AUG-16:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 59613.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 114985000000 | 103077.99 | 09-SEP-15:30 | 32837.857 | 8089.532 | 8887.227 | 0 | 53263.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 97247700000 | 85549.918 | 14-OCT-13:00 | 32837.857 | 8089.532 | 8887.227 | 0 | 35735.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 79949700000 | 76175.14 | 13-NOV-15:30 | 32837.857 | 8089.532 | 8887.227 | 0 | 26360.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 75849100000 | 62740.306 | 09-DEC-15:30 | 32837.857 | 8089.532 | 8887.227 | 0 | 12925.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1170030000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 68770500000 | 62740.306 |  | 32837.857 | 8089.532 | 8887.227 | 0 | 12925.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 128663000000 | 109904.194 |  | 32837.857 | 8089.532 | 8887.227 | 0 | 60089.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34352.42 | 1488.27 | 0 | 35840.69
Cost per Total Building Area ($/m2) | 16.43 | 0.71 | 0 | 17.15
Cost per Net Conditioned Building Area ($/m2) | 16.43 | 0.71 | 0 | 17.15

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1481.34 | 708.67 | 708.67
Net Site Energy | 1481.34 | 708.67 | 708.67
Total Source Energy | 3988.14 | 1907.91 | 1907.91
Net Source Energy | 3988.14 | 1907.91 | 1907.91
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 437.98 | 0 | 0 | 0 | 0
Cooling | 167.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.71 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 169.31 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1043.36 | 437.98 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16847.24 | 11390.13 | 5457.1 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40040.25 | 27070.54 | 12969.71 | 0.68 | 3.21
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17698.42 | 11965.6 | 5732.81 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15505.11 | 10482.74 | 5022.36 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15199.42 | 10276.08 | 4923.35 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14948.73 | 10106.59 | 4842.14 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27960.19 | 18903.41 | 9056.77 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14556.45 | 9841.37 | 4715.08 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14498.75 | 9802.36 | 4696.39 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14610.49 | 9877.91 | 4732.58 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17505.84 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31373.9 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14598.27 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14598.27 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14598.27 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14598.27 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29196.54 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14598.27 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14598.27 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14598.27 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 786.93 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.61 | 1836.86 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.71 | 826.68 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 724.24 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 709.96 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 698.25 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.13 | 1282.68 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 679.92 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 677.23 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 682.45 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20509.9202 | 33.4985 | 73.0393 | 0 | 0.0003 | 129867.9298 | 8472.8801
February | 17867.8247 | 29.6874 | 66.1022 | 0 | 0.0003 | 117539.6855 | 7427.9685
March | 17535.4423 | 31.1984 | 74.9863 | 0 | 0.0003 | 133362.0926 | 7480.3308
April | 16206.9169 | 30.166 | 75.8312 | 0 | 0.0003 | 134878.7585 | 7036.5518
May | 17885.6383 | 34.4609 | 89.4227 | 0 | 0.0003 | 159064.7656 | 7873.4814
June | 19960.5254 | 38.5437 | 100.2133 | 0 | 0.0004 | 178259.7476 | 8794.7243
July | 21650.9412 | 41.8078 | 108.7001 | 0 | 0.0004 | 193356.1279 | 9539.5307
August | 21844.5321 | 42.1818 | 109.6726 | 0 | 0.0004 | 195085.9572 | 9624.838
September | 19253.473 | 37.1763 | 96.6536 | 0 | 0.0004 | 171927.6838 | 8483.0061
October | 16516.6548 | 31.0816 | 78.9429 | 0 | 0.0003 | 140416.5745 | 7202.3492
November | 16706.7502 | 29.6071 | 70.8694 | 0 | 0.0003 | 126039.0418 | 7116.0261
December | 19500.562 | 32.567 | 72.9598 | 0 | 0.0003 | 129735.5538 | 8122.123
Annual Sum or Average | 225439.1812 | 411.9764 | 1017.3935 | 0 | 0.0038 | 1809530 | 97173.81
Minimum of Months | 16206.9169 | 29.6071 | 66.1022 | 0 | 0.0003 | 117539.6855 | 7036.5518
Maximum of Months | 21844.5321 | 42.1818 | 109.6726 | 0 | 0.0004 | 195085.9572 | 9624.838
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74880600000 | 55375.422 | 23-JAN-17:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 473.842 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67772300000 | 58281.493 | 18-FEB-15:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 8448.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 76895300000 | 63594.246 | 28-MAR-15:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 13761.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 77769800000 | 77036.731 | 15-APR-15:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 27204.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 91715200000 | 86169.4 | 15-MAY-14:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 36336.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 102783000000 | 93988.4 | 19-JUN-14:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 44155.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 111487000000 | 102543.179 | 03-JUL-14:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 52710.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 112485000000 | 97225.236 | 17-AUG-14:39 | 32837.857 | 8089.532 | 8905.191 | 0 | 47392.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 99131900000 | 90818.697 | 11-SEP-13:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 40986.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 80962900000 | 81150.655 | 12-OCT-15:00 | 32837.857 | 8089.532 | 8905.191 | 0 | 31318.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 72672900000 | 59647.475 | 22-NOV-15:09 | 32837.857 | 8089.532 | 8905.191 | 0 | 9814.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74804300000 | 54901.58 | 01-DEC-17:30 | 32837.857 | 8089.532 | 8905.191 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1043360000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67772300000 | 54901.58 |  | 32837.857 | 8089.532 | 8905.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 112485000000 | 102543.179 |  | 32837.857 | 8089.532 | 8905.191 | 0 | 52710.599 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29884.77 | 4167.63 | 0 | 34052.4
Cost per Total Building Area ($/m2) | 14.3 | 1.99 | 0 | 16.29
Cost per Net Conditioned Building Area ($/m2) | 14.3 | 1.99 | 0 | 16.29

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1054.82 | 504.62 | 504.62
Net Site Energy | 1054.82 | 504.62 | 504.62
Total Source Energy | 2975.52 | 1423.48 | 1423.48
Net Source Energy | 2975.52 | 1423.48 | 1423.48
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 144.36 | 0 | 0 | 0 | 0
Cooling | 58.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.65 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 145.28 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 910.46 | 144.36 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12612.7 | 8824.57 | 3788.13 | 0.7 | 3.72
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28911.46 | 20826.9 | 8084.56 | 0.72 | 3.55
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14366.9 | 9840.51 | 4526.39 | 0.68 | 3.68
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12597.41 | 8819.03 | 3778.37 | 0.7 | 3.72
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12495.05 | 8735.21 | 3759.83 | 0.7 | 3.72
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12443.4 | 8692.94 | 3750.46 | 0.7 | 3.72
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22653.35 | 15574.38 | 7078.98 | 0.69 | 3.47
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11665.83 | 8060.56 | 3605.27 | 0.69 | 3.7
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11630.33 | 8031.87 | 3598.46 | 0.69 | 3.69
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11674.74 | 8067.89 | 3606.85 | 0.69 | 3.7
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21322.87 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21322.87 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10661.44 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 645.8 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.37 | 1565.98 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 695.33 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 646 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.55 | 638.43 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.55 | 634.62 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.95 | 1087.68 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 577.97 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 575.42 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 578.63 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 7947.2136 | 6.883 | 59.4512 | 0 | 0 | 358670.4416 | 2931.9273
February | 7082.1826 | 6.1304 | 53.5854 | 0 | 0 | 323284.5829 | 2614.6423
March | 7605.5785 | 6.5678 | 60.3477 | 0 | 0 | 364093.3016 | 2816.422
April | 6958.1961 | 5.9982 | 57.0979 | 0 | 0 | 344493.9096 | 2582.4469
May | 6803.6061 | 5.8429 | 59.7679 | 0 | 0 | 360617.653 | 2537.0889
June | 6561.8278 | 5.6247 | 59.5394 | 0 | 0 | 359246.0547 | 2452.7121
July | 7140.1759 | 6.1105 | 66.5739 | 0 | 0 | 401696.646 | 2674.3413
August | 7750.44 | 6.6326 | 72.279 | 0 | 0 | 436120.0191 | 2902.9607
September | 7160.2185 | 6.1278 | 66.7273 | 0 | 0 | 402621.9803 | 2681.7461
October | 6884.1597 | 5.8984 | 62.9269 | 0 | 0 | 379686.7344 | 2574.6067
November | 6895.0975 | 5.9353 | 58.1086 | 0 | 0 | 350597.7457 | 2563.692
December | 7642.3383 | 6.6056 | 59.5604 | 0 | 0 | 359339.2119 | 2826.7426
Annual Sum or Average | 86431.0345 | 74.3573 | 735.9658 | 0 | 0.0003 | 4440470 | 32159.3289
Minimum of Months | 6561.8278 | 5.6247 | 53.5854 | 0 | 0 | 323284.5829 | 2452.7121
Maximum of Months | 7947.2136 | 6.883 | 72.279 | 0 | 0 | 436120.0191 | 2931.9273
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73540900000 | 62888.215 | 26-JAN-13:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 14314.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66285500000 | 59370.727 | 13-FEB-11:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 10797.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74652800000 | 59699.236 | 31-MAR-14:09 | 32837.857 | 8089.532 | 7645.866 | 0 | 11125.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 70634200000 | 66746.588 | 11-APR-15:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 18173.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 73940200000 | 63160.559 | 30-MAY-14:09 | 32837.857 | 8089.532 | 7645.866 | 0 | 14587.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 73658900000 | 65800.731 | 30-JUN-14:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 17227.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 82362900000 | 72205.003 | 10-JUL-14:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 23631.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 89421000000 | 78479.181 | 08-AUG-14:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 29905.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 82552600000 | 77428.945 | 25-SEP-14:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 28855.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 77850000000 | 69580.454 | 05-OCT-14:09 | 32837.857 | 8089.532 | 7645.866 | 0 | 21007.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71885700000 | 64224.61 | 20-NOV-12:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 15651.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73678000000 | 63790.814 | 19-DEC-12:00 | 32837.857 | 8089.532 | 7645.866 | 0 | 15217.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 910463000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66285500000 | 59370.727 |  | 32837.857 | 8089.532 | 7645.866 | 0 | 10797.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 89421000000 | 78479.181 |  | 32837.857 | 8089.532 | 7645.866 | 0 | 29905.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33401.46 | 1246.13 | 0 | 34647.59
Cost per Total Building Area ($/m2) | 15.98 | 0.6 | 0 | 16.58
Cost per Net Conditioned Building Area ($/m2) | 15.98 | 0.6 | 0 | 16.58

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1361.54 | 651.35 | 651.35
Net Site Energy | 1361.54 | 651.35 | 651.35
Total Source Energy | 4116.42 | 1969.28 | 1969.28
Net Source Energy | 4116.42 | 1969.28 | 1969.28
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 303.34 | 0 | 0 | 0 | 0
Cooling | 195.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.63 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 156.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1058.2 | 303.34 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.252 | 0.162 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.252 | 0.162
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.252 | 0.162
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14982.34 | 10326.43 | 4655.9 | 0.69 | 3.69
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32558.02 | 23335.59 | 9222.43 | 0.72 | 3.54
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15045.58 | 10467.08 | 4578.5 | 0.7 | 3.71
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14035.66 | 9615.28 | 4420.38 | 0.69 | 3.68
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13921.42 | 9522.28 | 4399.14 | 0.68 | 3.68
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13859.5 | 9471.9 | 4387.6 | 0.68 | 3.67
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25003.95 | 16904.75 | 8099.2 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12943.91 | 8753.55 | 4190.37 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12906.11 | 8725.61 | 4180.51 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13001.55 | 8799.99 | 4201.56 | 0.68 | 3.66
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13978.82 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25050.95 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12342.56 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12342.56 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12342.56 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12342.56 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24685.13 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12342.56 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12342.56 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12342.56 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.64 | 737.39 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.53 | 1741.38 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 759 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.59 | 679.61 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 671.27 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.57 | 666.76 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1147.07 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.52 | 605.06 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.52 | 602.84 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 609.17 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20845.562 | 30.9208 | 112.8586 | 0 | 0.0002 | 562742.6079 | 8461.8207
February | 17027.378 | 26.2989 | 101.9786 | 0 | 0.0002 | 508538.3544 | 7020.1862
March | 19174.5996 | 29.6429 | 115.0982 | 0 | 0.0002 | 573963.2688 | 7908.332
April | 18045.8173 | 29.2531 | 121.0606 | 0 | 0.0002 | 603750.5536 | 7583.6373
May | 20211.1321 | 33.0284 | 138.0796 | 0 | 0.0003 | 688636.776 | 8521.1638
June | 23999.541 | 39.356 | 165.2459 | 0 | 0.0003 | 824126.6391 | 10132.5886
July | 25782.522 | 42.2815 | 177.5381 | 0 | 0.0003 | 885430.946 | 10885.5348
August | 26154.2607 | 42.8911 | 180.0978 | 0 | 0.0003 | 898197.3051 | 11042.4851
September | 22424.5837 | 36.7743 | 154.4119 | 0 | 0.0003 | 770094.2812 | 9467.7547
October | 19047.3922 | 30.9541 | 128.5066 | 0 | 0.0002 | 640887.9249 | 8012.5811
November | 17646.2998 | 27.6391 | 109.297 | 0 | 0.0002 | 545048.6612 | 7315.2978
December | 20258.6383 | 30.3853 | 112.8311 | 0 | 0.0002 | 562620.2161 | 8258.405
Annual Sum or Average | 250617.7267 | 399.4255 | 1617.0041 | 0 | 0.0031 | 8064040 | 104609.787
Minimum of Months | 17027.378 | 26.2989 | 101.9786 | 0 | 0.0002 | 508538.3544 | 7020.1862
Maximum of Months | 26154.2607 | 42.8911 | 180.0978 | 0 | 0.0003 | 898197.3051 | 11042.4851
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73845400000 | 54215.925 | 02-JAN-16:40 | 32837.857 | 8089.532 | 8219.536 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66732500000 | 55058.758 | 08-FEB-17:10 | 32837.857 | 8089.532 | 8219.536 | 0 | 842.832 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 75317800000 | 60285.069 | 31-MAR-15:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 11138.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 79226600000 | 77858.522 | 21-APR-14:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 28711.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 90365700000 | 86923.269 | 31-MAY-15:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 37776.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 108145000000 | 100327.527 | 27-JUN-15:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 51180.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 116190000000 | 99665.66 | 24-JUL-15:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 50518.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 117865000000 | 97461.508 | 04-AUG-14:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 48314.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 101055000000 | 95419.621 | 01-SEP-14:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 46272.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 84099900000 | 79032.973 | 03-OCT-14:00 | 32837.857 | 8089.532 | 8219.536 | 0 | 29886.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71523500000 | 58886.747 | 10-NOV-16:40 | 32837.857 | 8089.532 | 8219.536 | 0 | 4670.821 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73829300000 | 55690.175 | 05-DEC-16:30 | 32837.857 | 8089.532 | 8219.536 | 0 | 1474.25 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1058200000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66732500000 | 54215.925 |  | 32837.857 | 8089.532 | 8219.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 117865000000 | 100327.527 |  | 32837.857 | 8089.532 | 8219.536 | 0 | 51180.601 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29194.13 | 2315.7 | 0 | 31509.83
Cost per Total Building Area ($/m2) | 13.97 | 1.11 | 0 | 15.07
Cost per Net Conditioned Building Area ($/m2) | 13.97 | 1.11 | 0 | 15.07

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1259.51 | 602.55 | 602.55
Net Site Energy | 1259.51 | 602.55 | 602.55
Total Source Energy | 3074.65 | 1470.9 | 1470.9
Net Source Energy | 3074.65 | 1470.9 | 1470.9
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 411.16 | 0 | 0 | 0 | 0
Cooling | 12.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.67 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 129.17 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 848.36 | 411.16 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.39 | 0.223 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.39 | 0.223 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.39 | 0.223 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.39 | 0.223 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.39 | 0.223 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.39 | 0.223
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.39 | 0.223
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9043.41 | 6871.4 | 2172.02 | 0.76 | 3.9
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20985.96 | 16261.4 | 4724.56 | 0.77 | 3.7
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10144.6 | 7788.47 | 2356.14 | 0.77 | 3.93
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9220.54 | 7020.93 | 2199.61 | 0.76 | 3.91
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9115.77 | 6934.39 | 2181.37 | 0.76 | 3.91
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9052.64 | 6882.27 | 2170.36 | 0.76 | 3.91
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15976.67 | 12022.58 | 3954.09 | 0.75 | 3.88
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8271.27 | 6241.64 | 2029.63 | 0.75 | 3.89
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8241.57 | 6217.46 | 2024.11 | 0.75 | 3.89
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8281.51 | 6250.14 | 2031.36 | 0.75 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23568.82 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23568.82 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 11784.41 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 566.74 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.19 | 1350.8 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 651.07 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 580.69 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 572.81 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 568.06 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.84 | 978.97 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.44 | 510.15 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.44 | 507.98 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.44 | 510.93 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10077.3 | 8.8256 | 57.8944 | 0 | 0 | 349205.6787 | 3664.4041
February | 7780.1003 | 6.7709 | 52.3673 | 0 | 0 | 315909.0088 | 2852.4765
March | 8913.5013 | 7.7649 | 58.6284 | 0 | 0 | 353673.1985 | 3263.8508
April | 7867.4183 | 6.833 | 55.4397 | 0 | 0 | 334454.8116 | 2892.0711
May | 7445.7293 | 6.4395 | 57.3343 | 0 | 0 | 345905.914 | 2751.9042
June | 6983.9636 | 6.0266 | 56.2059 | 0 | 0 | 339107.9546 | 2588.6436
July | 6848.9945 | 5.8968 | 57.4979 | 0 | 0 | 346911.884 | 2545.8723
August | 7174.1725 | 6.1809 | 59.5029 | 0 | 0 | 359006.7594 | 2664.5343
September | 6939.9853 | 5.9735 | 58.5548 | 0 | 0 | 353290.0246 | 2580.589
October | 7382.8237 | 6.375 | 58.6634 | 0 | 0 | 353931.8533 | 2734.1874
November | 7723.8203 | 6.7002 | 55.8741 | 0 | 0 | 337081.4648 | 2843.6968
December | 9810.6415 | 8.5836 | 57.8747 | 0 | 0 | 349094.6891 | 3572.0529
Annual Sum or Average | 94948.4505 | 82.3704 | 685.8379 | 0 | 0.0004 | 4137570 | 34954.2829
Minimum of Months | 6848.9945 | 5.8968 | 52.3673 | 0 | 0 | 315909.0088 | 2545.8723
Maximum of Months | 10077.3 | 8.8256 | 59.5029 | 0 | 0 | 359006.7594 | 3664.4041
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 71600300000 | 52794.573 | 02-JAN-16:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 64773200000 | 55889.323 | 15-FEB-15:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 8163.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 72516300000 | 52794.573 | 01-MAR-17:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 68575800000 | 58216.435 | 29-APR-13:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 10490.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 70923700000 | 59210.678 | 17-MAY-13:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 11485.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 69529900000 | 59952.113 | 16-JUN-14:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 12226.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 71130000000 | 66386.153 | 03-JUL-12:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 18660.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 73609900000 | 63519.236 | 26-AUG-12:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 15793.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 72437700000 | 74852.048 | 28-SEP-14:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 27126.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 72569300000 | 60058.827 | 13-OCT-14:00 | 32837.857 | 8089.532 | 6798.184 | 0 | 12333.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 69114400000 | 52794.573 | 06-NOV-17:10 | 32837.857 | 8089.532 | 6798.184 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 71577500000 | 52794.573 | 01-DEC-16:49 | 32837.857 | 8089.532 | 6798.184 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 848358000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 64773200000 | 52794.573 |  | 32837.857 | 8089.532 | 6798.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73609900000 | 74852.048 |  | 32837.857 | 8089.532 | 6798.184 | 0 | 27126.475 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 35335.43 | 3517.69 | 0 | 38853.13
Cost per Total Building Area ($/m2) | 16.9 | 1.68 | 0 | 18.59
Cost per Net Conditioned Building Area ($/m2) | 16.9 | 1.68 | 0 | 18.59

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1768.48 | 846.03 | 846.03
Net Site Energy | 1768.48 | 846.03 | 846.03
Total Source Energy | 4401.66 | 2105.74 | 2105.74
Net Source Energy | 4401.66 | 2105.74 | 2105.74
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 773.91 | 0 | 0 | 0 | 0
Cooling | 123.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.62 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 163.99 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 994.56 | 773.91 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16168.05 | 10930.95 | 5237.1 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38121.35 | 25773.2 | 12348.14 | 0.68 | 3.44
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16243.53 | 10981.98 | 5261.55 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15462.03 | 10453.62 | 5008.41 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15301.44 | 10345.04 | 4956.39 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15226.76 | 10294.56 | 4932.2 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26901.37 | 18187.57 | 8713.81 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14005.79 | 9469.08 | 4536.71 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13949.58 | 9431.08 | 4518.5 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14055.51 | 9502.69 | 4552.81 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20794.15 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37381.37 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16844.23 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16771.56 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16767.95 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16779.31 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 33313.23 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16779.71 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16774.56 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16882.29 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 755.2 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.54 | 1748.83 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 758.73 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 722.22 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 714.72 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 711.23 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.08 | 1234.11 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 654.2 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 651.58 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.57 | 656.52 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22559.5623 | 34.2099 | 75.92 | 0 | 0.0003 | 4718.6738 | 9063.5704
February | 19173.6869 | 29.7692 | 68.3561 | 0 | 0.0003 | 4248.9142 | 7766.6894
March | 17885.5961 | 30.1445 | 76.879 | 0 | 0.0003 | 4779.8653 | 7462.1083
April | 14585.5809 | 26.3436 | 72.4175 | 0 | 0.0003 | 4503.2018 | 6246.3145
May | 14040.5321 | 27.2861 | 80.351 | 0 | 0.0003 | 4997.2183 | 6189.0875
June | 16385.9374 | 32.7264 | 98.6445 | 0 | 0.0004 | 6135.2121 | 7303.6146
July | 18003.1086 | 35.991 | 108.5719 | 0 | 0.0004 | 6752.6576 | 8027.6054
August | 18464.6638 | 36.9022 | 111.2921 | 0 | 0.0004 | 6921.8379 | 8232.3649
September | 14683.9165 | 29.1926 | 87.6556 | 0 | 0.0004 | 5451.7153 | 6532.6843
October | 14702.9935 | 27.6581 | 79.0876 | 0 | 0.0003 | 4918.3634 | 6397.399
November | 15980.1186 | 27.8526 | 73.7662 | 0 | 0.0003 | 4586.7086 | 6751.2037
December | 21040.8469 | 32.8017 | 75.7499 | 0 | 0.0003 | 4708.5673 | 8535.2279
Annual Sum or Average | 207506.5435 | 370.8779 | 1008.6915 | 0 | 0.0041 | 62722.9355 | 88507.8699
Minimum of Months | 14040.5321 | 26.3436 | 68.3561 | 0 | 0.0003 | 4248.9142 | 6189.0875
Maximum of Months | 22559.5623 | 36.9022 | 111.2921 | 0 | 0.0004 | 6921.8379 | 9063.5704
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74821200000 | 54603.739 | 02-JAN-16:49 | 32837.857 | 8089.532 | 8607.349 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67372500000 | 54603.739 | 01-FEB-17:30 | 32837.857 | 8089.532 | 8607.349 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 75791500000 | 62987.891 | 09-MAR-15:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 13453.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 71404600000 | 63548.798 | 04-APR-15:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 14014.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 79237900000 | 77610.53 | 31-MAY-15:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 28075.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 97282400000 | 97776.512 | 30-JUN-14:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 48241.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 107073000000 | 100766.693 | 25-JUL-12:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 51231.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 109755000000 | 100742.522 | 17-AUG-14:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 51207.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 86444600000 | 87453.316 | 09-SEP-14:30 | 32837.857 | 8089.532 | 8607.349 | 0 | 37918.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 77987600000 | 74461.956 | 20-OCT-14:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 24927.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 72728700000 | 66928.168 | 04-NOV-13:00 | 32837.857 | 8089.532 | 8607.349 | 0 | 17393.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74660900000 | 54603.739 | 01-DEC-16:40 | 32837.857 | 8089.532 | 8607.349 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 994560000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67372500000 | 54603.739 |  | 32837.857 | 8089.532 | 8607.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 109755000000 | 100766.693 |  | 32837.857 | 8089.532 | 8607.349 | 0 | 51231.954 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21314.96 | 7471.8 | 0 | 28786.76
Cost per Total Building Area ($/m2) | 10.2 | 3.57 | 0 | 13.77
Cost per Net Conditioned Building Area ($/m2) | 10.2 | 3.57 | 0 | 13.77

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1511.95 | 723.31 | 723.31
Net Site Energy | 1511.95 | 723.31 | 723.31
Total Source Energy | 3782.18 | 1809.38 | 1809.38
Net Source Energy | 3782.18 | 1809.38 | 1809.38
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 554.56 | 0 | 0 | 0 | 0
Cooling | 89.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.65 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 161.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 957.38 | 554.56 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11396.77 | 8662.04 | 2734.73 | 0.76 | 3.9
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25987.42 | 20754.99 | 5232.43 | 0.8 | 3.77
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12163.87 | 9437.09 | 2726.77 | 0.78 | 3.96
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11171.38 | 8552.42 | 2618.96 | 0.77 | 3.92
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11064.17 | 8457.45 | 2606.72 | 0.76 | 3.92
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11004.22 | 8404.37 | 2599.85 | 0.76 | 3.92
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19803.45 | 14874.63 | 4928.83 | 0.75 | 3.63
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10191.97 | 7690.12 | 2501.86 | 0.75 | 3.89
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10159.84 | 7662.06 | 2497.78 | 0.75 | 3.89
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10210.55 | 7706.45 | 2504.11 | 0.75 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17128.33 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30590.64 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13728.18 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13658.69 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13655.32 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13667.22 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27075.97 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13667.59 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13661.49 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13762.88 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 714.7 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.57 | 1788.42 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 799.41 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 712.33 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 703.03 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 697.84 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1186.61 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 628.43 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 625.73 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 630.02 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 25809.9139 | 40.0656 | 90.162 | 0 | 0.0004 | 93721.6364 | 10564.8363
February | 22134.7959 | 35.1102 | 81.3807 | 0 | 0.0003 | 84599.8745 | 9134.0156
March | 23914.8999 | 38.5942 | 91.5004 | 0 | 0.0004 | 95124.9975 | 9933.3697
April | 21036.8765 | 35.3015 | 87.8059 | 0 | 0.0003 | 91294.4558 | 8870.5509
May | 22277.9079 | 38.6475 | 99.824 | 0 | 0.0004 | 103798.7823 | 9517.7781
June | 23504.0153 | 41.204 | 107.6428 | 0 | 0.0004 | 111931.7201 | 10083.7395
July | 25283.6517 | 44.3608 | 115.9933 | 0 | 0.0005 | 120615.1299 | 10850.8699
August | 25185.8246 | 44.1842 | 115.5173 | 0 | 0.0004 | 120120.1664 | 10808.3935
September | 22410.0289 | 39.2401 | 102.383 | 0 | 0.0004 | 106462.0068 | 9609.8709
October | 21709.3295 | 36.7192 | 92.1781 | 0 | 0.0004 | 95842.3775 | 9182.4722
November | 22770.4763 | 36.7212 | 86.98 | 0 | 0.0003 | 90425.3773 | 9455.4503
December | 25987.2143 | 40.2126 | 90.0874 | 0 | 0.0004 | 93642.9587 | 10624.8334
Annual Sum or Average | 282024.9345 | 470.3611 | 1161.4549 | 0 | 0.0046 | 1207580 | 118636.1803
Minimum of Months | 21036.8765 | 35.1102 | 81.3807 | 0 | 0.0003 | 84599.8745 | 8870.5509
Maximum of Months | 25987.2143 | 44.3608 | 115.9933 | 0 | 0.0005 | 120615.1299 | 10850.8699
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74303600000 | 54482.915 | 02-JAN-17:10 | 32837.857 | 8089.532 | 8486.526 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 67071800000 | 54977.799 | 14-FEB-17:49 | 32837.857 | 8089.532 | 8486.526 | 0 | 494.884 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 75416200000 | 54907.375 | 02-MAR-15:09 | 32837.857 | 8089.532 | 8486.526 | 0 | 5493.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 72379300000 | 65923.808 | 22-APR-14:09 | 32837.857 | 8089.532 | 8486.526 | 0 | 16509.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 82292900000 | 71710.438 | 31-MAY-15:00 | 32837.857 | 8089.532 | 8486.526 | 0 | 22296.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 88740800000 | 80313.473 | 29-JUN-14:00 | 32837.857 | 8089.532 | 8486.526 | 0 | 30899.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 95625100000 | 82761.435 | 31-JUL-14:00 | 32837.857 | 8089.532 | 8486.526 | 0 | 33347.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 95232700000 | 82078.575 | 01-AUG-14:00 | 32837.857 | 8089.532 | 8486.526 | 0 | 32664.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 84404400000 | 73682.417 | 02-SEP-15:20 | 32837.857 | 8089.532 | 8486.526 | 0 | 24268.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 75985000000 | 64366.243 | 13-OCT-14:00 | 32837.857 | 8089.532 | 8486.526 | 0 | 14952.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71690300000 | 55110.634 | 08-NOV-17:10 | 32837.857 | 8089.532 | 8486.526 | 0 | 627.719 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74241300000 | 54482.915 | 01-DEC-16:00 | 32837.857 | 8089.532 | 8486.526 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 957384000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 67071800000 | 54482.915 |  | 32837.857 | 8089.532 | 8486.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 95625100000 | 82761.435 |  | 32837.857 | 8089.532 | 8486.526 | 0 | 33347.519 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 10013.16 | 3815.17 | 0 | 13828.33
Cost per Total Building Area ($/m2) | 4.79 | 1.83 | 0 | 6.62
Cost per Net Conditioned Building Area ($/m2) | 4.79 | 1.83 | 0 | 6.62

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1644.83 | 786.88 | 786.88
Net Site Energy | 1644.83 | 786.88 | 786.88
Total Source Energy | 2355.26 | 1126.75 | 1126.75
Net Source Energy | 2355.26 | 1126.75 | 1126.75
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 784.67 | 0 | 0 | 0 | 0
Cooling | 18.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.49 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 135.53 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 860.16 | 784.67 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.704 | 0.787 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10479.47 | 7783.46 | 2696.01 | 0.74 | 3.85
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23277.38 | 17821.38 | 5456.01 | 0.77 | 3.67
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11206.7 | 8355.52 | 2851.18 | 0.75 | 3.86
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10258.43 | 7569.34 | 2689.09 | 0.74 | 3.83
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10152.63 | 7482.11 | 2670.52 | 0.74 | 3.83
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10092.97 | 7432.95 | 2660.02 | 0.74 | 3.83
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17984.14 | 13068.44 | 4915.7 | 0.73 | 3.8
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9298.72 | 6782.78 | 2515.94 | 0.73 | 3.81
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9267.4 | 6757.31 | 2510.09 | 0.73 | 3.81
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9329.89 | 6808.33 | 2521.56 | 0.73 | 3.81
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16004.86 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28693.84 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14053.58 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14053.58 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14053.58 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14053.58 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28107.17 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14053.58 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14053.58 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14053.58 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 622.61 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.28 | 1457.93 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.58 | 671.9 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.52 | 599.96 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.51 | 592.02 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.51 | 587.55 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.87 | 1013.4 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.46 | 528.88 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.45 | 526.6 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.46 | 531.19 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10647.8793 | 12.1094 | 15.6498 | 0 | 0.0001 | 206379.1471 | 3947.011
February | 8219.6905 | 9.6577 | 14.0591 | 0 | 0.0001 | 185494.6637 | 3080.1006
March | 8697.397 | 10.3526 | 15.7289 | 0 | 0.0001 | 207558.7207 | 3273.4103
April | 6777.073 | 8.4531 | 14.7225 | 0 | 0.0001 | 194371.7202 | 2592.0377
May | 5259.3108 | 7.1668 | 15.2996 | 0 | 0.0001 | 202111.5483 | 2076.5244
June | 4362.4128 | 6.3171 | 15.0689 | 0 | 0.0001 | 199119.5355 | 1762.2999
July | 4018.9264 | 6.1458 | 15.9645 | 0 | 0.0001 | 210995.6213 | 1658.4667
August | 4083.4839 | 6.3115 | 16.6485 | 0 | 0.0001 | 220042.7743 | 1692.2789
September | 4655.4617 | 6.6672 | 15.6073 | 0 | 0.0001 | 206224.925 | 1872.7356
October | 6124.5405 | 7.9682 | 15.4056 | 0 | 0.0001 | 203455.3467 | 2377.6988
November | 8653.8194 | 10.2107 | 15.0753 | 0 | 0.0001 | 198912.8873 | 3247.3684
December | 10720.5428 | 12.1764 | 15.6568 | 0 | 0.0001 | 206467.7463 | 3972.2734
Annual Sum or Average | 82220.5379 | 103.5364 | 184.8867 | 0 | 0.0008 | 2441130 | 31552.2056
Minimum of Months | 4018.9264 | 6.1458 | 14.0591 | 0 | 0.0001 | 185494.6637 | 1658.4667
Maximum of Months | 10720.5428 | 12.1764 | 16.6485 | 0 | 0.0001 | 220042.7743 | 3972.2734
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 72719900000 | 53128.435 | 02-JAN-17:19 | 32837.857 | 8089.532 | 7132.046 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 65361100000 | 53128.435 | 01-FEB-17:10 | 32837.857 | 8089.532 | 7132.046 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 73135600000 | 53128.435 | 01-MAR-17:49 | 32837.857 | 8089.532 | 7132.046 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 68489000000 | 54348.377 | 29-APR-15:09 | 32837.857 | 8089.532 | 7132.046 | 0 | 6288.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 71216200000 | 59083.465 | 06-MAY-14:00 | 32837.857 | 8089.532 | 7132.046 | 0 | 11024.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 70161900000 | 63445.804 | 28-JUN-14:00 | 32837.857 | 8089.532 | 7132.046 | 0 | 15386.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 74346600000 | 71035.936 | 24-JUL-14:00 | 32837.857 | 8089.532 | 7132.046 | 0 | 22976.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 77534500000 | 68134.978 | 07-AUG-14:00 | 32837.857 | 8089.532 | 7132.046 | 0 | 20075.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 72665600000 | 78769.292 | 02-SEP-15:00 | 32837.857 | 8089.532 | 7132.046 | 0 | 30709.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 71689700000 | 54151.627 | 17-OCT-14:00 | 32837.857 | 8089.532 | 7132.046 | 0 | 6092.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 70089100000 | 53128.435 | 01-NOV-16:49 | 32837.857 | 8089.532 | 7132.046 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 72751100000 | 53128.435 | 01-DEC-16:19 | 32837.857 | 8089.532 | 7132.046 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 860160000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 65361100000 | 53128.435 |  | 32837.857 | 8089.532 | 7132.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 77534500000 | 78769.292 |  | 32837.857 | 8089.532 | 7132.046 | 0 | 30709.856 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18032.89 | 6600.38 | 0 | 24633.27
Cost per Total Building Area ($/m2) | 8.63 | 3.16 | 0 | 11.78
Cost per Net Conditioned Building Area ($/m2) | 8.63 | 3.16 | 0 | 11.78

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2011.97 | 962.52 | 962.52
Net Site Energy | 2011.97 | 962.52 | 962.52
Total Source Energy | 4513.57 | 2159.27 | 2159.27
Net Source Energy | 4513.57 | 2159.27 | 2159.27
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1068 | 0 | 0 | 0 | 0
Cooling | 85.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.63 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 152.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 943.97 | 1068 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14966.39 | 10118.52 | 4847.86 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34277.72 | 23174.59 | 11103.13 | 0.68 | 3.44
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16117.13 | 10896.52 | 5220.61 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13985.82 | 9455.58 | 4530.24 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13700.21 | 9262.48 | 4437.73 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13453.33 | 9095.57 | 4357.76 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25379.76 | 17158.83 | 8220.93 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13203.3 | 8926.53 | 4276.77 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13147.22 | 8888.62 | 4258.61 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13229.17 | 8944.02 | 4285.15 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26080.94 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 47555.97 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21753.4 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21683.81 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21680.6 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21693.91 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 43110.11 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21694.25 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21686.36 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21782.8 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 699.07 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.38 | 1572.5 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.65 | 752.82 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 653.27 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.55 | 639.93 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 628.4 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.02 | 1164.31 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 616.72 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 614.1 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 617.93 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37920.9003 | 57.5441 | 138.7745 | 0 | 0.0004 | 31932.5409 | 15335.302
February | 32416.9101 | 50.1908 | 124.62 | 0 | 0.0004 | 28677.4713 | 13204.9748
March | 33603.0436 | 53.7478 | 139.494 | 0 | 0.0004 | 32103.4492 | 13852.6462
April | 27626.5822 | 46.9012 | 130.9466 | 0 | 0.0004 | 30140.9657 | 11648.2552
May | 27241.3855 | 48.575 | 143.075 | 0 | 0.0004 | 32936.1469 | 11708.4012
June | 30279.22 | 55.0559 | 165.4085 | 0 | 0.0005 | 38078.8025 | 13115.7987
July | 33739.2525 | 61.4283 | 184.7964 | 0 | 0.0006 | 42542.2042 | 14622.3117
August | 33039.1037 | 60.1377 | 180.8663 | 0 | 0.0005 | 41637.4522 | 14317.3553
September | 27511.9832 | 49.8043 | 148.9731 | 0 | 0.0004 | 34294.9078 | 11896.1067
October | 27664.1752 | 48.1969 | 138.5091 | 0 | 0.0004 | 31883.5287 | 11781.8788
November | 30686.8884 | 50.102 | 133.4945 | 0 | 0.0004 | 30724.4569 | 12747.8669
December | 36467.2306 | 56.1691 | 138.4359 | 0 | 0.0004 | 31856.2428 | 14826.8807
Annual Sum or Average | 378196.6754 | 637.8532 | 1767.3938 | 0 | 0.0054 | 406808.169 | 159057.7782
Minimum of Months | 27241.3855 | 46.9012 | 124.62 | 0 | 0.0004 | 28677.4713 | 11648.2552
Maximum of Months | 37920.9003 | 61.4283 | 184.7964 | 0 | 0.0006 | 42542.2042 | 15335.302
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74097100000 | 53955.433 | 02-JAN-16:30 | 32837.857 | 8089.532 | 7959.044 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66543900000 | 53955.433 | 01-FEB-16:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74493600000 | 53955.433 | 01-MAR-17:40 | 32837.857 | 8089.532 | 7959.044 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 69939800000 | 55657.855 | 07-APR-14:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 6771.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 76425800000 | 73991.869 | 30-MAY-15:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 25105.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 88359000000 | 91347.112 | 08-JUN-12:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 42460.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 98716000000 | 93757.971 | 13-JUL-14:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 44871.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 96616600000 | 93348.899 | 04-AUG-15:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 44462.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 79578700000 | 78253.608 | 05-SEP-14:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 29367.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 73983300000 | 62372.55 | 31-OCT-16:49 | 32837.857 | 8089.532 | 7959.044 | 0 | 8417.118 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71293800000 | 60689.259 | 02-NOV-14:00 | 32837.857 | 8089.532 | 7959.044 | 0 | 11802.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73920000000 | 53955.433 | 01-DEC-16:19 | 32837.857 | 8089.532 | 7959.044 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 943968000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66543900000 | 53955.433 |  | 32837.857 | 8089.532 | 7959.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 98716000000 | 93757.971 |  | 32837.857 | 8089.532 | 7959.044 | 0 | 44871.538 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13862.91 | 8881.22 | 0 | 22744.12
Cost per Total Building Area ($/m2) | 6.63 | 4.25 | 0 | 10.88
Cost per Net Conditioned Building Area ($/m2) | 6.63 | 4.25 | 0 | 10.88

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1714.07 | 820.01 | 820.01
Net Site Energy | 1714.07 | 820.01 | 820.01
Total Source Energy | 3889.13 | 1860.54 | 1860.54
Net Source Energy | 3889.13 | 1860.54 | 1860.54
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 807.8 | 0 | 0 | 0 | 0
Cooling | 51.16 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.59 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 148.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 906.27 | 807.8 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11469.48 | 8610.85 | 2858.63 | 0.75 | 3.87
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23151.23 | 18252.33 | 4898.9 | 0.79 | 3.74
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 11556.52 | 8894.57 | 2661.96 | 0.77 | 3.94
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10582.44 | 8030.05 | 2552.4 | 0.76 | 3.9
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10473.58 | 7934.13 | 2539.44 | 0.76 | 3.9
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10356.78 | 7855.25 | 2501.53 | 0.76 | 3.9
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18528.48 | 13806.99 | 4721.49 | 0.75 | 3.84
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9534.1 | 7136.58 | 2397.52 | 0.75 | 3.87
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9501.83 | 7108.63 | 2393.2 | 0.75 | 3.87
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9536.16 | 7138.43 | 2397.72 | 0.75 | 3.87
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21790.61 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39557.72 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18051.38 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17984.2 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17981.15 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17994.71 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35705.53 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17995.03 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17986.64 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18078.89 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.6 | 698.98 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.36 | 1548.78 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.64 | 745.9 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.57 | 661.15 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 651.81 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 646.37 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.96 | 1089.63 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 576.98 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 574.3 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.5 | 577.16 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 27459.0924 | 41.3959 | 89.2668 | 0 | 0.0004 | 92780.8731 | 11119.2681
February | 23934.8755 | 36.543 | 80.3 | 0 | 0.0003 | 83465.1443 | 9737.3002
March | 25039.9526 | 39.3785 | 90.2224 | 0 | 0.0004 | 93788.5917 | 10299.5049
April | 21524.805 | 35.2499 | 85.1315 | 0 | 0.0003 | 88507.7433 | 8990.9183
May | 21286.3212 | 35.8996 | 89.8183 | 0 | 0.0004 | 93388.0456 | 8993.3348
June | 21001.3979 | 36.4191 | 94.0289 | 0 | 0.0004 | 97772.9008 | 8971.0528
July | 23094.4881 | 40.5119 | 105.9071 | 0 | 0.0004 | 110126.9822 | 9910.5768
August | 23384.5334 | 40.9792 | 107.0122 | 0 | 0.0004 | 111275.839 | 10030.9666
September | 21115.2868 | 36.3247 | 92.9591 | 0 | 0.0004 | 96658.5805 | 8991.0728
October | 22078.29 | 36.6167 | 89.8124 | 0 | 0.0004 | 93377.7001 | 9267.2689
November | 23906.4749 | 37.5497 | 85.8882 | 0 | 0.0003 | 89282.7169 | 9828.7469
December | 27879.2764 | 41.7604 | 89.1774 | 0 | 0.0004 | 92685.5037 | 11263.0408
Annual Sum or Average | 281704.7942 | 458.6286 | 1099.5243 | 0 | 0.0044 | 1143110 | 117403.0519
Minimum of Months | 21001.3979 | 35.2499 | 80.3 | 0 | 0.0003 | 83465.1443 | 8971.0528
Maximum of Months | 27879.2764 | 41.7604 | 107.0122 | 0 | 0.0004 | 111275.839 | 11263.0408
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73557800000 | 53767.434 | 02-JAN-16:49 | 32837.857 | 8089.532 | 7771.045 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66172200000 | 53767.434 | 01-FEB-17:19 | 32837.857 | 8089.532 | 7771.045 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74356700000 | 55159.758 | 30-MAR-15:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 6461.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 70170000000 | 59335.953 | 25-APR-14:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 10637.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 74039200000 | 65030.353 | 23-MAY-15:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 16331.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 77515500000 | 72841.943 | 27-JUN-15:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 24143.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 87310000000 | 77780.264 | 17-JUL-15:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 29081.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 88220800000 | 78663.56 | 30-AUG-13:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 29965.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 76632100000 | 72025.065 | 02-SEP-14:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 23326.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 74031000000 | 64422.91 | 05-OCT-14:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 15724.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 70784400000 | 53767.434 | 01-NOV-16:00 | 32837.857 | 8089.532 | 7771.045 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73482200000 | 53767.434 | 01-DEC-16:40 | 32837.857 | 8089.532 | 7771.045 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 906272000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66172200000 | 53767.434 |  | 32837.857 | 8089.532 | 7771.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 88220800000 | 78663.56 |  | 32837.857 | 8089.532 | 7771.045 | 0 | 29965.126 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 9488.87 | 5587.88 | 0 | 15076.75
Cost per Total Building Area ($/m2) | 4.54 | 2.67 | 0 | 7.21
Cost per Net Conditioned Building Area ($/m2) | 4.54 | 2.67 | 0 | 7.21

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2345.09 | 1121.88 | 1121.88
Net Site Energy | 2345.09 | 1121.88 | 1121.88
Total Source Energy | 4744.14 | 2269.58 | 2269.58
Net Source Energy | 4744.14 | 2269.58 | 2269.58
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1414.04 | 0 | 0 | 0 | 0
Cooling | 72.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.58 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 152.26 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 931.05 | 1414.04 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16935.84 | 11450.04 | 5485.8 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33393.39 | 22576.71 | 10816.68 | 0.68 | 3.44
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15930.77 | 10770.52 | 5160.24 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13784.75 | 9319.64 | 4465.11 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13493.49 | 9122.72 | 4370.77 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13243.42 | 8953.65 | 4289.77 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24751.7 | 16734.21 | 8017.49 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12880.01 | 8707.96 | 4172.05 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12824.5 | 8670.43 | 4154.07 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12907.01 | 8726.22 | 4180.8 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29825.07 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 54402.99 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24890.91 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24813.67 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24810.24 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24825.48 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 49338.05 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24825.83 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24816.41 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24922.71 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 791.06 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1531.93 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.64 | 744.12 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.56 | 643.88 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 630.27 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 618.59 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1135.49 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.52 | 601.62 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.52 | 599.03 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.52 | 602.88 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 34114.0319 | 45.9871 | 49.0701 | 0 | 0.0004 | 32195.9988 | 13242.7906
February | 28038.15 | 38.8952 | 43.9077 | 0 | 0.0003 | 28817.2909 | 10989.1959
March | 25355.2705 | 37.9896 | 48.8762 | 0 | 0.0004 | 32097.9987 | 10206.862
April | 19241.2814 | 31.5094 | 45.8184 | 0 | 0.0003 | 30105.195 | 8001.8629
May | 18139.5524 | 32.0732 | 50.9053 | 0 | 0.0004 | 33458.5551 | 7770.0316
June | 19076.287 | 34.6817 | 56.6345 | 0 | 0.0004 | 37227.9774 | 8262.2965
July | 20455.3763 | 37.2946 | 61.0729 | 0 | 0.0004 | 40145.8786 | 8869.7064
August | 20844.157 | 38.0258 | 62.3067 | 0 | 0.0005 | 40956.9632 | 9040.4291
September | 16959.4803 | 30.2815 | 48.5537 | 0 | 0.0004 | 31914.0968 | 7292.7346
October | 19893.5312 | 32.7971 | 48.0862 | 0 | 0.0004 | 31596.313 | 8294.0935
November | 24176.8512 | 36.264 | 46.735 | 0 | 0.0004 | 30692.0511 | 9736.312
December | 31462.9256 | 43.5034 | 48.8061 | 0 | 0.0004 | 32031.1551 | 12317.8477
Annual Sum or Average | 277756.8947 | 439.3026 | 610.7727 | 0 | 0.0046 | 401239.4737 | 114024.1629
Minimum of Months | 16959.4803 | 30.2815 | 43.9077 | 0 | 0.0003 | 28817.2909 | 7292.7346
Maximum of Months | 34114.0319 | 45.9871 | 62.3067 | 0 | 0.0005 | 40956.9632 | 13242.7906
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74708400000 | 53895.264 | 02-JAN-16:40 | 32837.857 | 8089.532 | 7898.875 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66868400000 | 53895.264 | 01-FEB-17:19 | 32837.857 | 8089.532 | 7898.875 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74481000000 | 53895.264 | 01-MAR-17:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 69856800000 | 53808.865 | 14-APR-15:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 4982.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 77638100000 | 88605.609 | 27-MAY-14:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 39779.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 86384700000 | 89561.347 | 29-JUN-14:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 40735.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 93155500000 | 93650.883 | 15-JUL-14:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 44824.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 95037500000 | 89674.86 | 25-AUG-15:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 40848.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 74054300000 | 75376.396 | 14-SEP-14:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 26550.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 73316900000 | 65260.617 | 07-OCT-14:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 16434.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71218600000 | 53895.264 | 01-NOV-16:00 | 32837.857 | 8089.532 | 7898.875 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74325900000 | 53895.264 | 01-DEC-16:30 | 32837.857 | 8089.532 | 7898.875 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 931046000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66868400000 | 53808.865 |  | 32837.857 | 8089.532 | 7898.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 95037500000 | 93650.883 |  | 32837.857 | 8089.532 | 7898.875 | 0 | 44824.619 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 16074.82 | 11113.95 | 0 | 27188.77
Cost per Total Building Area ($/m2) | 7.69 | 5.32 | 0 | 13.01
Cost per Net Conditioned Building Area ($/m2) | 7.69 | 5.32 | 0 | 13.01

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2116.19 | 1012.38 | 1012.38
Net Site Energy | 2116.19 | 1012.38 | 1012.38
Total Source Energy | 4422.48 | 2115.69 | 2115.69
Net Source Energy | 4422.48 | 2115.69 | 2115.69
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1230.45 | 0 | 0 | 0 | 0
Cooling | 28.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 150.46 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 885.74 | 1230.45 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.477 | 0.514 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.351 | 0.376 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12826.31 | 10096.41 | 2729.9 | 0.79 | 4
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21300.95 | 17012.11 | 4288.83 | 0.8 | 3.77
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10166.04 | 8119.16 | 2046.88 | 0.8 | 4.04
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9148.19 | 7258.82 | 1889.38 | 0.79 | 4.02
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 9043.24 | 7167.41 | 1875.83 | 0.79 | 4.01
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8982.42 | 7114.48 | 1867.95 | 0.79 | 4.01
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17278.45 | 13523.57 | 3754.88 | 0.78 | 3.96
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8725 | 6849.46 | 1875.54 | 0.79 | 3.99
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8722.82 | 6845.34 | 1877.48 | 0.78 | 3.99
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 8807.2 | 6914.71 | 1892.49 | 0.79 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28381.86 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 51651.97 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23601.1 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23522.01 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23518.56 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23534.82 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46738.18 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23535.17 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23524.76 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23632.86 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.75 | 870.65 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.29 | 1465.9 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.61 | 712.33 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 631.97 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 623.17 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.53 | 618.08 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1137.43 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.51 | 588.72 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.51 | 588.11 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.51 | 594.4 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 30962.4445 | 43.3443 | 55.2547 | 0 | 0.0004 | 1309190 | 12189.2614
February | 26051.5086 | 37.321 | 49.5703 | 0 | 0.0004 | 1174720 | 10338.2395
March | 24499.3686 | 37.4732 | 55.2087 | 0 | 0.0004 | 1308890 | 9951.9367
April | 21147.1126 | 33.4381 | 51.6052 | 0 | 0.0004 | 1223670 | 8695.8077
May | 19529.5762 | 32.4768 | 53.4313 | 0 | 0.0004 | 1267260 | 8184.9808
June | 18693.3117 | 32.3769 | 55.8111 | 0 | 0.0004 | 1323910 | 7959.2588
July | 19357.4698 | 34.2285 | 60.3303 | 0 | 0.0004 | 1431220 | 8309.8369
August | 19516.726 | 34.3242 | 60.1543 | 0 | 0.0004 | 1427020 | 8360.2311
September | 18637.7838 | 31.8083 | 53.9371 | 0 | 0.0004 | 1279390 | 7889.9572
October | 21082.9272 | 34.0519 | 54.0354 | 0 | 0.0004 | 1281420 | 8738.5551
November | 23984.7815 | 36.3478 | 52.8257 | 0 | 0.0004 | 1252330 | 9710.206
December | 29766.0911 | 42.2219 | 55.1172 | 0 | 0.0004 | 1306070 | 11771.6721
Annual Sum or Average | 273229.1015 | 429.4129 | 657.2814 | 0 | 0.0047 | 15585100 | 112099.9431
Minimum of Months | 18637.7838 | 31.8083 | 49.5703 | 0 | 0.0004 | 1174720 | 7889.9572
Maximum of Months | 30962.4445 | 43.3443 | 60.3303 | 0 | 0.0004 | 1431220 | 12189.2614
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 74404500000 | 53827.158 | 02-JAN-16:49 | 32837.857 | 8089.532 | 7830.769 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66762000000 | 53827.158 | 01-FEB-17:30 | 32837.857 | 8089.532 | 7830.769 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74387200000 | 51057.523 | 30-MAR-15:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 2299.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 69544200000 | 48997.699 | 06-APR-15:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 239.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 72021400000 | 58676.927 | 16-MAY-16:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 9918.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 75241100000 | 73965.04 | 30-JUN-14:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 25206.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 81339600000 | 74622.175 | 21-JUL-16:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 25864.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 81100700000 | 71121.894 | 09-AUG-16:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 22363.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 72710700000 | 66198.864 | 01-SEP-16:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 17440.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 72826400000 | 55686.911 | 06-OCT-15:00 | 32837.857 | 8089.532 | 7830.769 | 0 | 6928.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71172700000 | 53827.158 | 06-NOV-17:10 | 32837.857 | 8089.532 | 7830.769 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 74227100000 | 53827.158 | 01-DEC-16:40 | 32837.857 | 8089.532 | 7830.769 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 885738000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66762000000 | 48997.699 |  | 32837.857 | 8089.532 | 7830.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 81339600000 | 74622.175 |  | 32837.857 | 8089.532 | 7830.769 | 0 | 25864.016 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18541.22 | 9995.31 | 0 | 28536.53
Cost per Total Building Area ($/m2) | 8.87 | 4.78 | 0 | 13.65
Cost per Net Conditioned Building Area ($/m2) | 8.87 | 4.78 | 0 | 13.65

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2636.17 | 1261.13 | 1261.13
Net Site Energy | 2636.17 | 1261.13 | 1261.13
Total Source Energy | 4919.03 | 2353.24 | 2353.24
Net Source Energy | 4919.03 | 2353.24 | 2353.24
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1766.09 | 0 | 0 | 0 | 0
Cooling | 21.08 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.52 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 142.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 870.08 | 1766.09 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.358 | 0.384 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 3.241 | 0.487 | 0.409 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 3.241 | 0.487 | 0.409 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 3.241 | 0.487 | 0.409 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.24 | 0.487 | 0.409
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.24 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17596.59 | 11896.76 | 5699.83 | 0.68 | 3.65
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28705.83 | 19604.84 | 9100.99 | 0.68 | 3.46
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13518.7 | 9141.33 | 4377.37 | 0.68 | 3.65
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12188.73 | 8240.6 | 3948.14 | 0.68 | 3.65
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12185.44 | 8238.37 | 3947.07 | 0.68 | 3.65
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12203.27 | 8250.42 | 3952.84 | 0.68 | 3.65
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24043.11 | 16255.15 | 7787.97 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12203.59 | 8250.65 | 3952.95 | 0.68 | 3.65
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12191.25 | 8242.3 | 3948.95 | 0.68 | 3.65
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12291.56 | 8310.12 | 3981.44 | 0.68 | 3.65
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30695.25 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 56391.24 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26005.98 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25937.53 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25934.64 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25950.32 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 51581.01 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25950.61 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25939.75 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26027.98 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.71 | 821.93 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.19 | 1353.82 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.54 | 631.75 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 569.33 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 569.18 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 570.01 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1102.99 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 570.02 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 569.45 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.49 | 574.13 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 34476.7846 | 46.156 | 48.5494 | 0 | 0.0004 | 31851.9435 | 13353.0072
February | 29493.3435 | 40.1191 | 43.5986 | 0 | 0.0003 | 28608.787 | 11483.5684
March | 28412.9466 | 40.624 | 48.4311 | 0 | 0.0004 | 31794.5887 | 11251.6506
April | 21805.0977 | 33.6186 | 45.1202 | 0 | 0.0003 | 29636.8148 | 8868.3634
May | 18899.1137 | 31.405 | 46.4879 | 0 | 0.0003 | 30547.2526 | 7903.1401
June | 16542.6447 | 29.4155 | 46.9637 | 0 | 0.0003 | 30868.5553 | 7101.8492
July | 17691.3408 | 32.0332 | 52.0978 | 0 | 0.0004 | 34245.3175 | 7649.9725
August | 18002.5519 | 32.1925 | 51.6981 | 0 | 0.0004 | 33981.0439 | 7745.9064
September | 17664.7521 | 30.1077 | 45.9065 | 0 | 0.0003 | 30168.5643 | 7459.0238
October | 21140.9234 | 33.6753 | 47.2649 | 0 | 0.0004 | 31051.273 | 8701.5392
November | 25770.866 | 37.59 | 46.3485 | 0 | 0.0004 | 30432.1687 | 10276.4424
December | 32833.9479 | 44.6303 | 48.4297 | 0 | 0.0004 | 31778.6687 | 12781.1262
Annual Sum or Average | 282734.3129 | 431.5672 | 570.8964 | 0 | 0.0044 | 374964.9782 | 114575.5895
Minimum of Months | 16542.6447 | 29.4155 | 43.5986 | 0 | 0.0003 | 28608.787 | 7101.8492
Maximum of Months | 34476.7846 | 46.156 | 52.0978 | 0 | 0.0004 | 34245.3175 | 13353.0072
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73910000000 | 53328.989 | 02-JAN-16:30 | 32837.857 | 8089.532 | 7332.6 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 66384500000 | 53328.989 | 01-FEB-17:10 | 32837.857 | 8089.532 | 7332.6 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 73776900000 | 53328.989 | 01-MAR-17:49 | 32837.857 | 8089.532 | 7332.6 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 68770000000 | 48259.989 | 01-APR-09:09 | 32837.857 | 8089.532 | 7332.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 70882600000 | 57207.026 | 31-MAY-15:00 | 32837.857 | 8089.532 | 7332.6 | 0 | 8947.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 71628200000 | 71896.65 | 14-JUN-14:00 | 32837.857 | 8089.532 | 7332.6 | 0 | 23636.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 79463700000 | 82053.777 | 08-JUL-15:50 | 32837.857 | 8089.532 | 7332.6 | 0 | 33793.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 78850500000 | 81622.096 | 12-AUG-14:00 | 32837.857 | 8089.532 | 7332.6 | 0 | 33362.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 70003900000 | 65802.618 | 07-SEP-14:00 | 32837.857 | 8089.532 | 7332.6 | 0 | 17542.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 72052100000 | 61141.992 | 07-OCT-14:00 | 32837.857 | 8089.532 | 7332.6 | 0 | 12882.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 70615600000 | 53328.989 | 01-NOV-16:49 | 32837.857 | 8089.532 | 7332.6 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73740000000 | 53328.989 | 01-DEC-16:19 | 32837.857 | 8089.532 | 7332.6 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 870078000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 66384500000 | 48259.989 |  | 32837.857 | 8089.532 | 7332.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 79463700000 | 82053.777 |  | 32837.857 | 8089.532 | 7332.6 | 0 | 33793.788 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14728.57 | 13878.36 | 0 | 28606.92
Cost per Total Building Area ($/m2) | 7.05 | 6.64 | 0 | 13.69
Cost per Net Conditioned Building Area ($/m2) | 7.05 | 6.64 | 0 | 13.69

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3710.99 | 1775.32 | 1775.32
Net Site Energy | 3710.99 | 1775.32 | 1775.32
Total Source Energy | 6269.43 | 2999.27 | 2999.27
Net Source Energy | 6269.43 | 2999.27 | 2999.27
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2817.03 | 0 | 0 | 0 | 0
Cooling | 6.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 477.81 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 79.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 181.6 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 893.96 | 2817.03 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 23.99 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 13.77 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 23.99 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 18.29 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 13.77 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 13.77 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 17.455 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.363 | 0.384 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.269 | 0.283 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 2.615 | 0.702 | 0.633 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 2.615 | 0.702 | 0.633 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.9 | 3.9 | 2.615 | 0.702 | 0.633 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-90.1-2004-NONRES-FIXED | 3.88 | 3.88 | 2.615 | 0.702 | 0.633 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-90.1-2004-NONRES-FIXED | 3.24 | 3.24 | 2.615 | 0.702 | 0.633 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 2.61 | 0.702 | 0.633
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 2.61 | 0.702 | 0.633
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14918.06 | 11914.38 | 3003.67 | 0.8 | 4.01
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24959.69 | 19934.19 | 5025.5 | 0.8 | 3.77
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10297.61 | 8224.24 | 2073.37 | 0.8 | 4.04
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10237.84 | 8176.51 | 2061.34 | 0.8 | 4.04
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10235.34 | 8174.51 | 2060.83 | 0.8 | 4.04
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10248.55 | 8185.06 | 2063.49 | 0.8 | 4.04
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20234.8 | 16160.63 | 4074.17 | 0.8 | 3.77
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10248.8 | 8185.26 | 2063.54 | 0.8 | 4.04
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10239.83 | 8178.09 | 2061.74 | 0.8 | 4.04
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 10319.23 | 8241.5 | 2077.72 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40404.33 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 74142.42 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34088.12 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34006.44 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34003.03 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34021.08 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 67683.75 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34021.42 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34009.15 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34117.66 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1026.64 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.51 | 1717.69 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 721.55 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 717.37 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 717.19 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 718.12 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.22 | 1392.53 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 718.13 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 717.5 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.62 | 723.07 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43199.5401 | 44.6366 | 113.5525 | 0 | 0.0004 | 22762.417 | 15785.7195
February | 36916.7212 | 38.3082 | 100.4563 | 0 | 0.0004 | 20138.5327 | 13515.0345
March | 32876.5735 | 35.0778 | 109.5891 | 0 | 0.0004 | 21977.0442 | 12183.9993
April | 23729.5338 | 26.3392 | 100.4577 | 0 | 0.0004 | 20152.4491 | 8951.2294
May | 17382.2116 | 20.6259 | 101.4546 | 0 | 0.0003 | 20359.2205 | 6761.8832
June | 15035.585 | 18.4221 | 99.9076 | 0 | 0.0003 | 20050.9417 | 5938.3851
July | 15127.5727 | 18.68 | 103.5554 | 0 | 0.0004 | 20783.5081 | 5997.0518
August | 16394.733 | 19.9287 | 105.6199 | 0 | 0.0004 | 21196.8382 | 6450.775
September | 18855.0664 | 21.9742 | 101.6943 | 0 | 0.0004 | 20405.8429 | 7273.3713
October | 26306.8858 | 28.9998 | 107.1808 | 0 | 0.0004 | 21500.1154 | 9892.6501
November | 35255.1433 | 37.1436 | 107.6441 | 0 | 0.0004 | 21583.9145 | 12992.8664
December | 40725.3189 | 42.3982 | 113.7044 | 0 | 0.0004 | 22795.4817 | 14930.5595
Annual Sum or Average | 321804.8852 | 352.5342 | 1264.8167 | 0 | 0.0046 | 253706.3058 | 120673.5252
Minimum of Months | 15035.585 | 18.4221 | 99.9076 | 0 | 0.0003 | 20050.9417 | 5938.3851
Maximum of Months | 43199.5401 | 44.6366 | 113.7044 | 0 | 0.0004 | 22795.4817 | 15785.7195
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 80205800000 | 55166.187 | 02-JAN-09:09 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 70960300000 | 55166.187 | 01-FEB-09:09 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 77438500000 | 55166.187 | 01-MAR-17:00 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 71009300000 | 50097.187 | 01-APR-09:09 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 71737900000 | 53673.037 | 24-MAY-14:00 | 32837.857 | 8089.532 | 9169.798 | 0 | 3575.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 70651700000 | 63083.632 | 20-JUN-15:00 | 32837.857 | 8089.532 | 9169.798 | 0 | 12986.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 73232900000 | 67575.822 | 29-JUL-15:00 | 32837.857 | 8089.532 | 9169.798 | 0 | 17478.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 74689400000 | 62707.67 | 15-AUG-14:50 | 32837.857 | 8089.532 | 9169.798 | 0 | 12610.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 71902200000 | 50097.187 | 01-SEP-08:09 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 75758000000 | 55166.187 | 23-OCT-08:09 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 76053300000 | 55166.187 | 01-NOV-08:09 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 80322300000 | 55166.187 | 01-DEC-09:09 | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 893962000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 70651700000 | 50097.187 |  | 32837.857 | 8089.532 | 9169.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 80322300000 | 67575.822 |  | 32837.857 | 8089.532 | 9169.798 | 0 | 17478.635 | 5069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 24131.37 | 11633.46 | 0 | 35764.83
Cost per Total Building Area ($/m2) | 11.54 | 5.57 | 0 | 17.11
Cost per Net Conditioned Building Area ($/m2) | 11.54 | 5.57 | 0 | 17.11

## Picture
DOE Commercial Building Benchmark - Strip Mall

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0