## BuildingSummary
Building Summary Hospital post-1980 construction
|  | Value | Data Source
Program
| Building Name | Hospital
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, inpatient
Form
| Total Floor Area (m2) | 22422.1768 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3142
| Number of Floors | 5 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.1334
| East | 0.121
| North | 0.117
| West | 0.2315
| Total | 0.1461
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures and zone summary
| Floor to Ceiling Height (m) | 4.27
| Floor to Floor Height (m) | 4.27
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 5184.32
| Net Dimensions - Total Area (m2) | 4338.78
| Wall to Skin Ratio | 0.41902
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3739.134
| Net Dimensions - Total Area (m2) | 3739.134
| Roof to Skin Ratio | 0.58098
Window Dimensions (m2)
| South | 220.72
| East | 144.86
| North | 186.18
| West | 293.66
| Total Area (m2) | 845.42
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab
| Dimensions - Total Area (m2) | 3739.134
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15534.17
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 44872.35
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.26534 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Boiler | 2003 CBECS
| Cooling Type | Chiller, water cooled | 2003 CBECS
| Fan Control | CAV, VAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 4037.61

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 19.375 | 8.0729 |  |  | 10 |  | 1006.2497 |  | 0
ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
ER_Trauma1_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.66938
ER_Trauma2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
ER_Triage_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1.0503 | 25.7922 | 11.8403 |  |  | 10 |  | 10.5034 |  | 0.89241
Lobby_Records_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.7804 | 62.6301 | 13.0064 | 113.3908 | 15.7328 | 1.0764 |  |  | 10 |  | 1133.9077 |  | 0.26568
Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  |  | 0.25 | 1349.325 |  | 0.15304
ER_NurseStn_Lobby_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.5801 | 30.42 | 14.8645 | 83.1249 | 17.8959 | 14.6389 |  |  |  |  | 2929.9675 |  | 0.085575
OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.0501 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 1.1159
OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.44637
OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.66955
OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 84.9091 | 53.8195 |  | 22.7124 |  |  | 793.0838 |  | 0
IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 41.3698 | 32.2917 |  |  |  |  | 66.0874 |  | 1.5621
IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.6802 | 25.03 | 4.6452 | 133.0332 | 41.3698 | 32.2917 |  |  |  |  | 1465.3513 |  | 0.33219
ICU_NurseStn_Lobby_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 18.4588 | 21.5278 |  |  | 10 |  | 1585.8356 |  | 0
Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  | 10 | 0.25 | 1349.325 |  | 0.15304
OR_NurseStn_Lobby_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.1402 | 35.76 | 13.0064 | 77.8568 | 15.6644 | 11.1945 |  |  | 10 |  | 2401.245 |  | 0.17199
PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 26.9378 | 16.1458 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
NurseStn_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 23.8269 | 107.639 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
NurseStn_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.6702 | 35.76 | 9.2903 | 74.9999 | 27.7331 | 10.7639 |  |  | 10 |  | 749.9993 |  | 0.31244
NurseStn_Lobby_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.0801 | 0 | 13.0064 | 79.9999 | 15.6443 | 11.1945 |  |  | 10 |  | 2467.3419 |  | 0.095647
Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2002 | 0 | 18.5806 | 49.9999 | 15.2932 | 80.7294 | 304.9413 | 567.81 | 15 |  | 2202.9829 | 2501.3191 | 0.26781
Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.5601 | 17.98 | 13.2719 | 5.2517 | 25.7922 | 10.7639 |  |  | 10 |  | 52.5171 |  | 0.98173
Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.44627
Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.5501 | 17.98 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.98187
Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1 | 25.7922 | 10.7639 |  |  | 10 |  | 10 |  | 0.89241
Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.0601 | 0 | 92.9031 | 5.4 | 14.6034 | 0 |  |  |  | 0.25 | 125.42 |  | 0.14878
Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 1291.1824 |  |  |  | 1052.3412
Data Source | [7 empty] | 1 |  | 2 | 5, 6 | 5, 6 | 5, 6 | 3, 4 | 3, 4 | 3, 4 | 5 | 5
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] DOE Benchmark Report
[6] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
| R-value (m2·K / W) | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 3247.6451 | 3194.2306 | 2926.2883 | 2958.3517 | 2586.1675 | 2537.6329 | 2161.9782 | 2953.5117 | 2120.3054 | 2214.7201 | 2910.0748 | 2073.1414 | 2791.6536 | 1968.8933 | 2466.7644 | 1973.6
Heating (kW)
| HEATSYS1 BOILER | 3285.6656 | 3455.0864 | 3441.1008 | 3445.7953 | 3291.824 | 3331.2891 | 3194.5554 | 3558.0221 | 3148.8197 | 3417.8574 | 3729.7323 | 3271.8645 | 3813.3537 | 3536.3053 | 3817.562 | 4313.5552
HVAC Efficiency
| Air Conditioning (COP) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
| Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
HVAC Control - Economizer
| CAV_1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| CAV_2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CAV_1_FAN | 17.08 | 17.09 | 18.93 | 16.79 | 17.38 | 18.06 | 16.6 | 16.58 | 17.51 | 16.83 | 16.81 | 17.14 | 16.7 | 16.88 | 17.11 | 18.22
| CAV_2_FAN | 15.89 | 15.74 | 17.12 | 16.06 | 15.35 | 17.03 | 14.9 | 15.5 | 17.89 | 15.42 | 15.58 | 17.7 | 15.62 | 16.89 | 15.72 | 15.34
| VAV_1_FAN | 29.67 | 29.42 | 29.8 | 29.11 | 28.82 | 28.95 | 25.39 | 27.63 | 29.95 | 25.91 | 27.73 | 29.33 | 27.47 | 27.93 | 26.29 | 24.95
| VAV_2_FAN | 46.61 | 46.47 | 47.57 | 47.08 | 46.74 | 47.11 | 44.4 | 44.52 | 48.45 | 44.16 | 44.37 | 46.91 | 43.46 | 45.39 | 43.22 | 42.34
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.07506 | 0.097127 | 0.067328 | 0.096326 | 0.043921 | 0.08698 | 0.13011 | 0.055144 | 0.036954 | 0.065588 | 0.098243 | 0.036954 | 0.051467 | 0.068989 | 0.051533 | 0.08717
| Total Cost ($/m2) | 29.56 | 36.3 | 24.32 | 33.65 | 14.66 | 30.77 | 39.58 | 18.86 | 12.28 | 20.07 | 32.41 | 12 | 16.88 | 21.85 | 16.4 | 27.57
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011443 | 0.0081705 | 0.0085511 | 0.010657 | 0.0084143 | 0.0080888 | 0.0084157 | 0.010074 | 0.0071657 | 0.0082892 | 0.0088867 | 0.0071683 | 0.0079742 | 0.0086835 | 0.00797 | 0.0041745
| Total Cost ($/m2) | 5.46 | 4.59 | 4.84 | 6.45 | 5.15 | 4.48 | 5.54 | 6.5 | 3.65 | 5.54 | 6.11 | 3.88 | 5.82 | 5.34 | 6.26 | 4.62
Total Utility Costs
| Cost Intensity ($/m2) | 35.02 | 40.89 | 29.16 | 40.1 | 19.81 | 35.25 | 45.11 | 25.36 | 15.93 | 25.61 | 38.52 | 15.88 | 22.7 | 27.19 | 22.66 | 32.19
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 2335141.6667 | 1868441.6667 | 1323880.5556 | 1285777.7778 | 1121077.7778 | 969816.6667 | 647219.4444 | 1061555.5556 | 657452.7778 | 563805.5556 | 779847.2222 | 519097.2222 | 699955.5556 | 415469.4444 | 438419.4444 | 288844.4444
| Interior Lighting | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667
| Exterior Lighting | 30086.1111 | 30033.3333 | 30025 | 30075 | 30069.4444 | 30041.6667 | 30008.3333 | 30038.8889 | 30033.3333 | 29988.8889 | 29997.2222 | 30002.7778 | 30022.2222 | 29986.1111 | 29977.7778 | 29797.2222
| Interior Equipment | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444
| Exterior Equipment | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667
| Fans | 709208.3333 | 693977.7778 | 764858.3333 | 688413.8889 | 689258.3333 | 744383.3333 | 654758.3333 | 664719.4444 | 743930.5556 | 666963.8889 | 670477.7778 | 723813.8889 | 670500 | 697958.3333 | 679683.3333 | 701002.7778
| Pumps | 496786.1111 | 471866.6667 | 420563.8889 | 422783.3333 | 381058.3333 | 361566.6667 | 304613.8889 | 410322.2222 | 299047.2222 | 305519.4444 | 387219.4444 | 281627.7778 | 353841.6667 | 255716.6667 | 296319.4444 | 196950
| Heat Rejection | 356086.1111 | 334994.4444 | 312016.6667 | 288408.3333 | 282936.1111 | 251763.8889 | 234769.4444 | 250486.1111 | 174286.1111 | 219144.4444 | 205772.2222 | 151638.8889 | 182983.3333 | 131616.6667 | 141047.2222 | 93247.2222
| Humidification | 7083.3333 | 86850 | 355888.8889 | 225908.3333 | 89550 | 682147.2222 | 59791.6667 | 361050 | 656863.8889 | 186916.6667 | 435702.7778 | 684566.6667 | 527336.1111 | 682997.2222 | 663702.7778 | 896166.6667
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 57152.7778 | 54941.6667 | 55308.3333 | 52866.6667 | 53091.6667 | 53347.2222 | 51597.2222 | 51622.2222 | 51461.1111 | 50588.8889 | 50627.7778 | 50427.7778 | 50152.7778 | 49455.5556 | 48788.8889 | 47880.5556
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas (MJ)
| Heating | 8873200 | 10688630 | 10816840 | 11566730 | 11740280 | 10486960 | 12678750 | 12386360 | 9350490 | 12880460 | 13265260 | 9996420 | 14168340 | 11591360 | 15329100 | 22409780
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 468230 | 561660 | 507910 | 651710 | 634220 | 572650 | 711280 | 722460 | 709040 | 759300 | 784570 | 781340 | 838260 | 848000 | 926780 | 1033940
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 42485680 | 42772970 | 41844600 | 41772370 | 40678540 | 40969350 | 39302640 | 42070770 | 38241290 | 39696990 | 42039240 | 38340670 | 42834540 | 39361560 | 43303150 | 50332430
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 374.9184 | 299.9874 | 212.5555 | 206.4379 | 179.9945 | 155.7088 | 103.9142 | 170.4379 | 105.5573 | 90.5217 | 125.2083 | 83.3436 | 112.3813 | 66.7056 | 70.3904 | 46.3754
| Interior Lighting (elec) | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135
| Exterior Lighting (elec) | 4.8305 | 4.822 | 4.8207 | 4.8287 | 4.8278 | 4.8233 | 4.818 | 4.8229 | 4.822 | 4.8149 | 4.8162 | 4.8171 | 4.8202 | 4.8144 | 4.8131 | 4.7841
| Interior Equipment (elec) | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554
| Exterior Equipment (elec) | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719
| Fans (elec) | 113.8669 | 111.4215 | 122.8017 | 110.5282 | 110.6638 | 119.5144 | 105.1246 | 106.7239 | 119.4417 | 107.0843 | 107.6485 | 116.2119 | 107.652 | 112.0606 | 109.1265 | 112.5494
| Pumps (elec) | 79.7614 | 75.7605 | 67.5236 | 67.8799 | 61.1808 | 58.0513 | 48.9072 | 65.8792 | 48.0135 | 49.0526 | 62.17 | 45.2167 | 56.811 | 41.0566 | 47.5755 | 31.6213
| Heat Rejection (elec) | 57.1714 | 53.785 | 50.0958 | 46.3054 | 45.4268 | 40.4219 | 37.6934 | 40.2168 | 27.9825 | 35.1847 | 33.0377 | 24.3464 | 29.3789 | 21.1317 | 22.6458 | 14.9713
| Humidification (elec) | 1.1373 | 13.9442 | 57.1397 | 36.2707 | 14.3777 | 109.5221 | 9.5998 | 57.9683 | 105.4627 | 30.0104 | 69.9542 | 109.9105 | 84.6664 | 109.6585 | 106.5607 | 143.8839
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 9.1762 | 8.8212 | 8.88 | 8.488 | 8.5241 | 8.5652 | 8.2842 | 8.2882 | 8.2623 | 8.1223 | 8.1285 | 8.0964 | 8.0523 | 7.9403 | 7.8333 | 7.6875
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas (MJ/m2)
| Heating (gas) | 395.7321 | 476.6977 | 482.4157 | 515.8597 | 523.5998 | 467.7035 | 565.4542 | 552.414 | 417.0185 | 574.4502 | 591.6117 | 445.8261 | 631.8878 | 516.9582 | 683.656 | 999.4443
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.8824 | 25.0492 | 22.6521 | 29.0653 | 28.2853 | 25.5394 | 31.7221 | 32.2207 | 31.6222 | 33.8637 | 34.9907 | 34.8467 | 37.3852 | 37.8196 | 41.3331 | 46.1123
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1894.8009 | 1907.6136 | 1866.2096 | 1862.9883 | 1814.205 | 1827.1747 | 1752.8418 | 1876.2965 | 1705.5071 | 1770.4293 | 1874.8903 | 1709.9393 | 1910.3595 | 1755.4696 | 1931.2589 | 2244.7548
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1442.0067 | 1391.7174 | 1368.2576 | 1295.276 | 1332.3278 | 1339.3072 | 1237.6552 | 1300.2538 | 1296.9453 | 1220.1272 | 1228.254 | 1293.1548 | 1220.1095 | 1214.2732 | 1223.1539 | 1216.1915
| Feb | 1446.4952 | 1347.293 | 1409.2988 | 1306.3493 | 1292.4258 | 1340.5426 | 1229.0329 | 1258.1054 | 1334.7377 | 1230.9274 | 1210.4135 | 1278.7352 | 1221.7042 | 1255.6291 | 1224.2604 | 1221.459
| Mar | 1462.3518 | 1383.4389 | 1461.1633 | 1353.8375 | 1350.5158 | 1366.2909 | 1219.9188 | 1311.2203 | 1359.1053 | 1234.4077 | 1255.9915 | 1370.2306 | 1251.5694 | 1295.4065 | 1227.3294 | 1218.4903
| Apr | 1482.4908 | 1421.5546 | 1439.7689 | 1341.0909 | 1415.1612 | 1367.3421 | 1268.5411 | 1305.2932 | 1421.2945 | 1229.1 | 1299.6672 | 1321.4664 | 1258.1289 | 1298.6481 | 1248.8318 | 1237.1659
| May | 1564.2545 | 1556.7763 | 1482.2418 | 1428.0004 | 1338.9533 | 1484.921 | 1264.9511 | 1419.0864 | 1413.581 | 1266.2881 | 1367.9628 | 1353.449 | 1332.6022 | 1308.4449 | 1300.9945 | 1311.621
| Jun | 1620.4793 | 1545.3971 | 1547.3008 | 1484.892 | 1363.4258 | 1509.2886 | 1254.5325 | 1535.7956 | 1450.5669 | 1269.2416 | 1503.8267 | 1414.3401 | 1462.5405 | 1353.6663 | 1372.8167 | 1328.8132
| Jul | 1600.4739 | 1620.6622 | 1517.6969 | 1513.6078 | 1364.5032 | 1466.0836 | 1276.2322 | 1546.1543 | 1428.8108 | 1309.1952 | 1491.4334 | 1369.1943 | 1517.7238 | 1357.5213 | 1418.0236 | 1289.6354
| Aug | 1575.7068 | 1584.8302 | 1526.9552 | 1510.5556 | 1407.0278 | 1448.7431 | 1267.9608 | 1606.306 | 1352.4042 | 1307.342 | 1562.4317 | 1372.9442 | 1505.0785 | 1345.7188 | 1391.7715 | 1272.915
| Sep | 1560.2311 | 1599.8375 | 1465.1617 | 1458.1685 | 1393.0232 | 1452.803 | 1312.0818 | 1398.4666 | 1387.16 | 1308.4574 | 1416.0228 | 1399.787 | 1377.2895 | 1288.2657 | 1373.1013 | 1224.8076
| Oct | 1559.2815 | 1479.3941 | 1421.6306 | 1366.2539 | 1369.0818 | 1397.6822 | 1252.7691 | 1358.958 | 1348.4061 | 1234.1154 | 1329.0356 | 1365.2389 | 1238.1216 | 1295.9318 | 1238.7892 | 1213.7163
| Nov | 1486.9943 | 1433.3064 | 1390.1839 | 1315.3629 | 1308.2591 | 1326.3769 | 1217.8144 | 1308.7585 | 1308.033 | 1211.0558 | 1343.2875 | 1325.7348 | 1256.9391 | 1238.604 | 1246.1537 | 1211.6313
| Dec | 1455.1415 | 1384.7085 | 1403.7636 | 1299.0669 | 1331.5685 | 1339.0489 | 1230.3989 | 1273.1035 | 1268.0122 | 1175.3359 | 1211.1633 | 1275.8409 | 1222.3246 | 1220.6459 | 1214.8491 | 1216.9163
Time of Peak Electrical Demand
| Jan | 06-JAN-17:45 | 03-JAN-11:45 | 26-JAN-16:15 | 26-JAN-16:00 | 26-JAN-14:15 | 30-JAN-16:00 | 20-JAN-14:00 | 05-JAN-16:15 | 20-JAN-16:15 | 03-JAN-17:00 | 26-JAN-16:00 | 24-JAN-16:15 | 03-JAN-17:00 | 10-JAN-17:45 | 12-JAN-17:00 | 25-JAN-16:15
| Feb | 23-FEB-11:45 | 15-FEB-16:15 | 28-FEB-17:00 | 06-FEB-16:15 | 10-FEB-10:00 | 17-FEB-17:30 | 15-FEB-16:30 | 16-FEB-16:15 | 13-FEB-16:30 | 22-FEB-11:45 | 09-FEB-17:15 | 07-FEB-14:00 | 08-FEB-17:00 | 03-FEB-17:30 | 15-FEB-17:00 | 28-FEB-17:00
| Mar | 14-MAR-10:45 | 24-MAR-16:30 | 30-MAR-15:00 | 22-MAR-16:00 | 31-MAR-15:00 | 21-MAR-15:00 | 13-MAR-12:00 | 17-MAR-16:00 | 02-MAR-16:15 | 23-MAR-15:00 | 31-MAR-16:45 | 30-MAR-15:15 | 31-MAR-15:00 | 29-MAR-16:00 | 03-MAR-17:00 | 22-MAR-15:15
| Apr | 04-APR-16:00 | 20-APR-15:15 | 26-APR-16:00 | 14-APR-16:00 | 11-APR-16:00 | 12-APR-16:00 | 13-APR-15:00 | 20-APR-15:00 | 21-APR-16:00 | 14-APR-16:00 | 27-APR-16:00 | 27-APR-12:00 | 06-APR-16:00 | 06-APR-16:00 | 27-APR-15:15 | 21-APR-16:00
| May | 19-MAY-15:15 | 18-MAY-16:00 | 19-MAY-16:00 | 31-MAY-16:00 | 31-MAY-15:15 | 11-MAY-15:00 | 25-MAY-15:30 | 31-MAY-15:00 | 12-MAY-16:00 | 05-MAY-15:00 | 30-MAY-16:00 | 19-MAY-16:00 | 31-MAY-16:00 | 04-MAY-16:00 | 12-MAY-16:00 | 24-MAY-15:15
| Jun | 27-JUN-15:00 | 29-JUN-16:30 | 08-JUN-15:00 | 08-JUN-15:00 | 23-JUN-16:30 | 29-JUN-15:00 | 16-JUN-15:45 | 30-JUN-16:00 | 27-JUN-16:00 | 27-JUN-16:00 | 08-JUN-12:00 | 15-JUN-16:00 | 29-JUN-16:00 | 30-JUN-15:00 | 14-JUN-15:15 | 15-JUN-16:00
| Jul | 13-JUL-15:45 | 18-JUL-12:30 | 11-JUL-16:15 | 25-JUL-16:15 | 26-JUL-16:00 | 31-JUL-16:00 | 03-JUL-12:00 | 25-JUL-10:45 | 31-JUL-16:00 | 27-JUL-16:00 | 14-JUL-10:45 | 12-JUL-16:00 | 13-JUL-16:00 | 21-JUL-16:00 | 12-JUL-08:30 | 20-JUL-16:00
| Aug | 21-AUG-15:15 | 03-AUG-15:15 | 11-AUG-16:00 | 17-AUG-15:15 | 08-AUG-16:30 | 02-AUG-16:00 | 15-AUG-12:15 | 09-AUG-16:00 | 01-AUG-16:00 | 18-AUG-16:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-16:15 | 18-AUG-16:45
| Sep | 12-SEP-15:00 | 15-SEP-15:15 | 08-SEP-15:00 | 01-SEP-15:45 | 01-SEP-15:00 | 21-SEP-16:00 | 28-SEP-15:00 | 27-SEP-15:15 | 20-SEP-16:00 | 01-SEP-16:15 | 07-SEP-16:00 | 13-SEP-15:00 | 22-SEP-13:15 | 01-SEP-16:00 | 08-SEP-16:00 | 07-SEP-15:00
| Oct | 06-OCT-15:00 | 30-OCT-15:15 | 03-OCT-09:30 | 20-OCT-16:00 | 19-OCT-15:45 | 31-OCT-15:00 | 13-OCT-15:00 | 03-OCT-10:45 | 13-OCT-15:15 | 17-OCT-16:00 | 31-OCT-09:00 | 05-OCT-15:00 | 25-OCT-15:15 | 19-OCT-16:00 | 25-OCT-15:15 | 27-OCT-16:45
| Nov | 01-NOV-15:00 | 27-NOV-17:00 | 15-NOV-16:00 | 03-NOV-15:15 | 29-NOV-11:45 | 22-NOV-16:30 | 16-NOV-16:15 | 03-NOV-13:00 | 13-NOV-17:00 | 28-NOV-17:00 | 02-NOV-09:30 | 10-NOV-13:00 | 01-NOV-15:15 | 21-NOV-11:45 | 03-NOV-16:00 | 29-NOV-17:30
| Dec | 15-DEC-17:30 | 06-DEC-17:30 | 06-DEC-16:00 | 28-DEC-14:00 | 18-DEC-11:45 | 05-DEC-16:30 | 29-DEC-16:00 | 06-DEC-16:00 | 05-DEC-16:15 | 07-DEC-17:00 | 05-DEC-16:00 | 29-DEC-14:00 | 20-DEC-16:30 | 12-DEC-16:45 | 21-DEC-16:30 | 13-DEC-17:00
Source Energy
| Total Source Energy (GJ) | 117117.84 | 123325.29 | 106087.63 | 109675.63 | 98393.04 | 115688.57 | 92100.54 | 114508.45 | 101468.26 | 59403.34 | 111259.3 | 100199.22 | 108846.36 | 103926.9 | 107527.42 | 118278.1
| Total Source Energy (MJ/m2) | 5223.29 | 5500.13 | 4731.36 | 4891.38 | 4388.19 | 5159.55 | 4107.55 | 5106.91 | 4525.34 | 2649.3 | 4962.01 | 4468.74 | 4854.39 | 4634.99 | 4795.57 | 5275.04
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 33351.95 | 26668.6 | 35326.1 | 21112.21 | 18419.46 | 29925.9 | 10859.06 | 17727.04 | 18148.17 | 10035.93 | 14018.2 | 14117.75 | 12442 | 10601.36 | 8007.48 | 5754.3
| Humidification | 9.48 | 116.31 | 476.6 | 302.54 | 119.92 | 913.53 | 80.07 | 483.52 | 879.67 | 250.32 | 583.49 | 916.77 | 706.21 | 914.67 | 888.83 | 1200.15
| Water Systems | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61
| Total Building | 37399.04 | 30822.52 | 39840.32 | 25452.35 | 22576.99 | 34877.04 | 14976.74 | 22248.17 | 23065.45 | 14323.86 | 18639.3 | 19072.13 | 17185.81 | 15553.64 | 12933.92 | 10992.05
Emissions
| Carbon Equivalent (kg) | 2614410 | 3022260 | 2674020 | 2657400 | 1122370 | 2898830 | 1063050 | 2330040 | 3249590 | 770156.6431 | 4221820 | 3192320 | 2811860 | 2843800 | 2760170 | 2442780
| CO2 (kg) | 6164480 | 7670100 | 6411430 | 6182920 | 3050860 | 6982520 | 2896510 | 5393900 | 7686970 | 1968430 | 9902580 | 7560760 | 6654740 | 6754470 | 6548700 | 6291020
| NOX (kg) | 10394.6748 | 9814.5882 | 10319.4187 | 11215.5021 | 2648.1237 | 10977.1993 | 2518.7862 | 9961.8477 | 12983.4188 | 2616.6561 | 17298.6122 | 12730.3065 | 11361.8755 | 11366.4185 | 11108.6998 | 7435.7193
| SO2 (kg) | 37796.2194 | 39971.0161 | 32576.7169 | 27494.2625 | 21783.8256 | 43629.7505 | 19851.1077 | 27993.8599 | 32539.7778 | 5306.8555 | 49857.3425 | 31789.3052 | 17357.8067 | 18964.3597 | 16846.3369 | 36106.4638
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1734 | 0.1137 | 0.0897 | 0.1018 | 0.0113 | 0.0831 | 0.0105 | 0.1143 | 0.1279 | 0.0222 | 0.1519 | 0.1251 | 0.1283 | 0.1329 | 0.1247 | 0.1247
| Water for Electricity (m3) | 4677.44 | 13633.5 | 240617 | 48900.4 | 131418 | 217577 | 119755 | 1740.84 | 33833.2 | 70095.2 | 11476.8 | 33052.6 | 11407.2 | 449810 | 11070.8 | 7245.49

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 42485.68 | 1894.8 | 1894.8
Net Site Energy | 42485.68 | 1894.8 | 1894.8
Total Source Energy | 117117.84 | 5223.29 | 5223.29
Net Source Energy | 117117.84 | 5223.29 | 5223.29
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 8873.2 | 0 | 0 | 0 | 0
Cooling | 8406.51 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2553.15 | 0 | 0 | 0 | 0 | 0
Pumps | 1788.43 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1281.91 | 0 | 0 | 0 | 0 | 33351.95
Humidification | 25.5 | 0 | 0 | 0 | 0 | 9.48
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 468.23 | 0 | 0 | 0 | 4037.61
Refrigeration | 205.75 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 31785.83 | 10699.85 | 0 | 0 | 0 | 37399.04
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.251 | 0.11 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.251 | 0.11 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.251 | 0.11 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.251 | 0.11 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.251 | 0.11 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 186.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3247645.08 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3285665.65 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3097753.77
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 573100.92 | 369427.43 | 203673.49 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 398964.79 | 283205.85 | 115758.94 | 0.71 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 927184.74 | 610529 | 316655.74 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1486454.02 | 972651.21 | 513802.82 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 79793.83 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15197.24 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16735.32 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 18522.27 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 51274.01 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52626.22 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16393.61 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16393.61 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 191288.04 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29819.47 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38162.1 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15158.19 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 65356.69 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 137561.43 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77806.32 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77806.32 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 54080.41 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28609.69 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29158.92 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 48042.48 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57941.73 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 274063.05 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 55114.26 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204792.82 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36727.82 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7749.89 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4284.74 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 33812.82 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7911.87 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7622.45 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12349.5 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12276.74 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 69134.09 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 68556.48 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12516.41 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12443.98 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12353.79 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12278.08 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 86966.26 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 86438.15 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12754.01 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12674.91 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 43033.68 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107584.19 | -
CAV_1_HEATC | Coil:Heating:Water | 2428.96 | -
CAV_2_HEATC | Coil:Heating:Water | 196178.12 | -
VAV_1_HEATC | Coil:Heating:Water | 67867.53 | -
VAV_2_HEATC | Coil:Heating:Water | 121463.96 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.08 | 28759.6 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.89 | 26923.99 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.67 | 49627.35 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.61 | 77218.34 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29760.17 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18092.27 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 43720.47 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 498543.4805 | 829.5963 | 2969.6821 | 0 | 0.0137 | 367501.8179 | 210328.3585
February | 448614.931 | 748.7666 | 2690.0071 | 0 | 0.0124 | 332893.5868 | 189490.0014
March | 508219.066 | 851.5544 | 3073.4193 | 0 | 0.0141 | 380344.3541 | 214997.2711
April | 489847.1634 | 824.7815 | 2993.8814 | 0 | 0.0137 | 370504.6456 | 207627.0586
May | 538033.2672 | 911.4263 | 3331.7659 | 0 | 0.0153 | 412323.707 | 228603.4926
June | 531221.3154 | 903.0324 | 3314.3408 | 0 | 0.0152 | 410169.798 | 226024.3674
July | 551543.6076 | 939.3115 | 3454.7722 | 0 | 0.0158 | 427550.4261 | 234844.7396
August | 558917.4917 | 952.6083 | 3506.7746 | 0 | 0.0161 | 433986.652 | 238058.5186
September | 530362.0716 | 900.4905 | 3300.4696 | 0 | 0.0151 | 408452.2811 | 225550.4327
October | 528328.8831 | 893.4756 | 3259.7755 | 0 | 0.0149 | 403413.2869 | 224328.7762
November | 492041.1975 | 825.6439 | 2985.003 | 0 | 0.0137 | 369403.5754 | 208273.2781
December | 488810.3241 | 813.9874 | 2916.328 | 0 | 0.0134 | 360899.6745 | 206280.9405
Annual Sum or Average | 6164480 | 10394.6748 | 37796.2194 | 0 | 0.1734 | 4677440 | 2614410
Minimum of Months | 448614.931 | 748.7666 | 2690.0071 | 0 | 0.0124 | 332893.5868 | 189490.0014
Maximum of Months | 558917.4917 | 952.6083 | 3506.7746 | 0 | 0.0161 | 433986.652 | 238058.5186
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2497380000000 | 1442006.741 | 06-JAN-17:45 | 445952.007 | 310109.712 | 92596.157 | 0 | 317015.779 | 6881 | 59565.878 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6265.552 | 0 | 0
February | 2262200000000 | 1446495.187 | 23-FEB-11:45 | 445952.007 | 310109.712 | 91357.744 | 0 | 324886.007 | 0 | 59368.179 | 40658.018 | 162962.637 | 0 | 0 | 0 | 11200.883 | 0 | 0
March | 2584650000000 | 1462351.845 | 14-MAR-10:45 | 445952.007 | 310109.712 | 88145.366 | 0 | 343579.932 | 0 | 59854.554 | 40658.018 | 162962.637 | 0 | 0 | 0 | 11089.618 | 0 | 0
April | 2517780000000 | 1482490.834 | 04-APR-16:00 | 445952.007 | 310109.712 | 101781.969 | 0 | 353671.396 | 0 | 60802.893 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6552.202 | 0 | 0
May | 2801970000000 | 1564254.455 | 19-MAY-15:15 | 445952.007 | 310109.712 | 105105.026 | 0 | 430168.951 | 0 | 62723.017 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6575.087 | 0 | 0
June | 2787330000000 | 1620479.315 | 27-JUN-15:00 | 445952.007 | 310109.712 | 102144.153 | 0 | 488451.699 | 0 | 63478.654 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6722.435 | 0 | 0
July | 2905440000000 | 1600473.866 | 13-JUL-15:45 | 445952.007 | 310109.712 | 106903.35 | 0 | 463735.069 | 0 | 63467.154 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6685.918 | 0 | 0
August | 2949180000000 | 1575706.832 | 21-AUG-15:15 | 445952.007 | 310109.712 | 94795.761 | 0 | 452462.104 | 0 | 62075.431 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6691.161 | 0 | 0
September | 2775660000000 | 1560231.07 | 12-SEP-15:00 | 445952.007 | 310109.712 | 101465.481 | 0 | 429851.283 | 0 | 62632.126 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6599.804 | 0 | 0
October | 2741420000000 | 1559281.496 | 06-OCT-15:00 | 445952.007 | 310109.712 | 106522.51 | 0 | 423615.02 | 0 | 62857.528 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6604.063 | 0 | 0
November | 2510300000000 | 1486994.267 | 01-NOV-15:00 | 445952.007 | 310109.712 | 96775.364 | 0 | 363291.426 | 0 | 60784.965 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6460.138 | 0 | 0
December | 2452510000000 | 1455141.529 | 15-DEC-17:30 | 445952.007 | 310109.712 | 96996.418 | 0 | 325229.215 | 6881 | 60033.85 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6318.671 | 0 | 0
Annual Sum or Average | 31785800000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2262200000000 | 1442006.741 |  | 445952.007 | 310109.712 | 88145.366 | 0 | 317015.779 | 0 | 59368.179 | 40658.018 | 162962.637 | 0 | 0 | 0 | 6265.552 | 0 | 0
Maximum of Months | 2949180000000 | 1620479.315 |  | 445952.007 | 310109.712 | 106903.35 | 0 | 488451.699 | 6881 | 63478.654 | 40658.018 | 162962.637 | 0 | 0 | 0 | 11200.883 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 662734.56 | 122436.71 | 0 | 785171.27
Cost per Total Building Area ($/m2) | 29.56 | 5.46 | 0 | 35.02
Cost per Net Conditioned Building Area ($/m2) | 29.56 | 5.46 | 0 | 35.02

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 42772.97 | 1907.61 | 1907.61
Net Site Energy | 42772.97 | 1907.61 | 1907.61
Total Source Energy | 123325.29 | 5500.13 | 5500.13
Net Source Energy | 123325.29 | 5500.13 | 5500.13
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10688.63 | 0 | 0 | 0 | 0
Cooling | 6726.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.12 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2498.32 | 0 | 0 | 0 | 0 | 0
Pumps | 1698.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1205.98 | 0 | 0 | 0 | 0 | 26668.6
Humidification | 312.66 | 0 | 0 | 0 | 0 | 116.31
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 561.66 | 0 | 0 | 0 | 4037.61
Refrigeration | 197.79 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 30164.25 | 12608.71 | 0 | 0 | 0 | 30822.52
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.251 | 0.11 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.251 | 0.11 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.251 | 0.11 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.251 | 0.11 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.251 | 0.11 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 186.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3194230.58 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3455086.41 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3046804.55
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 569722.2 | 366283.83 | 203438.37 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 371133.18 | 268305.78 | 102827.4 | 0.72 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 915678.82 | 600996.44 | 314682.38 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1478255.14 | 963728.5 | 514526.64 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 76575.02 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14607.74 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16674.1 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 17896.57 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 50586.42 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52337.86 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16333.64 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16333.64 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 192039.3 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29820.07 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37404.94 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15037.22 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 65449.62 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 136277.27 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77521.69 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77521.69 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53454.38 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28557.13 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29114.72 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 47208.71 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 58709.35 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 271526.15 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54086.82 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198678.44 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37140.08 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7825.4 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4457.94 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 33551.46 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7819.86 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7382.08 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12683.94 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12622.54 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 68784.02 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 68290.55 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12477.78 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12423.05 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61244.19 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12613.8 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12531.27 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 86862.86 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 86263.94 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12602.85 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12523.36 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42876.25 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107190.62 | -
CAV_1_HEATC | Coil:Heating:Water | 12790.92 | -
CAV_2_HEATC | Coil:Heating:Water | 202244.43 | -
VAV_1_HEATC | Coil:Heating:Water | 119271.36 | -
VAV_2_HEATC | Coil:Heating:Water | 212631.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.09 | 28760.51 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.74 | 26668.71 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.42 | 49207.14 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.47 | 76984.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29270.7 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19025.17 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 43001.4 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 621069.7704 | 785.4755 | 3107.1647 | 0 | 0.0089 | 1059770 | 243530.185
February | 544444.8527 | 687.5136 | 2709.0636 | 0 | 0.0078 | 923980.1553 | 213348.7049
March | 628313.2887 | 799.7289 | 3214.7258 | 0 | 0.0092 | 1096480 | 247026.8792
April | 612829.4597 | 783.8797 | 3189.5495 | 0 | 0.0091 | 1087910 | 241436.6819
May | 666600.4387 | 856.9962 | 3530.1515 | 0 | 0.01 | 1204100 | 263179.9107
June | 674178.5223 | 870.3219 | 3620.468 | 0 | 0.0103 | 1234930 | 266633.6788
July | 706443.5971 | 913.0619 | 3808.9732 | 0 | 0.0108 | 1299230 | 279534.5473
August | 713499.994 | 921.9038 | 3843.1216 | 0 | 0.0109 | 1310880 | 282290.8366
September | 651757.3234 | 839.4383 | 3472.9014 | 0 | 0.0098 | 1184580 | 257516.2564
October | 641238.4093 | 821.5538 | 3356.1152 | 0 | 0.0095 | 1144730 | 252801.1423
November | 601541.232 | 766.3468 | 3087.4659 | 0 | 0.0088 | 1053080 | 236590.6466
December | 608186.1474 | 768.3679 | 3031.3157 | 0 | 0.0087 | 1033890 | 238373.4788
Annual Sum or Average | 7670100 | 9814.5882 | 39971.0161 | 0 | 0.1137 | 13633500 | 3022260
Minimum of Months | 544444.8527 | 687.5136 | 2709.0636 | 0 | 0.0078 | 923980.1553 | 213348.7049
Maximum of Months | 713499.994 | 921.9038 | 3843.1216 | 0 | 0.0109 | 1310880 | 282290.8366
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2344740000000 | 1391717.417 | 03-JAN-11:45 | 445952.007 | 310109.712 | 78132.321 | 0 | 286618.252 | 0 | 57058.606 | 39989.31 | 162962.637 | 0 | 0 | 0 | 10894.572 | 0 | 0
February | 2044310000000 | 1347292.996 | 15-FEB-16:15 | 445952.007 | 310109.712 | 82514.337 | 0 | 243735.881 | 0 | 55891.463 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6137.648 | 0 | 0
March | 2425960000000 | 1383438.932 | 24-MAR-16:30 | 445952.007 | 310109.712 | 87122.812 | 0 | 273920.59 | 0 | 57080.626 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6301.237 | 0 | 0
April | 2407000000000 | 1421554.621 | 20-APR-15:15 | 445952.007 | 310109.712 | 92428.12 | 0 | 305718.962 | 0 | 58036.558 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6357.316 | 0 | 0
May | 2664080000000 | 1556776.267 | 18-MAY-16:00 | 445952.007 | 310109.712 | 102783.145 | 0 | 426642.036 | 0 | 61694.79 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6642.63 | 0 | 0
June | 2732280000000 | 1545397.143 | 29-JUN-16:30 | 445952.007 | 310109.712 | 102993.565 | 0 | 415354.292 | 0 | 61366.518 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6669.101 | 0 | 0
July | 2874550000000 | 1620662.16 | 18-JUL-12:30 | 445952.007 | 302612.437 | 96660.987 | 0 | 502452.751 | 0 | 62421.212 | 39989.31 | 162962.637 | 0 | 0 | 0 | 7610.82 | 0 | 0
August | 2900320000000 | 1584830.166 | 03-AUG-15:15 | 445952.007 | 310109.712 | 102703.93 | 0 | 454247.261 | 0 | 62190.742 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6674.566 | 0 | 0
September | 2620890000000 | 1599837.459 | 15-SEP-15:15 | 445952.007 | 310109.712 | 99659.274 | 0 | 472383.986 | 0 | 62148.889 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6631.645 | 0 | 0
October | 2532710000000 | 1479394.064 | 30-OCT-15:15 | 445952.007 | 310109.712 | 86534.876 | 0 | 368329.797 | 0 | 59162.86 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6352.865 | 0 | 0
November | 2329930000000 | 1433306.389 | 27-NOV-17:00 | 445952.007 | 310109.712 | 82891.087 | 0 | 320060.697 | 6881 | 58150.303 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6309.637 | 0 | 0
December | 2287490000000 | 1384708.462 | 06-DEC-17:30 | 445952.007 | 310109.712 | 83360.48 | 0 | 272406.246 | 6881 | 56943.06 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6104.009 | 0 | 0
Annual Sum or Average | 30164300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2044310000000 | 1347292.996 |  | 445952.007 | 302612.437 | 78132.321 | 0 | 243735.881 | 0 | 55891.463 | 39989.31 | 162962.637 | 0 | 0 | 0 | 6104.009 | 0 | 0
Maximum of Months | 2900320000000 | 1620662.16 |  | 445952.007 | 310109.712 | 102993.565 | 0 | 502452.751 | 6881 | 62421.212 | 39989.31 | 162962.637 | 0 | 0 | 0 | 10894.572 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 813820.9 | 103019.4 | 0 | 916840.3
Cost per Total Building Area ($/m2) | 36.3 | 4.59 | 0 | 40.89
Cost per Net Conditioned Building Area ($/m2) | 36.3 | 4.59 | 0 | 40.89

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 41844.6 | 1866.21 | 1866.21
Net Site Energy | 41844.6 | 1866.21 | 1866.21
Total Source Energy | 106087.63 | 4731.36 | 4731.36
Net Source Energy | 106087.63 | 4731.36 | 4731.36
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10816.84 | 0 | 0 | 0 | 0
Cooling | 4765.97 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.09 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2753.49 | 0 | 0 | 0 | 0 | 0
Pumps | 1514.03 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1123.26 | 0 | 0 | 0 | 0 | 35326.1
Humidification | 1281.2 | 0 | 0 | 0 | 0 | 476.6
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 507.91 | 0 | 0 | 0 | 4037.61
Refrigeration | 199.11 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 29161.43 | 12683.17 | 0 | 0 | 0 | 39840.32
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.251 | 0.11 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.251 | 0.11 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.251 | 0.11 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.251 | 0.11 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.251 | 0.11 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 186.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2926288.28 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3441100.81 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2791228.83
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 581838.99 | 372222.25 | 209616.74 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 391084.37 | 277522.01 | 113562.35 | 0.71 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 874199.18 | 567563.4 | 306635.78 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1429578.51 | 920964.3 | 508614.21 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 47188.1 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14851.25 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16079.49 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 16368.72 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 50559.05 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53963.43 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16756.94 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16141.04 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204207.25 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29824.07 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41802.43 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17138.17 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 71826.16 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 136789.15 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74757.19 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74757.19 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60166.78 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29617.74 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30157.58 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 43134.26 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 63490.34 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 278316.31 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 56060.65 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204464.01 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40439.82 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8633.46 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5443.65 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34162.18 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8458.47 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7954.71 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 69897.76 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 69740.87 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15761.26 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15706.86 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 78170.84 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77913.64 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15091.4 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15047.39 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 65909.53 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 65818.66 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15127.23 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15042.11 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 97180 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 96558.13 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14723.81 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14644.17 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41347.24 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 103368.1 | -
CAV_1_HEATC | Coil:Heating:Water | 0 | -
CAV_2_HEATC | Coil:Heating:Water | 209329.28 | -
VAV_1_HEATC | Coil:Heating:Water | 83094.25 | -
VAV_2_HEATC | Coil:Heating:Water | 165247.55 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.93 | 31869.97 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.12 | 28822.75 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.8 | 49840.25 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 47.57 | 78800.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26815.38 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18948.16 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 39394.3 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 528862.9222 | 832.4166 | 2551.123 | 0 | 0.0071 | 18842000 | 218671.8155
February | 482564.1507 | 762.3015 | 2347.7385 | 0 | 0.0065 | 17340000 | 199807.2989
March | 541218.8919 | 865.038 | 2706.023 | 0 | 0.0075 | 19986800 | 225112.8317
April | 525462.162 | 846.1767 | 2672.9813 | 0 | 0.0074 | 19743100 | 219198.409
May | 550268.6472 | 891.9267 | 2841.1485 | 0 | 0.0078 | 20985600 | 230133.3275
June | 542333.5508 | 887.2668 | 2859.5127 | 0 | 0.0078 | 21121600 | 227644.1293
July | 563991.3525 | 925.6756 | 2995.236 | 0 | 0.0082 | 22124300 | 237035.9391
August | 569762.7343 | 934.4314 | 3020.7019 | 0 | 0.0083 | 22312400 | 239389.0775
September | 528758.9393 | 861.7204 | 2763.791 | 0 | 0.0076 | 20414400 | 221608.6384
October | 534187.5599 | 860.2045 | 2717.1998 | 0 | 0.0075 | 20069700 | 222835.9083
November | 510303.4895 | 812.87 | 2531.5164 | 0 | 0.007 | 18697800 | 211975.3339
December | 533712.8385 | 839.3905 | 2569.745 | 0 | 0.0071 | 18979500 | 220610.4167
Annual Sum or Average | 6411430 | 10319.4187 | 32576.7169 | 0 | 0.0897 | 240617000 | 2674020
Minimum of Months | 482564.1507 | 762.3015 | 2347.7385 | 0 | 0.0065 | 17340000 | 199807.2989
Maximum of Months | 569762.7343 | 934.4314 | 3020.7019 | 0 | 0.0083 | 22312400 | 239389.0775
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2283540000000 | 1368257.628 | 26-JAN-16:15 | 445952.007 | 310109.712 | 93302.335 | 0 | 151995.999 | 0 | 49156.92 | 36634.878 | 162962.637 | 0 | 0 | 0 | 5994.485 | 0 | 0
February | 2101510000000 | 1409298.77 | 28-FEB-17:00 | 445952.007 | 310109.712 | 93925.56 | 0 | 163269.211 | 0 | 49371.087 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6171.286 | 0 | 0
March | 2422290000000 | 1461163.28 | 30-MAR-15:00 | 445952.007 | 310109.712 | 103316.314 | 0 | 192738.026 | 0 | 50603.025 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6412.6 | 0 | 0
April | 2392750000000 | 1439768.909 | 26-APR-16:00 | 445952.007 | 310109.712 | 107765.638 | 0 | 212723.308 | 0 | 51200.626 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6554.35 | 0 | 0
May | 2543330000000 | 1482241.819 | 19-MAY-16:00 | 445952.007 | 310109.712 | 114855.987 | 0 | 243180.101 | 0 | 52229.125 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6663.593 | 0 | 0
June | 2559820000000 | 1547300.769 | 08-JUN-15:00 | 445952.007 | 310109.712 | 123192.894 | 0 | 310418.227 | 0 | 53972.846 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6742.154 | 0 | 0
July | 2681340000000 | 1517696.899 | 11-JUL-16:15 | 445952.007 | 310109.712 | 120238.585 | 0 | 378778.024 | 0 | 56147.071 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6873.985 | 0 | 0
August | 2704130000000 | 1526955.248 | 11-AUG-16:00 | 445952.007 | 310109.712 | 120258.253 | 0 | 386350.23 | 0 | 57820.462 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6867.068 | 0 | 0
September | 2474110000000 | 1465161.709 | 08-SEP-15:00 | 445952.007 | 310109.712 | 117978.202 | 0 | 329845.833 | 0 | 54859.617 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6818.823 | 0 | 0
October | 2432340000000 | 1421630.565 | 03-OCT-09:30 | 445952.007 | 310109.712 | 94668.573 | 0 | 307806.578 | 0 | 56597.988 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6898.191 | 0 | 0
November | 2266060000000 | 1390183.873 | 15-NOV-16:00 | 445952.007 | 310109.712 | 98659.949 | 0 | 179235.952 | 0 | 49997.542 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6273.187 | 0 | 0
December | 2300210000000 | 1403763.613 | 06-DEC-16:00 | 445952.007 | 310109.712 | 92594.282 | 0 | 134927.799 | 0 | 48677.409 | 36634.878 | 162962.637 | 0 | 0 | 0 | 5846.026 | 0 | 0
Annual Sum or Average | 29161400000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2101510000000 | 1368257.628 |  | 445952.007 | 310109.712 | 92594.282 | 0 | 134927.799 | 0 | 48677.409 | 36634.878 | 162962.637 | 0 | 0 | 0 | 5846.026 | 0 | 0
Maximum of Months | 2704130000000 | 1547300.769 |  | 445952.007 | 310109.712 | 123192.894 | 0 | 386350.23 | 0 | 57820.462 | 36634.878 | 162962.637 | 0 | 0 | 0 | 6898.191 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 545379.9 | 108455.61 | 0 | 653835.51
Cost per Total Building Area ($/m2) | 24.32 | 4.84 | 0 | 29.16
Cost per Net Conditioned Building Area ($/m2) | 24.32 | 4.84 | 0 | 29.16

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 41772.37 | 1862.99 | 1862.99
Net Site Energy | 41772.37 | 1862.99 | 1862.99
Total Source Energy | 109675.63 | 4891.38 | 4891.38
Net Source Energy | 109675.63 | 4891.38 | 4891.38
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11566.73 | 0 | 0 | 0 | 0
Cooling | 4628.8 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2478.29 | 0 | 0 | 0 | 0 | 0
Pumps | 1522.02 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1038.27 | 0 | 0 | 0 | 0 | 21112.21
Humidification | 813.27 | 0 | 0 | 0 | 0 | 302.54
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 651.71 | 0 | 0 | 0 | 4037.61
Refrigeration | 190.32 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 28195.51 | 13576.85 | 0 | 0 | 0 | 25452.35
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.255 | 0.129 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 4.092 | 0.255 | 0.129 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 4.092 | 0.255 | 0.129 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 4.092 | 0.255 | 0.129 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 4.092 | 0.255 | 0.129 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 4.092 | 0.255 | 0.129 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 4.092 | 0.255 | 0.129 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.255 | 0.129 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.255 | 0.129 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.255 | 0.129 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 4.092 | 0.255 | 0.129 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 4.092 | 0.255 | 0.129 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.255 | 0.129 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.255 | 0.129 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 4.092 | 0.255 | 0.129 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.255 | 0.129 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.255 | 0.129 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.255 | 0.129 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.255 | 0.129 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.255 | 0.129 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.255 | 0.129 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.255 | 0.129 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.255 | 0.129 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.255 | 0.129 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.255 | 0.129 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.255 | 0.129 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.255 | 0.129 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.255 | 0.129 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.255 | 0.129 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.255 | 0.129 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.255 | 0.129 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.255 | 0.129 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 186.18 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 659.24 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2958351.69 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3445795.29 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2821812.38
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 541241.66 | 342745.88 | 198495.78 | 0.63 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 359703.6 | 258364.01 | 101339.59 | 0.72 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 874824.9 | 566050.93 | 308773.96 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1439455.49 | 926251.12 | 513204.37 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 71902.18 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14423.14 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16125.49 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 18209.97 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 50437.31 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51415.97 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15796.23 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15796.23 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 188327.36 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29823.76 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35622.48 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13765.88 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 60909.46 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 135090.1 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74971.08 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74971.08 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49764.36 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28380.78 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28937.62 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 48092.18 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 56194.37 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 270869.89 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53972.12 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198665.55 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36479.79 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7420.14 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4256.51 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 31984.98 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7251.36 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7013.35 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11846.88 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11804.6 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64836.64 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64557.15 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11491.19 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11447.63 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11640.56 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11576.95 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 79427.39 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 78970.24 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11298.71 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11235.33 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41465.54 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 103663.85 | -
CAV_1_HEATC | Coil:Heating:Water | 36726.96 | -
CAV_2_HEATC | Coil:Heating:Water | 189287.21 | -
VAV_1_HEATC | Coil:Heating:Water | 136047.91 | -
VAV_2_HEATC | Coil:Heating:Water | 246977.36 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.79 | 28269.76 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.06 | 27207.69 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.11 | 48696.52 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 47.08 | 77989.88 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27109.2 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18974.01 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 39825.95 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 516126.1273 | 909.4535 | 2163.8719 | 0 | 0.0081 | 3848320 | 219356.5845
February | 467171.2238 | 828.2715 | 1983.531 | 0 | 0.0074 | 3527650 | 199019.6433
March | 518301.2681 | 931.4622 | 2262.0911 | 0 | 0.0084 | 4023190 | 221959.6317
April | 490608.3603 | 888.7807 | 2175.9664 | 0 | 0.0081 | 3870090 | 210754.7684
May | 519649.5787 | 951.6948 | 2355.2789 | 0 | 0.0087 | 4189110 | 224181.7917
June | 524183.1446 | 969.143 | 2420.6582 | 0 | 0.0089 | 4305490 | 226982.2151
July | 552431.6129 | 1024.7064 | 2567.461 | 0 | 0.0095 | 4566630 | 239522.4631
August | 561449.9751 | 1041.8344 | 2611.3345 | 0 | 0.0096 | 4644670 | 243469.5577
September | 523715.3709 | 966.224 | 2408.4286 | 0 | 0.0089 | 4283720 | 226589.9559
October | 507232.4963 | 920.4991 | 2257.553 | 0 | 0.0084 | 4015210 | 218044.1147
November | 491940.4677 | 880.5541 | 2129.7175 | 0 | 0.0079 | 3787730 | 210344.3973
December | 510112.8302 | 902.8782 | 2158.3703 | 0 | 0.008 | 3838580 | 217172.2129
Annual Sum or Average | 6182920 | 11215.5021 | 27494.2625 | 0 | 0.1018 | 48900400 | 2657400
Minimum of Months | 467171.2238 | 828.2715 | 1983.531 | 0 | 0.0074 | 3527650 | 199019.6433
Maximum of Months | 561449.9751 | 1041.8344 | 2611.3345 | 0 | 0.0096 | 4644670 | 243469.5577
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2218910000000 | 1295276.013 | 26-JAN-16:00 | 445952.007 | 310109.712 | 82708.289 | 0 | 105631.128 | 0 | 46962.034 | 37036.288 | 162962.637 | 0 | 0 | 0 | 5582.138 | 0 | 0
February | 2034010000000 | 1306349.283 | 06-FEB-16:15 | 445952.007 | 310109.712 | 78532.171 | 0 | 105437.285 | 0 | 46928.491 | 37036.288 | 162962.637 | 0 | 0 | 0 | 5604.07 | 0 | 0
March | 2319740000000 | 1353837.466 | 22-MAR-16:00 | 445952.007 | 310109.712 | 88549.276 | 0 | 141697.471 | 0 | 48731.456 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6084.324 | 0 | 0
April | 2231460000000 | 1341090.879 | 14-APR-16:00 | 445952.007 | 310109.712 | 92995.533 | 0 | 233257.923 | 0 | 52327.253 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6449.525 | 0 | 0
May | 2415400000000 | 1428000.354 | 31-MAY-16:00 | 445952.007 | 310109.712 | 95007.01 | 0 | 315038.955 | 0 | 55305.032 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6588.713 | 0 | 0
June | 2482500000000 | 1484892.041 | 08-JUN-15:00 | 445952.007 | 310109.712 | 100338.732 | 0 | 365011.802 | 0 | 56929.422 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6551.44 | 0 | 0
July | 2633080000000 | 1513607.821 | 25-JUL-16:15 | 445952.007 | 310109.712 | 96221.807 | 0 | 397260.195 | 0 | 57511.319 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6553.856 | 0 | 0
August | 2678070000000 | 1510555.612 | 17-AUG-15:15 | 445952.007 | 310109.712 | 101338.778 | 0 | 389124.362 | 0 | 57323.589 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6708.239 | 0 | 0
September | 2469950000000 | 1458168.523 | 01-SEP-15:45 | 445952.007 | 310109.712 | 100521.422 | 0 | 338781.041 | 0 | 56347.229 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6458.187 | 0 | 0
October | 2315130000000 | 1366253.936 | 20-OCT-16:00 | 445952.007 | 310109.712 | 91519.791 | 0 | 258702.198 | 0 | 53706.897 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6264.406 | 0 | 0
November | 2183970000000 | 1315362.885 | 03-NOV-15:15 | 445952.007 | 310109.712 | 83909.677 | 0 | 100344.585 | 0 | 46907.408 | 37036.288 | 162962.637 | 0 | 0 | 0 | 5481.426 | 0 | 0
December | 2213290000000 | 1299066.899 | 28-DEC-14:00 | 445952.007 | 302612.437 | 81695.899 | 0 | 93567.855 | 0 | 46424.661 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6273.436 | 0 | 0
Annual Sum or Average | 28195500000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2034010000000 | 1295276.013 |  | 445952.007 | 302612.437 | 78532.171 | 0 | 93567.855 | 0 | 46424.661 | 37036.288 | 162962.637 | 0 | 0 | 0 | 5481.426 | 0 | 0
Maximum of Months | 2678070000000 | 1513607.821 |  | 445952.007 | 310109.712 | 101338.778 | 0 | 397260.195 | 0 | 57511.319 | 37036.288 | 162962.637 | 0 | 0 | 0 | 6708.239 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 754430.36 | 144686.88 | 0 | 899117.23
Cost per Total Building Area ($/m2) | 33.65 | 6.45 | 0 | 40.1
Cost per Net Conditioned Building Area ($/m2) | 33.65 | 6.45 | 0 | 40.1

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40678.54 | 1814.2 | 1814.2
Net Site Energy | 40678.54 | 1814.2 | 1814.2
Total Source Energy | 98393.04 | 4388.19 | 4388.19
Net Source Energy | 98393.04 | 4388.19 | 4388.19
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11740.28 | 0 | 0 | 0 | 0
Cooling | 4035.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2481.33 | 0 | 0 | 0 | 0 | 0
Pumps | 1371.81 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1018.57 | 0 | 0 | 0 | 0 | 18419.46
Humidification | 322.38 | 0 | 0 | 0 | 0 | 119.92
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 634.22 | 0 | 0 | 0 | 4037.61
Refrigeration | 191.13 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26945.62 | 13732.92 | 0 | 0 | 0 | 22576.99
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.44 | 0.272 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.44 | 0.272 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.44 | 0.272 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.44 | 0.272 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.44 | 0.272 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.44 | 0.272 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.44 | 0.272 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.44 | 0.272 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.44 | 0.272 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.44 | 0.272 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.44 | 0.272 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.44 | 0.272 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.44 | 0.272 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.44 | 0.272 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.44 | 0.272 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.44 | 0.272 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.44 | 0.272 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.44 | 0.272 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.44 | 0.272 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.44 | 0.272 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.44 | 0.272 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.44 | 0.272 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.44 | 0.272 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.44 | 0.272 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.44 | 0.272 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.44 | 0.272 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.44 | 0.272 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.44 | 0.272 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.44 | 0.272 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.44 | 0.272 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.44 | 0.272 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.44 | 0.272 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 186.18 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2586167.48 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3291823.96 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2466805.91
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 518084.9 | 344780.54 | 173304.36 | 0.67 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 346641.09 | 254607.78 | 92033.3 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 813428.72 | 551313.36 | 262115.36 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1344002.99 | 905135.34 | 438867.64 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 72374.39 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11925.94 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16676.07 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 18624.51 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 52803.03 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52860.71 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16335.57 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16335.57 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 195100.12 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29820.15 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30865.35 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13752.7 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 69792.47 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 135522.13 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77530.86 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77530.86 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53420.76 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29468 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30022.58 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 50085.43 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53438.27 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 262075.57 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50625.11 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204762.34 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37670.92 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8298.68 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5074.17 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 36200.49 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7429.2 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6164.38 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64142.15 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63583.17 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12876.18 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12746 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 70825.68 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 70320.9 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10210.43 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10210.43 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13205.73 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13056.6 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 93618.67 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 92759.64 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11324.85 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11217.14 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42881.32 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107203.3 | -
CAV_1_HEATC | Coil:Heating:Water | 8512.54 | -
CAV_2_HEATC | Coil:Heating:Water | 191467 | -
VAV_1_HEATC | Coil:Heating:Water | 72758.44 | -
VAV_2_HEATC | Coil:Heating:Water | 132417.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.38 | 29255.92 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.35 | 26003.8 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 28.82 | 48206.6 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.74 | 77424.7 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23698.65 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18126.18 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 34815.52 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 261089.4553 | 227.1883 | 1763.1965 | 0 | 0.0009 | 10636600 | 95742.9426
February | 230248.5552 | 200.2809 | 1567.6212 | 0 | 0.0008 | 9456850 | 84472.1628
March | 258728.2161 | 224.8767 | 1793.2161 | 0 | 0.0009 | 10817900 | 95017.3023
April | 244403.4643 | 212.304 | 1715.8018 | 0 | 0.0009 | 10351000 | 89823.2936
May | 256573.3358 | 222.6363 | 1844.0299 | 0 | 0.0009 | 11124800 | 94426.5255
June | 252280.0699 | 218.7348 | 1844.6845 | 0 | 0.0009 | 11128800 | 92942.616
July | 258762.3173 | 224.1356 | 1931.3543 | 0 | 0.001 | 11651900 | 95450.5588
August | 266228.0161 | 230.4488 | 2014.5461 | 0 | 0.001 | 12153900 | 98288.2648
September | 251984.1023 | 218.2755 | 1878.7935 | 0 | 0.0009 | 11334800 | 92944.2463
October | 260588.6716 | 226.0094 | 1892.7655 | 0 | 0.001 | 11418900 | 95964.9305
November | 250412.9148 | 217.516 | 1759.4427 | 0 | 0.0009 | 10614300 | 92036.3211
December | 259562.8087 | 225.7174 | 1778.3734 | 0 | 0.0009 | 10728300 | 95260.8718
Annual Sum or Average | 3050860 | 2648.1237 | 21783.8256 | 0 | 0.0113 | 131418000 | 1122370
Minimum of Months | 230248.5552 | 200.2809 | 1567.6212 | 0 | 0.0008 | 9456850 | 84472.1628
Maximum of Months | 266228.0161 | 230.4488 | 2014.5461 | 0 | 0.001 | 12153900 | 98288.2648
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2180910000000 | 1332327.833 | 26-JAN-14:15 | 445952.007 | 302612.437 | 87663.465 | 0 | 160648.55 | 0 | 44818.923 | 32376.828 | 162962.637 | 0 | 0 | 0 | 7097.269 | 0 | 0
February | 1939010000000 | 1292425.846 | 10-FEB-10:00 | 445952.007 | 310109.712 | 83149.187 | 0 | 133037.194 | 0 | 43984.52 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6809.745 | 0 | 0
March | 2218080000000 | 1350515.808 | 31-MAR-15:00 | 445952.007 | 310109.712 | 94094.321 | 0 | 149175.238 | 0 | 44713.471 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6102.984 | 0 | 0
April | 2122340000000 | 1415161.167 | 11-APR-16:00 | 445952.007 | 310109.712 | 90834.579 | 0 | 177129.283 | 0 | 45281.279 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6412.308 | 0 | 0
May | 2280990000000 | 1338953.311 | 31-MAY-15:15 | 445952.007 | 310109.712 | 90576.878 | 0 | 240888.913 | 0 | 49939.631 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6146.705 | 0 | 0
June | 2281830000000 | 1363425.845 | 23-JUN-16:30 | 445952.007 | 310109.712 | 95330.879 | 0 | 259358.057 | 0 | 51135.767 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6199.958 | 0 | 0
July | 2389070000000 | 1364503.222 | 26-JUL-16:00 | 445952.007 | 310109.712 | 99124.877 | 0 | 256474.277 | 0 | 51280.103 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6222.782 | 0 | 0
August | 2492010000000 | 1407027.761 | 08-AUG-16:30 | 445952.007 | 310109.712 | 101574.078 | 0 | 296207.587 | 0 | 51403.118 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6441.795 | 0 | 0
September | 2324050000000 | 1393023.211 | 01-SEP-15:00 | 445952.007 | 310109.712 | 99558.505 | 0 | 283427.038 | 0 | 52453.877 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6182.608 | 0 | 0
October | 2341300000000 | 1369081.76 | 19-OCT-15:45 | 445952.007 | 310109.712 | 95157.396 | 0 | 264851.97 | 0 | 51533.631 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6137.578 | 0 | 0
November | 2176330000000 | 1308259.125 | 29-NOV-11:45 | 445952.007 | 310109.712 | 83481.168 | 0 | 118469.933 | 0 | 43498.591 | 32376.828 | 162962.637 | 0 | 0 | 0 | 10192.942 | 0 | 0
December | 2199700000000 | 1331568.51 | 18-DEC-11:45 | 445952.007 | 310109.712 | 80133.658 | 0 | 140710.358 | 0 | 44028.255 | 32376.828 | 162962.637 | 0 | 0 | 0 | 10852.349 | 0 | 0
Annual Sum or Average | 26945600000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1939010000000 | 1292425.846 |  | 445952.007 | 302612.437 | 80133.658 | 0 | 118469.933 | 0 | 43498.591 | 32376.828 | 162962.637 | 0 | 0 | 0 | 6102.984 | 0 | 0
Maximum of Months | 2492010000000 | 1415161.167 |  | 445952.007 | 310109.712 | 101574.078 | 0 | 296207.587 | 0 | 52453.877 | 32376.828 | 162962.637 | 0 | 0 | 0 | 10852.349 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 328742.61 | 115552.92 | 0 | 444295.54
Cost per Total Building Area ($/m2) | 14.66 | 5.15 | 0 | 19.81
Cost per Net Conditioned Building Area ($/m2) | 14.66 | 5.15 | 0 | 19.81

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40969.35 | 1827.17 | 1827.17
Net Site Energy | 40969.35 | 1827.17 | 1827.17
Total Source Energy | 115688.57 | 5159.55 | 5159.55
Net Source Energy | 115688.57 | 5159.55 | 5159.55
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10486.96 | 0 | 0 | 0 | 0
Cooling | 3491.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2679.78 | 0 | 0 | 0 | 0 | 0
Pumps | 1301.64 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 906.35 | 0 | 0 | 0 | 0 | 29925.9
Humidification | 2455.73 | 0 | 0 | 0 | 0 | 913.53
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 572.65 | 0 | 0 | 0 | 4037.61
Refrigeration | 192.05 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 28551.32 | 12418.03 | 0 | 0 | 0 | 34877.04
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.251 | 0.11 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.251 | 0.11 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.251 | 0.11 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.251 | 0.11 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.251 | 0.11 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.251 | 0.11 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.251 | 0.11 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.251 | 0.11 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.251 | 0.11 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.251 | 0.11 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.251 | 0.11 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.251 | 0.11 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 186.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2537632.86 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3331289.13 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2420511.34
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 516846.16 | 330323.14 | 186523.02 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 348185.56 | 252088.9 | 96096.65 | 0.72 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 792828.82 | 514360.87 | 278467.96 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1318440.45 | 849023.31 | 469417.14 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 43093.95 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14393.06 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15466.93 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 16860.13 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 47067.1 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52221.91 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15151.12 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15151.12 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 194993.5 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29828.23 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38648.39 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15504.78 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 66428.37 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 142314.32 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 71909.3 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 71909.3 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 54800.47 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28206.2 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28756.99 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41480.5 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 58664 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 270487.47 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53943.41 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198654.46 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38721.68 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7775.08 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5002.5 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 31555.93 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7597.48 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7143.39 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64245.63 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64012.92 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13826.23 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13763.88 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 67570.12 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67334.31 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13021.14 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12982.17 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59221.18 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59137.04 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13508.94 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13412.38 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 88332.26 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 87624.26 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13058.3 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12974.62 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 39772.11 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 99430.28 | -
CAV_1_HEATC | Coil:Heating:Water | 3210.12 | -
CAV_2_HEATC | Coil:Heating:Water | 202420.61 | -
VAV_1_HEATC | Coil:Heating:Water | 101466.66 | -
VAV_2_HEATC | Coil:Heating:Water | 194076.24 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.06 | 30402.26 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.03 | 28664.6 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 28.95 | 48417.88 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 47.11 | 78049.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23253.89 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18343.49 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 34162.14 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 583764.2817 | 899.5169 | 3476.3766 | 0 | 0.0067 | 17335600 | 240459.6596
February | 524759.6144 | 814.6633 | 3182.0146 | 0 | 0.0061 | 15868000 | 216785.4088
March | 593678.2236 | 924.6083 | 3627.6704 | 0 | 0.0069 | 18090500 | 245563.4961
April | 577477.3043 | 908.591 | 3615.2828 | 0 | 0.0069 | 18029100 | 239820.0154
May | 605845.4058 | 958.1976 | 3839.622 | 0 | 0.0073 | 19148000 | 252117.8449
June | 600239.772 | 958.2123 | 3887.566 | 0 | 0.0074 | 19387400 | 250708.1231
July | 594986.7285 | 951.4787 | 3869.0736 | 0 | 0.0073 | 19295300 | 248685.7631
August | 605202.4563 | 967.2647 | 3930.3293 | 0 | 0.0074 | 19600700 | 252898.3903
September | 574301.6722 | 912.9603 | 3683.4344 | 0 | 0.007 | 18369300 | 239474.6766
October | 579043.2631 | 909.8223 | 3613.5023 | 0 | 0.0069 | 18020100 | 240342.2422
November | 557449.0127 | 866.9153 | 3394.3656 | 0 | 0.0065 | 16927000 | 230446.104
December | 585770.1015 | 904.9687 | 3510.5131 | 0 | 0.0067 | 17505900 | 241531.2769
Annual Sum or Average | 6982520 | 10977.1993 | 43629.7505 | 0 | 0.0831 | 217577000 | 2898830
Minimum of Months | 524759.6144 | 814.6633 | 3182.0146 | 0 | 0.0061 | 15868000 | 216785.4088
Maximum of Months | 605845.4058 | 967.2647 | 3930.3293 | 0 | 0.0074 | 19600700 | 252898.3903
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2274850000000 | 1339307.192 | 30-JAN-16:00 | 445952.007 | 310109.712 | 84930.475 | 0 | 88706.936 | 6881 | 41134.082 | 31769.211 | 162962.637 | 0 | 0 | 0 | 5541.669 | 0 | 0
February | 2082260000000 | 1340542.632 | 17-FEB-17:30 | 445952.007 | 310109.712 | 91629.656 | 0 | 96091.095 | 6881 | 41543.573 | 31769.211 | 162962.637 | 0 | 0 | 0 | 5613.817 | 0 | 0
March | 2373900000000 | 1366290.94 | 21-MAR-15:00 | 445952.007 | 310109.712 | 90339.99 | 0 | 119909.69 | 0 | 42870.808 | 31769.211 | 162962.637 | 0 | 0 | 0 | 5828.087 | 0 | 0
April | 2365850000000 | 1367342.104 | 12-APR-16:00 | 445952.007 | 310109.712 | 99374.769 | 0 | 148374.134 | 0 | 43907.995 | 31769.211 | 162962.637 | 0 | 0 | 0 | 6084.747 | 0 | 0
May | 2512680000000 | 1484921.046 | 11-MAY-15:00 | 445952.007 | 310109.712 | 109829.795 | 0 | 198844.386 | 0 | 46034.189 | 31769.211 | 162962.637 | 0 | 0 | 0 | 6537.732 | 0 | 0
June | 2544100000000 | 1509288.592 | 29-JUN-15:00 | 445952.007 | 310109.712 | 122338.809 | 0 | 259574.549 | 0 | 47922.007 | 31769.211 | 162962.637 | 0 | 0 | 0 | 6687.858 | 0 | 0
July | 2532000000000 | 1466083.623 | 31-JUL-16:00 | 445952.007 | 310109.712 | 105627.179 | 0 | 197958.319 | 0 | 45647.766 | 31769.211 | 162962.637 | 0 | 0 | 0 | 6578.625 | 0 | 0
August | 2572090000000 | 1448743.098 | 02-AUG-16:00 | 445952.007 | 310109.712 | 118301.904 | 0 | 322870.417 | 0 | 49956.784 | 31769.211 | 162962.637 | 0 | 0 | 0 | 6820.425 | 0 | 0
September | 2410490000000 | 1452803.034 | 21-SEP-16:00 | 445952.007 | 310109.712 | 115208.722 | 0 | 221424.946 | 0 | 46631.256 | 31769.211 | 162962.637 | 0 | 0 | 0 | 6620.963 | 0 | 0
October | 2364670000000 | 1397682.206 | 31-OCT-15:00 | 445952.007 | 310109.712 | 96771.922 | 0 | 136551.201 | 0 | 43632.893 | 31769.211 | 162962.637 | 0 | 0 | 0 | 5980.647 | 0 | 0
November | 2221230000000 | 1326376.885 | 22-NOV-16:30 | 445952.007 | 310109.712 | 91241.402 | 0 | 100758.901 | 6881 | 41796.503 | 31769.211 | 162962.637 | 0 | 0 | 0 | 5641.406 | 0 | 0
December | 2297200000000 | 1339048.851 | 05-DEC-16:30 | 445952.007 | 310109.712 | 87755.836 | 0 | 119339.542 | 6881 | 42483.187 | 31769.211 | 162962.637 | 0 | 0 | 0 | 5766.695 | 0 | 0
Annual Sum or Average | 28551300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2082260000000 | 1326376.885 |  | 445952.007 | 310109.712 | 84930.475 | 0 | 88706.936 | 0 | 41134.082 | 31769.211 | 162962.637 | 0 | 0 | 0 | 5541.669 | 0 | 0
Maximum of Months | 2572090000000 | 1509288.592 |  | 445952.007 | 310109.712 | 122338.809 | 0 | 322870.417 | 6881 | 49956.784 | 31769.211 | 162962.637 | 0 | 0 | 0 | 6820.425 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 689829.95 | 100446.52 | 0 | 790276.47
Cost per Total Building Area ($/m2) | 30.77 | 4.48 | 0 | 35.25
Cost per Net Conditioned Building Area ($/m2) | 30.77 | 4.48 | 0 | 35.25

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 39302.64 | 1752.84 | 1752.84
Net Site Energy | 39302.64 | 1752.84 | 1752.84
Total Source Energy | 92100.54 | 4107.55 | 4107.55
Net Source Energy | 92100.54 | 4107.55 | 4107.55
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12678.75 | 0 | 0 | 0 | 0
Cooling | 2329.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2357.13 | 0 | 0 | 0 | 0 | 0
Pumps | 1096.61 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 845.17 | 0 | 0 | 0 | 0 | 10859.06
Humidification | 215.25 | 0 | 0 | 0 | 0 | 80.07
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 711.28 | 0 | 0 | 0 | 4037.61
Refrigeration | 185.75 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24554.19 | 14748.45 | 0 | 0 | 0 | 14976.74
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.392 | 0.253 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 4.092 | 0.392 | 0.253 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 4.092 | 0.392 | 0.253 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 4.092 | 0.392 | 0.253 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.392 | 0.253 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.392 | 0.253 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 4.092 | 0.392 | 0.253 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 4.092 | 0.392 | 0.253 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.392 | 0.253 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 4.092 | 0.392 | 0.253 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 186.18 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 659.24 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2161978.22 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3194555.36 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2062194.61
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 459312.79 | 312390.43 | 146922.35 | 0.68 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 304928.41 | 231294.22 | 73634.19 | 0.76 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 683592.15 | 469346.7 | 214245.44 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1209390.36 | 827059.06 | 382331.3 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 38914.64 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11919.24 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16729.39 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 15108.51 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 49574.81 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49827.49 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16387.8 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16387.8 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 191149.98 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29819.65 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30723.64 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11415.11 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 60181.6 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 115608.04 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77778.74 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77778.74 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47067.26 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29456.07 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30009.09 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 44245.38 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50768.27 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 254568.52 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 48404.66 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204786.12 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39398.19 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7756.36 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5900.01 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30093.29 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5880.13 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4826.33 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74889.66 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74366.36 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13734.72 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13614.54 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59415.6 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59415.6 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10243.07 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10243.07 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61447.27 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61447.27 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12997.87 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12864.23 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 78183.83 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77471.08 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8988.85 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8898.9 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 43018.42 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107546.05 | -
CAV_1_HEATC | Coil:Heating:Water | 7803.1 | -
CAV_2_HEATC | Coil:Heating:Water | 191674.7 | -
VAV_1_HEATC | Coil:Heating:Water | 84648.05 | -
VAV_2_HEATC | Coil:Heating:Water | 160394.18 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.6 | 27936.95 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.9 | 25250.06 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 25.39 | 42735.63 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 44.4 | 73558.21 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19811.54 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17590.58 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29105 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 254009.2296 | 221.4672 | 1636.6771 | 0 | 0.0009 | 9873010 | 92906.4589
February | 222255.9093 | 193.5059 | 1481.4726 | 0 | 0.0008 | 8937000 | 81443.0586
March | 250957.1708 | 218.4599 | 1678.9714 | 0 | 0.0009 | 10128400 | 91979.1745
April | 235033.1919 | 204.4828 | 1593.0356 | 0 | 0.0008 | 9610130 | 86205.6718
May | 243853.9458 | 211.9458 | 1690.6211 | 0 | 0.0009 | 10199000 | 89556.2791
June | 236093.6406 | 205.0301 | 1667.3846 | 0 | 0.0009 | 10059000 | 86799.5307
July | 238654.4863 | 207.1658 | 1701.2441 | 0 | 0.0009 | 10263300 | 87789.1476
August | 245864.9717 | 213.3496 | 1766.1341 | 0 | 0.0009 | 10654800 | 90482.6855
September | 234627.4074 | 203.5967 | 1685.6631 | 0 | 0.0009 | 10169400 | 86347.8318
October | 242948.0422 | 211.0539 | 1703.0488 | 0 | 0.0009 | 10274100 | 89280.6606
November | 239777.4916 | 208.6538 | 1617.4463 | 0 | 0.0009 | 9757360 | 87922.1579
December | 252430.6738 | 220.0747 | 1629.409 | 0 | 0.0009 | 9829180 | 92337.9433
Annual Sum or Average | 2896510 | 2518.7862 | 19851.1077 | 0 | 0.0105 | 119755000 | 1063050
Minimum of Months | 222255.9093 | 193.5059 | 1481.4726 | 0 | 0.0008 | 8937000 | 81443.0586
Maximum of Months | 254009.2296 | 221.4672 | 1766.1341 | 0 | 0.0009 | 10654800 | 92906.4589
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2024340000000 | 1237655.226 | 20-JAN-14:00 | 445952.007 | 302612.437 | 82268.078 | 0 | 64554.023 | 0 | 34805.171 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6307.055 | 0 | 0
February | 1832420000000 | 1229032.908 | 15-FEB-16:30 | 445952.007 | 310109.712 | 85847.201 | 0 | 151801.106 | 0 | 39172.516 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6121.425 | 0 | 0
March | 2076710000000 | 1219918.776 | 13-MAR-12:00 | 445952.007 | 302612.437 | 76233.748 | 0 | 79863.162 | 0 | 35640.019 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6468.027 | 0 | 0
April | 1970440000000 | 1268541.087 | 13-APR-15:00 | 445952.007 | 310109.712 | 92069.597 | 0 | 130948.091 | 0 | 38407.326 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6104.85 | 0 | 0
May | 2091180000000 | 1264951.07 | 25-MAY-15:30 | 445952.007 | 310109.712 | 87844.538 | 0 | 183090.476 | 0 | 41773.17 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6152.226 | 0 | 0
June | 2062460000000 | 1254532.479 | 16-JUN-15:45 | 445952.007 | 310109.712 | 93881.666 | 0 | 168651.996 | 0 | 39503.877 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6404.281 | 0 | 0
July | 2104360000000 | 1276232.24 | 03-JUL-12:00 | 445952.007 | 302612.437 | 85330.46 | 0 | 204232.938 | 0 | 40591.237 | 27066.304 | 162962.637 | 0 | 0 | 0 | 7484.22 | 0 | 0
August | 2184640000000 | 1267960.806 | 15-AUG-12:15 | 445952.007 | 302612.437 | 83934.695 | 0 | 197487.994 | 0 | 40567.685 | 27066.304 | 162962.637 | 0 | 0 | 0 | 7377.046 | 0 | 0
September | 2085100000000 | 1312081.844 | 28-SEP-15:00 | 445952.007 | 310109.712 | 101675.61 | 0 | 216211.992 | 0 | 41330.803 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6772.778 | 0 | 0
October | 2106570000000 | 1252769.064 | 13-OCT-15:00 | 445952.007 | 310109.712 | 91425.137 | 0 | 169050.053 | 0 | 39899.32 | 27066.304 | 162962.637 | 0 | 0 | 0 | 6303.893 | 0 | 0
November | 2000620000000 | 1217814.375 | 16-NOV-16:15 | 445952.007 | 310109.712 | 81196.673 | 0 | 144407.342 | 0 | 40283.406 | 27066.304 | 162962.637 | 0 | 0 | 0 | 5836.293 | 0 | 0
December | 2015350000000 | 1230398.864 | 29-DEC-16:00 | 445952.007 | 310109.712 | 79862.457 | 0 | 41196.009 | 6881 | 33055.565 | 27066.304 | 162962.637 | 0 | 0 | 0 | 5339.279 | 0 | 0
Annual Sum or Average | 24554200000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1832420000000 | 1217814.375 |  | 445952.007 | 302612.437 | 76233.748 | 0 | 41196.009 | 0 | 33055.565 | 27066.304 | 162962.637 | 0 | 0 | 0 | 5339.279 | 0 | 0
Maximum of Months | 2184640000000 | 1312081.844 |  | 445952.007 | 310109.712 | 101675.61 | 0 | 216211.992 | 6881 | 41773.17 | 27066.304 | 162962.637 | 0 | 0 | 0 | 7484.22 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 887435.91 | 124118.34 | 0 | 1011554.24
Cost per Total Building Area ($/m2) | 39.58 | 5.54 | 0 | 45.11
Cost per Net Conditioned Building Area ($/m2) | 39.58 | 5.54 | 0 | 45.11

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 42070.77 | 1876.3 | 1876.3
Net Site Energy | 42070.77 | 1876.3 | 1876.3
Total Source Energy | 114508.45 | 5106.91 | 5106.91
Net Source Energy | 114508.45 | 5106.91 | 5106.91
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12386.36 | 0 | 0 | 0 | 0
Cooling | 3821.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2392.99 | 0 | 0 | 0 | 0 | 0
Pumps | 1477.16 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 901.75 | 0 | 0 | 0 | 0 | 17727.04
Humidification | 1299.78 | 0 | 0 | 0 | 0 | 483.52
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 722.46 | 0 | 0 | 0 | 4037.61
Refrigeration | 185.84 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 27603.53 | 14467.23 | 0 | 0 | 0 | 22248.17
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.354 | 0.355 | 0.274 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.354 | 0.355 | 0.274 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.354 | 0.355 | 0.274 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.354 | 0.355 | 0.274 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.354 | 0.355 | 0.274 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.354 | 0.355 | 0.274 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.354 | 0.355 | 0.274 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.354 | 0.355 | 0.274 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.354 | 0.355 | 0.274 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.354 | 0.355 | 0.274 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.354 | 0.355 | 0.274 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.354 | 0.355 | 0.274 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.354 | 0.355 | 0.274 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.354 | 0.355 | 0.274 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.354 | 0.355 | 0.274 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.355 | 0.274 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.355 | 0.274 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.355 | 0.274 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.355 | 0.274 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.355 | 0.274 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.355 | 0.274 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.355 | 0.274 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.355 | 0.274 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.355 | 0.274 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.355 | 0.274 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.355 | 0.274 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.355 | 0.274 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.355 | 0.274 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.355 | 0.274 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.355 | 0.274 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.355 | 0.274 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.355 | 0.274 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 186.18 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 659.24 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2953511.71 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3558022.13 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2817195.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 549549.07 | 353195.83 | 196353.24 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 344427.64 | 253854.93 | 90572.71 | 0.74 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 858069.98 | 562356.82 | 295713.16 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1407415.38 | 917375.25 | 490040.14 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 68179.31 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11817.45 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16646.51 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 15318.05 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 45504.69 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51205.9 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16306.61 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16306.61 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 186527.7 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29820.37 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34783.71 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13728.24 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 61476.97 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 123158.77 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77393.42 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77393.42 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47609.46 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29456.11 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30015.16 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 42616.19 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54624.42 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 266383.58 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53221.67 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204747.08 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35777.25 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7096.04 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4104.17 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30849.78 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6970.84 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6325.8 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11176.9 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11153.72 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64158.65 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63984.45 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10704.62 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10684.13 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11474.36 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11435.01 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 80040.07 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 79769.73 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11190.72 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11155.28 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42805.31 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107013.27 | -
CAV_1_HEATC | Coil:Heating:Water | 56215.75 | -
CAV_2_HEATC | Coil:Heating:Water | 216982.49 | -
VAV_1_HEATC | Coil:Heating:Water | 155461.74 | -
VAV_2_HEATC | Coil:Heating:Water | 271147.01 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.58 | 27906.67 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.5 | 26254.33 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 27.63 | 46210 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 44.52 | 73760.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27064.85 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19591.98 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 39760.79 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 459216.8723 | 820.2708 | 2229.5485 | 0 | 0.0092 | 138638.6706 | 195825.1325
February | 408834.2372 | 736.3299 | 2018.3658 | 0 | 0.0083 | 125509.0276 | 174893.9341
March | 453210.295 | 829.2168 | 2309.0237 | 0 | 0.0094 | 143587.7916 | 195062.7715
April | 428297.7784 | 787.1197 | 2201.3368 | 0 | 0.009 | 136892.4381 | 184658.9446
May | 450189.4113 | 837.4429 | 2369.5722 | 0 | 0.0097 | 147357.8063 | 195020.1321
June | 457754.9029 | 864.0288 | 2478.4823 | 0 | 0.0101 | 154134.8581 | 199441.5865
July | 477956.1996 | 906.5236 | 2611.9577 | 0 | 0.0106 | 162437.0097 | 208642.2365
August | 491098.0309 | 932.6966 | 2690.6627 | 0 | 0.0109 | 167332.0597 | 214493.088
September | 439192.3749 | 821.9289 | 2338.9808 | 0 | 0.0095 | 145457.0619 | 190708.2097
October | 446721.991 | 826.6205 | 2327.1797 | 0 | 0.0095 | 144720.055 | 193118.274
November | 433582.8153 | 793.5723 | 2210.4995 | 0 | 0.009 | 137461.1094 | 186639.472
December | 447841.9377 | 806.0971 | 2208.2503 | 0 | 0.0091 | 137316.5382 | 191536.3417
Annual Sum or Average | 5393900 | 9961.8477 | 27993.8599 | 0 | 0.1143 | 1740840 | 2330040
Minimum of Months | 408834.2372 | 736.3299 | 2018.3658 | 0 | 0.0083 | 125509.0276 | 174893.9341
Maximum of Months | 491098.0309 | 932.6966 | 2690.6627 | 0 | 0.0109 | 167332.0597 | 214493.088
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2198310000000 | 1300253.817 | 05-JAN-16:15 | 445952.007 | 310109.712 | 79556.698 | 0 | 87601.98 | 0 | 45818.673 | 36975.695 | 162962.637 | 0 | 0 | 0 | 5299.612 | 0 | 0
February | 1990120000000 | 1258105.39 | 16-FEB-16:15 | 445952.007 | 310109.712 | 80323.013 | 0 | 68391.913 | 0 | 44875.946 | 27515.334 | 162962.637 | 0 | 0 | 0 | 5206.5 | 0 | 0
March | 2276790000000 | 1311220.335 | 17-MAR-16:00 | 445952.007 | 310109.712 | 82072.326 | 0 | 114727.098 | 0 | 47304.076 | 36975.695 | 162962.637 | 0 | 0 | 0 | 5749.539 | 0 | 0
April | 2170620000000 | 1305293.166 | 20-APR-15:00 | 445952.007 | 310109.712 | 81149.736 | 0 | 104934.795 | 0 | 46997.169 | 36975.695 | 162962.637 | 0 | 0 | 0 | 5658.931 | 0 | 0
May | 2336560000000 | 1419086.383 | 31-MAY-15:00 | 445952.007 | 310109.712 | 83506.477 | 0 | 318278.058 | 0 | 54879.45 | 36975.695 | 162962.637 | 0 | 0 | 0 | 6422.348 | 0 | 0
June | 2444020000000 | 1535795.58 | 30-JUN-16:00 | 445952.007 | 310109.712 | 99180.949 | 0 | 416208.789 | 0 | 57585.811 | 36975.695 | 162962.637 | 0 | 0 | 0 | 6819.979 | 0 | 0
July | 2575670000000 | 1546154.295 | 25-JUL-10:45 | 445952.007 | 310109.712 | 88886.883 | 0 | 432108.313 | 0 | 57280.812 | 36975.695 | 162962.637 | 0 | 0 | 0 | 11878.235 | 0 | 0
August | 2653280000000 | 1606306 | 09-AUG-16:00 | 445952.007 | 310109.712 | 97223.191 | 0 | 487393.773 | 0 | 59023.735 | 36975.695 | 162962.637 | 0 | 0 | 0 | 6665.25 | 0 | 0
September | 2306430000000 | 1398466.636 | 27-SEP-15:15 | 445952.007 | 310109.712 | 86593.749 | 0 | 295320.999 | 0 | 54284.776 | 36975.695 | 162962.637 | 0 | 0 | 0 | 6267.061 | 0 | 0
October | 2294740000000 | 1358958.033 | 03-OCT-10:45 | 445952.007 | 310109.712 | 79700.351 | 0 | 259420.791 | 0 | 52834.099 | 36975.695 | 162962.637 | 0 | 0 | 0 | 11002.74 | 0 | 0
November | 2179640000000 | 1308758.519 | 03-NOV-13:00 | 445952.007 | 302612.437 | 83095.012 | 0 | 218494.309 | 0 | 51563.718 | 36975.695 | 162962.637 | 0 | 0 | 0 | 7102.703 | 0 | 0
December | 2177350000000 | 1273103.47 | 06-DEC-16:00 | 445952.007 | 310109.712 | 79161.886 | 0 | 67552.852 | 6881 | 44865.66 | 24914.463 | 162962.637 | 0 | 0 | 0 | 5210.217 | 0 | 0
Annual Sum or Average | 27603500000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1990120000000 | 1258105.39 |  | 445952.007 | 302612.437 | 79161.886 | 0 | 67552.852 | 0 | 44865.66 | 24914.463 | 162962.637 | 0 | 0 | 0 | 5206.5 | 0 | 0
Maximum of Months | 2653280000000 | 1606306 |  | 445952.007 | 310109.712 | 99180.949 | 0 | 487393.773 | 6881 | 59023.735 | 36975.695 | 162962.637 | 0 | 0 | 0 | 11878.235 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 422827.09 | 145747.9 | 0 | 568574.99
Cost per Total Building Area ($/m2) | 18.86 | 6.5 | 0 | 25.36
Cost per Net Conditioned Building Area ($/m2) | 18.86 | 6.5 | 0 | 25.36

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 38241.29 | 1705.51 | 1705.51
Net Site Energy | 38241.29 | 1705.51 | 1705.51
Total Source Energy | 101468.26 | 4525.34 | 4525.34
Net Source Energy | 101468.26 | 4525.34 | 4525.34
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9350.49 | 0 | 0 | 0 | 0
Cooling | 2366.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.12 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2678.15 | 0 | 0 | 0 | 0 | 0
Pumps | 1076.57 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 627.43 | 0 | 0 | 0 | 0 | 18148.17
Humidification | 2364.71 | 0 | 0 | 0 | 0 | 879.67
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 709.04 | 0 | 0 | 0 | 4037.61
Refrigeration | 185.26 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26823.35 | 11417.95 | 0 | 0 | 0 | 23065.45
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.362 | 0.225 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 4.092 | 0.362 | 0.225 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 4.092 | 0.362 | 0.225 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 4.092 | 0.362 | 0.225 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 4.092 | 0.362 | 0.225 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 4.092 | 0.362 | 0.225 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 4.092 | 0.362 | 0.225 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.362 | 0.225 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.362 | 0.225 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.362 | 0.225 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 4.092 | 0.362 | 0.225 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 4.092 | 0.362 | 0.225 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.362 | 0.225 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.362 | 0.225 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 4.092 | 0.362 | 0.225 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.362 | 0.225 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.362 | 0.225 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.362 | 0.225 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.362 | 0.225 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.362 | 0.225 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.362 | 0.225 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.362 | 0.225 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.362 | 0.225 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.362 | 0.225 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.362 | 0.225 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.362 | 0.225 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.362 | 0.225 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.362 | 0.225 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.362 | 0.225 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.362 | 0.225 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.362 | 0.225 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.362 | 0.225 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 186.18 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 659.24 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2120305.42 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3148819.7 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2022445.17
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 444836.95 | 272351.82 | 172485.13 | 0.61 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 300128.65 | 216986.43 | 83142.22 | 0.72 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 721880.17 | 450766 | 271114.16 | 0.62 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1195921.98 | 740091.61 | 455830.37 | 0.62 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 53743.65 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10607.76 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13775.78 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 14139.7 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 42786.59 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 50280.67 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13494.5 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13494.5 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 181334.66 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29841.49 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31485.08 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12498.83 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 60054.78 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 119379.82 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64046.75 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64046.75 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45010.81 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29432.35 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29991.16 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 40677.24 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50187.96 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 258042.51 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50427.88 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198620.38 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33885.64 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6434.31 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3496.28 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 29852.53 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6306.48 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5391.16 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9563.89 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9517.03 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58751.68 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58447.07 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9152.43 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9109.1 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10272.33 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10201.1 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77738.07 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77261.68 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9971.1 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9906.48 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35423.44 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88558.59 | -
CAV_1_HEATC | Coil:Heating:Water | 34577.79 | -
CAV_2_HEATC | Coil:Heating:Water | 194652.58 | -
VAV_1_HEATC | Coil:Heating:Water | 119080.8 | -
VAV_2_HEATC | Coil:Heating:Water | 224463.6 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.51 | 29473.94 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.89 | 30109.18 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.95 | 50092.89 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 48.45 | 80264.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19429.66 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17338.74 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 28543.99 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 658436.0123 | 1096.1334 | 2700.7608 | 0 | 0.0107 | 2808000 | 276779.9405
February | 589575.2037 | 985.7049 | 2441.0831 | 0 | 0.0096 | 2538040 | 248246.3662
March | 668809.8807 | 1123.5054 | 2797.9893 | 0 | 0.011 | 2909160 | 282131.5953
April | 641245.2178 | 1084.2409 | 2720.7767 | 0 | 0.0107 | 2828930 | 271194.2533
May | 673101.5359 | 1145.7994 | 2897.5896 | 0 | 0.0114 | 3012820 | 285421.6416
June | 636463.9763 | 1086.888 | 2758.5743 | 0 | 0.0108 | 2868300 | 270224.8234
July | 639216.0935 | 1093.0555 | 2778.4462 | 0 | 0.0109 | 2888980 | 271537.2569
August | 654814.2714 | 1119.7159 | 2846.1791 | 0 | 0.0112 | 2959400 | 278162.1087
September | 607534.7497 | 1033.3473 | 2610.7896 | 0 | 0.0102 | 2714610 | 257536.3491
October | 637526.7561 | 1076.8147 | 2698.8355 | 0 | 0.0106 | 2806110 | 269509.9417
November | 631224.6292 | 1057.8707 | 2627.2364 | 0 | 0.0104 | 2731610 | 266031.6807
December | 649019.2089 | 1080.3427 | 2661.5174 | 0 | 0.0105 | 2767200 | 272810.3013
Annual Sum or Average | 7686970 | 12983.4188 | 32539.7778 | 0 | 0.1279 | 33833200 | 3249590
Minimum of Months | 589575.2037 | 985.7049 | 2441.0831 | 0 | 0.0096 | 2538040 | 248246.3662
Maximum of Months | 673101.5359 | 1145.7994 | 2897.5896 | 0 | 0.0114 | 3012820 | 285421.6416
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2226220000000 | 1296945.289 | 20-JAN-16:15 | 445952.007 | 310109.712 | 91842.519 | 0 | 59974.889 | 0 | 33715.808 | 26544.593 | 162962.637 | 0 | 0 | 0 | 5378.926 | 0 | 0
February | 2012190000000 | 1334737.658 | 13-FEB-16:30 | 445952.007 | 310109.712 | 88349.051 | 0 | 100560.106 | 0 | 36155.312 | 26544.593 | 162962.637 | 0 | 0 | 0 | 5803.994 | 0 | 0
March | 2306420000000 | 1359105.321 | 02-MAR-16:15 | 445952.007 | 310109.712 | 97223.695 | 0 | 112249.576 | 0 | 37017.218 | 26544.593 | 162962.637 | 0 | 0 | 0 | 5882.775 | 0 | 0
April | 2242810000000 | 1421294.489 | 21-APR-16:00 | 445952.007 | 310109.712 | 109759.458 | 0 | 144345.761 | 0 | 38744.224 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6330.513 | 0 | 0
May | 2388600000000 | 1413581.021 | 12-MAY-16:00 | 445952.007 | 310109.712 | 112865.198 | 0 | 147592.683 | 0 | 38917.143 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6316.508 | 0 | 0
June | 2274030000000 | 1450566.916 | 27-JUN-16:00 | 445952.007 | 310109.712 | 115613.995 | 0 | 175859.777 | 0 | 39963.514 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6631.759 | 0 | 0
July | 2290410000000 | 1428810.834 | 31-JUL-16:00 | 445952.007 | 310109.712 | 111625.252 | 0 | 191566.769 | 0 | 39937.829 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6719.463 | 0 | 0
August | 2346250000000 | 1352404.229 | 01-AUG-16:00 | 445952.007 | 310109.712 | 116820.652 | 0 | 241033.77 | 0 | 42144.796 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6836.061 | 0 | 0
September | 2152180000000 | 1387160.008 | 20-SEP-16:00 | 445952.007 | 310109.712 | 116642.606 | 0 | 169918.149 | 0 | 39616.736 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6507.208 | 0 | 0
October | 2224720000000 | 1348406.107 | 13-OCT-15:15 | 445952.007 | 310109.712 | 104984.941 | 0 | 139750.481 | 0 | 38232.363 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6199.64 | 0 | 0
November | 2165650000000 | 1308033.04 | 13-NOV-17:00 | 445952.007 | 310109.712 | 85502.062 | 0 | 64953.392 | 6881 | 33926.668 | 26544.593 | 162962.637 | 0 | 0 | 0 | 5478.635 | 0 | 0
December | 2193870000000 | 1268012.233 | 05-DEC-16:15 | 445952.007 | 310109.712 | 89647.11 | 0 | 67306.487 | 0 | 34202.4 | 26544.593 | 162962.637 | 0 | 0 | 0 | 5464.3 | 0 | 0
Annual Sum or Average | 26823300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2012190000000 | 1268012.233 |  | 445952.007 | 310109.712 | 85502.062 | 0 | 59974.889 | 0 | 33715.808 | 26544.593 | 162962.637 | 0 | 0 | 0 | 5378.926 | 0 | 0
Maximum of Months | 2388600000000 | 1450566.916 |  | 445952.007 | 310109.712 | 116820.652 | 0 | 241033.77 | 6881 | 42144.796 | 26544.593 | 162962.637 | 0 | 0 | 0 | 6836.061 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 275338.68 | 81817.66 | 0 | 357156.34
Cost per Total Building Area ($/m2) | 12.28 | 3.65 | 0 | 15.93
Cost per Net Conditioned Building Area ($/m2) | 12.28 | 3.65 | 0 | 15.93

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 39696.99 | 1770.43 | 1770.43
Net Site Energy | 39696.99 | 1770.43 | 1770.43
Total Source Energy | 59403.34 | 2649.3 | 2649.3
Net Source Energy | 59403.34 | 2649.3 | 2649.3
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12880.46 | 0 | 0 | 0 | 0
Cooling | 2029.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2401.07 | 0 | 0 | 0 | 0 | 0
Pumps | 1099.87 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 788.92 | 0 | 0 | 0 | 0 | 10035.93
Humidification | 672.9 | 0 | 0 | 0 | 0 | 250.32
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 759.3 | 0 | 0 | 0 | 4037.61
Refrigeration | 182.12 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24698.82 | 14998.17 | 0 | 0 | 0 | 14323.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.392 | 0.253 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 4.092 | 0.392 | 0.253 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 4.092 | 0.392 | 0.253 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 4.092 | 0.392 | 0.253 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 4.092 | 0.392 | 0.253 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 4.092 | 0.392 | 0.253 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.392 | 0.253 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 4.092 | 0.392 | 0.253 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 4.092 | 0.392 | 0.253 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 4.092 | 0.392 | 0.253 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 4.092 | 0.392 | 0.253 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 4.092 | 0.392 | 0.253 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 4.092 | 0.392 | 0.253 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 4.092 | 0.392 | 0.253 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 4.092 | 0.392 | 0.253 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 186.18 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 659.24 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2214720.07 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3417857.38 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2112502.22
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 472793.2 | 316570.19 | 156223 | 0.67 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 302748.19 | 230828.6 | 71919.59 | 0.76 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 704896.45 | 477117.52 | 227778.93 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1216911.27 | 820067.63 | 396843.65 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 47404.71 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10902.44 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16499.34 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 14278.41 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 46358.25 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51020.56 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16162.45 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16162.45 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 184917.42 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29821.34 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31856.94 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12921.96 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 61733.22 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 118758.67 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76709.21 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76709.21 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46077.39 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29416.76 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29976.84 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41033.69 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52017.45 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 261312.59 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51612.52 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204671.49 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38941.57 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7330.15 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5416.42 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30588.27 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6524.78 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5530.96 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 71033.19 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 70806.2 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13401.52 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13347.07 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 63424.91 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63097.08 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10102.22 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10102.22 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12297.85 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12241.33 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 80377.92 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 80008.55 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10376.17 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10330.15 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42426.88 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 106067.2 | -
CAV_1_HEATC | Coil:Heating:Water | 61597.69 | -
CAV_2_HEATC | Coil:Heating:Water | 210203.15 | -
VAV_1_HEATC | Coil:Heating:Water | 122003.32 | -
VAV_2_HEATC | Coil:Heating:Water | 224302.8 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.83 | 28335.64 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.42 | 26134.45 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 25.91 | 43610.77 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 44.16 | 73154.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20294.84 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18820.18 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29815.02 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 177829.1671 | 230.553 | 442.1543 | 0 | 0.0019 | 5839220 | 68951.2462
February | 157218.7299 | 205.6228 | 402.3433 | 0 | 0.0017 | 5313780 | 61151.5921
March | 172825.0842 | 227.6445 | 452.5651 | 0 | 0.0019 | 5977340 | 67394.3108
April | 161394.2959 | 213.5517 | 428.7854 | 0 | 0.0018 | 5663420 | 63040.0161
May | 161532.3398 | 216.6723 | 447.9105 | 0 | 0.0019 | 5916510 | 63408.5936
June | 155197.6514 | 210.695 | 446.4333 | 0 | 0.0018 | 5897390 | 61191.8154
July | 157731.9664 | 215.6147 | 463.1678 | 0 | 0.0019 | 6118680 | 62349.476
August | 161311.4009 | 222.0381 | 483.4501 | 0 | 0.002 | 6386840 | 63928.2929
September | 155331.6119 | 209.9307 | 440.7779 | 0 | 0.0018 | 5822540 | 61143.3035
October | 164670.7641 | 218.0881 | 438.7742 | 0 | 0.0018 | 5795390 | 64341.3302
November | 168270.462 | 219.9531 | 429.8343 | 0 | 0.0018 | 5676840 | 65436.9779
December | 175116.3087 | 226.2919 | 430.6591 | 0 | 0.0018 | 5687280 | 67819.6883
Annual Sum or Average | 1968430 | 2616.6561 | 5306.8555 | 0 | 0.0222 | 70095200 | 770156.6431
Minimum of Months | 155197.6514 | 205.6228 | 402.3433 | 0 | 0.0017 | 5313780 | 61143.3035
Maximum of Months | 177829.1671 | 230.553 | 483.4501 | 0 | 0.002 | 6386840 | 68951.2462
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2057510000000 | 1220127.182 | 03-JAN-17:00 | 445952.007 | 310109.712 | 77911.823 | 0 | 29364.3 | 6881 | 32868.467 | 6812.413 | 162962.637 | 0 | 0 | 0 | 5114.898 | 0 | 0
February | 1872370000000 | 1230927.442 | 22-FEB-11:45 | 445952.007 | 310109.712 | 77106.581 | 0 | 78959.944 | 0 | 36154.617 | 27726.592 | 162962.637 | 0 | 0 | 0 | 9673.102 | 0 | 0
March | 2106180000000 | 1234407.736 | 23-MAR-15:00 | 445952.007 | 310109.712 | 85097.667 | 0 | 74915.205 | 0 | 35912.51 | 27726.592 | 162962.637 | 0 | 0 | 0 | 5627.02 | 0 | 0
April | 1995570000000 | 1229100.037 | 14-APR-16:00 | 445952.007 | 310109.712 | 86179.213 | 0 | 112420.945 | 0 | 38000.127 | 27726.592 | 162962.637 | 0 | 0 | 0 | 5958.116 | 0 | 0
May | 2084750000000 | 1266288.081 | 05-MAY-15:00 | 445952.007 | 310109.712 | 89386.378 | 0 | 182740.819 | 0 | 41077.824 | 27726.592 | 162962.637 | 0 | 0 | 0 | 6332.112 | 0 | 0
June | 2078010000000 | 1269241.561 | 27-JUN-16:00 | 445952.007 | 310109.712 | 91215.754 | 0 | 161297.15 | 0 | 39694.949 | 27726.592 | 162962.637 | 0 | 0 | 0 | 6406.593 | 0 | 0
July | 2155980000000 | 1309195.182 | 27-JUL-16:00 | 445952.007 | 310109.712 | 97003.615 | 0 | 216042.668 | 0 | 42986.506 | 27726.592 | 162962.637 | 0 | 0 | 0 | 6411.445 | 0 | 0
August | 2250470000000 | 1307341.964 | 18-AUG-16:00 | 445952.007 | 310109.712 | 97180.073 | 0 | 214309.7 | 0 | 42625.056 | 27726.592 | 162962.637 | 0 | 0 | 0 | 6476.187 | 0 | 0
September | 2051640000000 | 1308457.42 | 01-SEP-16:15 | 445952.007 | 310109.712 | 94366.044 | 0 | 218498.655 | 0 | 42311.101 | 27726.592 | 162962.637 | 0 | 0 | 0 | 6530.672 | 0 | 0
October | 2042070000000 | 1234115.39 | 17-OCT-16:00 | 445952.007 | 310109.712 | 84620.554 | 0 | 129954.98 | 0 | 38407.148 | 27726.592 | 162962.637 | 0 | 0 | 0 | 6069.859 | 0 | 0
November | 2000290000000 | 1211055.773 | 28-NOV-17:00 | 445952.007 | 310109.712 | 79218.597 | 0 | 23385.733 | 6881 | 32361.732 | 3214.018 | 162962.637 | 0 | 0 | 0 | 5044.68 | 0 | 0
December | 2003980000000 | 1175335.857 | 07-DEC-17:00 | 445952.007 | 310109.712 | 80883.443 | 0 | 32961.718 | 6881 | 33153.041 | 27726.592 | 162962.637 | 0 | 0 | 0 | 5281.508 | 0 | 0
Annual Sum or Average | 24698800000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1872370000000 | 1175335.857 |  | 445952.007 | 310109.712 | 77106.581 | 0 | 23385.733 | 0 | 32361.732 | 3214.018 | 162962.637 | 0 | 0 | 0 | 5044.68 | 0 | 0
Maximum of Months | 2250470000000 | 1309195.182 |  | 445952.007 | 310109.712 | 97180.073 | 0 | 218498.655 | 6881 | 42986.506 | 27726.592 | 162962.637 | 0 | 0 | 0 | 9673.102 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 449984.9 | 124322.93 | 0 | 574307.83
Cost per Total Building Area ($/m2) | 20.07 | 5.54 | 0 | 25.61
Cost per Net Conditioned Building Area ($/m2) | 20.07 | 5.54 | 0 | 25.61

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 42039.24 | 1874.89 | 1874.89
Net Site Energy | 42039.24 | 1874.89 | 1874.89
Total Source Energy | 111259.3 | 4962.01 | 4962.01
Net Source Energy | 111259.3 | 4962.01 | 4962.01
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13265.26 | 0 | 0 | 0 | 0
Cooling | 2807.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2413.72 | 0 | 0 | 0 | 0 | 0
Pumps | 1393.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 740.78 | 0 | 0 | 0 | 0 | 14018.2
Humidification | 1568.53 | 0 | 0 | 0 | 0 | 583.49
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 784.57 | 0 | 0 | 0 | 4037.61
Refrigeration | 182.26 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26630.99 | 15408.25 | 0 | 0 | 0 | 18639.3
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.354 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.354 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.354 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.354 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.354 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.354 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.354 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.354 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.354 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.354 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2910074.77 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3729732.34 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2775763.63
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 547565.39 | 350340.57 | 197224.82 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 329146.76 | 245245.26 | 83901.5 | 0.75 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 846741.96 | 552599.06 | 294142.89 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1381026.91 | 895897.31 | 485129.6 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 64205.08 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11659.23 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16366.83 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 14143.09 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 43861.77 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51384.15 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16032.64 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16032.64 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 187004.62 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29822.13 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34703.04 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13916 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 62708.31 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 124647.23 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76093.12 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76093.12 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 47998.38 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29450.7 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30009.71 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 40316.75 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54164.75 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 265209.83 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52987.37 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198669.39 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36025.37 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7072.29 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4175.13 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30594.5 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6918.16 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6114.42 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11268.96 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11250.07 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64870.77 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64697.65 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10626.18 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10608.47 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11736.82 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11698.58 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 82004.5 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 81736.36 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11372.66 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11339.16 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42086.12 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 105215.31 | -
CAV_1_HEATC | Coil:Heating:Water | 95718.82 | -
CAV_2_HEATC | Coil:Heating:Water | 208604.72 | -
VAV_1_HEATC | Coil:Heating:Water | 192810.92 | -
VAV_2_HEATC | Coil:Heating:Water | 334739.05 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.81 | 28296.52 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.58 | 26397.2 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 27.73 | 46373.15 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 44.37 | 73504.76 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26666.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20537.49 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 39176.03 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 840077.6336 | 1438.4519 | 4055.3876 | 0 | 0.0124 | 933477.8169 | 355376.3853
February | 750189.5802 | 1292.9754 | 3672.0422 | 0 | 0.0112 | 845250.9635 | 318157.9226
March | 828969.0841 | 1439.6124 | 4122.7445 | 0 | 0.0126 | 949011.8718 | 352606.7169
April | 772939.4506 | 1348.1124 | 3878.8761 | 0 | 0.0118 | 892884.2609 | 329328.9994
May | 822839.433 | 1445.1384 | 4189.2004 | 0 | 0.0127 | 964332.4246 | 351545.5542
June | 851977.4354 | 1507.1339 | 4402.4147 | 0 | 0.0134 | 1013430 | 365028.9118
July | 891517.7108 | 1580.7921 | 4628.9841 | 0 | 0.014 | 1065590 | 382324.8254
August | 915428.3196 | 1623.07 | 4752.4199 | 0 | 0.0144 | 1094000 | 392567.432
September | 819843.3357 | 1444.9771 | 4204.5239 | 0 | 0.0128 | 967866.9267 | 350753.1944
October | 809410.3888 | 1415.4604 | 4084.3062 | 0 | 0.0124 | 940177.8096 | 345225.6606
November | 777738.842 | 1350.7063 | 3868.3299 | 0 | 0.0118 | 890448.4322 | 330821.5557
December | 821647.9491 | 1412.1818 | 3998.1129 | 0 | 0.0122 | 920301.9776 | 348085.5819
Annual Sum or Average | 9902580 | 17298.6122 | 49857.3425 | 0 | 0.1519 | 11476800 | 4221820
Minimum of Months | 750189.5802 | 1292.9754 | 3672.0422 | 0 | 0.0112 | 845250.9635 | 318157.9226
Maximum of Months | 915428.3196 | 1623.07 | 4752.4199 | 0 | 0.0144 | 1094000 | 392567.432
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2166060000000 | 1228254.047 | 26-JAN-16:00 | 445952.007 | 310109.712 | 78897.259 | 0 | 170.347 | 6881 | 39743.768 | 0 | 162962.637 | 0 | 0 | 0 | 4915.974 | 0 | 0
February | 1961340000000 | 1210413.494 | 09-FEB-17:15 | 445952.007 | 310109.712 | 79365.044 | 0 | 8295.475 | 6881 | 40482.909 | 0 | 162962.637 | 0 | 0 | 0 | 4961.311 | 0 | 0
March | 2202110000000 | 1255991.458 | 31-MAR-16:45 | 445952.007 | 310109.712 | 83633.291 | 0 | 136137.855 | 0 | 47127.001 | 36431.898 | 162962.637 | 0 | 0 | 0 | 5994.041 | 0 | 0
April | 2071870000000 | 1299667.233 | 27-APR-16:00 | 445952.007 | 310109.712 | 84898.983 | 0 | 100362.958 | 0 | 45944.747 | 36431.898 | 162962.637 | 0 | 0 | 0 | 5729.766 | 0 | 0
May | 2237660000000 | 1367962.826 | 30-MAY-16:00 | 445952.007 | 310109.712 | 80069.606 | 0 | 273583.986 | 0 | 52401.542 | 36431.898 | 162962.637 | 0 | 0 | 0 | 6451.437 | 0 | 0
June | 2351580000000 | 1503826.692 | 08-JUN-12:00 | 445952.007 | 302612.437 | 91941.115 | 0 | 400250.671 | 0 | 56118.248 | 36431.898 | 162962.637 | 0 | 0 | 0 | 7557.679 | 0 | 0
July | 2472620000000 | 1491433.416 | 14-JUL-10:45 | 445952.007 | 310109.712 | 93678.091 | 0 | 374873.107 | 0 | 55591.133 | 36431.898 | 162962.637 | 0 | 0 | 0 | 11834.832 | 0 | 0
August | 2538550000000 | 1562431.728 | 04-AUG-15:00 | 445952.007 | 310109.712 | 99532.245 | 0 | 443130.089 | 0 | 57681.818 | 36431.898 | 162962.637 | 0 | 0 | 0 | 6631.322 | 0 | 0
September | 2245860000000 | 1416022.764 | 07-SEP-16:00 | 445952.007 | 310109.712 | 89765.506 | 0 | 309085.076 | 0 | 55529.48 | 36431.898 | 162962.637 | 0 | 0 | 0 | 6186.447 | 0 | 0
October | 2181610000000 | 1329035.565 | 31-OCT-09:00 | 445952.007 | 310109.712 | 79338.96 | 0 | 234987.453 | 0 | 52371.33 | 36431.898 | 162962.637 | 0 | 0 | 0 | 6881.568 | 0 | 0
November | 2066220000000 | 1343287.54 | 02-NOV-09:30 | 445952.007 | 310109.712 | 79765.495 | 0 | 248266.737 | 0 | 52959.605 | 36431.898 | 162962.637 | 0 | 0 | 0 | 6839.449 | 0 | 0
December | 2135490000000 | 1211163.295 | 05-DEC-16:00 | 445952.007 | 310109.712 | 78115.246 | 0 | 17345.171 | 6881 | 41129.42 | 0 | 162962.637 | 0 | 0 | 0 | 4975.744 | 0 | 0
Annual Sum or Average | 26631000000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1961340000000 | 1210413.494 |  | 445952.007 | 302612.437 | 78115.246 | 0 | 170.347 | 0 | 39743.768 | 0 | 162962.637 | 0 | 0 | 0 | 4915.974 | 0 | 0
Maximum of Months | 2538550000000 | 1562431.728 |  | 445952.007 | 310109.712 | 99532.245 | 0 | 443130.089 | 6881 | 57681.818 | 36431.898 | 162962.637 | 0 | 0 | 0 | 11834.832 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 726749.96 | 136927.73 | 0 | 863677.68
Cost per Total Building Area ($/m2) | 32.41 | 6.11 | 0 | 38.52
Cost per Net Conditioned Building Area ($/m2) | 32.41 | 6.11 | 0 | 38.52

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 38340.67 | 1709.94 | 1709.94
Net Site Energy | 38340.67 | 1709.94 | 1709.94
Total Source Energy | 100199.22 | 4468.74 | 4468.74
Net Source Energy | 100199.22 | 4468.74 | 4468.74
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9996.42 | 0 | 0 | 0 | 0
Cooling | 1868.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2605.73 | 0 | 0 | 0 | 0 | 0
Pumps | 1013.86 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 545.9 | 0 | 0 | 0 | 0 | 14117.75
Humidification | 2464.44 | 0 | 0 | 0 | 0 | 916.77
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 781.34 | 0 | 0 | 0 | 4037.61
Refrigeration | 181.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26204.5 | 12136.18 | 0 | 0 | 0 | 19072.13
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.354 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.354 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.354 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.354 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.354 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.354 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.354 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.354 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.354 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.354 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.354 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.354 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.354 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.354 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.354 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2073141.41 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3271864.47 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1977457.96
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 442735.27 | 267149.48 | 175585.79 | 0.6 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 280479.53 | 205340.35 | 75139.18 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 716580.08 | 441269.88 | 275310.2 | 0.62 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1173723.29 | 716457.21 | 457266.07 | 0.61 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 52961.3 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10203.99 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13750.47 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12235.5 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 39644.57 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49561.12 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13469.71 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13469.71 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 178811.69 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29841.75 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30421.33 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11871.81 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57657.43 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 111165.71 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 63929.09 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63929.09 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41998.75 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29412.24 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29972.44 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37066.31 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49079.13 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 255443.19 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49829.45 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198619.4 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33402.07 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5929.39 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3349.94 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 27744.62 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5754.07 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 4790.09 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9074.48 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9038.06 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 54961.48 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 54649.57 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8473.85 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8436.5 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9707.2 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9658.33 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 73813.15 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 73475.91 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9319.24 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9271.22 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35358.35 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88395.89 | -
CAV_1_HEATC | Coil:Heating:Water | 71920.14 | -
CAV_2_HEATC | Coil:Heating:Water | 199989.58 | -
VAV_1_HEATC | Coil:Heating:Water | 153321.54 | -
VAV_2_HEATC | Coil:Heating:Water | 276500.87 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.14 | 28847.25 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.7 | 29802.16 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.33 | 49057.69 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.91 | 77713.87 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18997.47 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18016.28 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 27909.06 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 664336.6092 | 1102.1502 | 2704.3623 | 0 | 0.0107 | 2811720 | 278886.9592
February | 590675.76 | 984.4584 | 2428.934 | 0 | 0.0096 | 2525390 | 248407.0107
March | 662471.7833 | 1111.1998 | 2762.4974 | 0 | 0.0109 | 2872250 | 279295.2502
April | 616055.552 | 1038.1816 | 2595.1295 | 0 | 0.0102 | 2698260 | 260200.9494
May | 626497.4413 | 1059.399 | 2658.7126 | 0 | 0.0104 | 2764400 | 264966.3954
June | 606171.7531 | 1029.9657 | 2599.1772 | 0 | 0.0102 | 2702530 | 256854.2713
July | 630990.4353 | 1077.0934 | 2732.4286 | 0 | 0.0107 | 2841110 | 267857.0142
August | 637587.022 | 1087.1359 | 2754.4032 | 0 | 0.0108 | 2863960 | 270537.8324
September | 606535.1227 | 1029.472 | 2594.7218 | 0 | 0.0102 | 2697890 | 256899.2618
October | 633589.2344 | 1069.0315 | 2676.0371 | 0 | 0.0105 | 2782400 | 267734.2934
November | 625270.2705 | 1046.5195 | 2595.0257 | 0 | 0.0102 | 2698110 | 263387.583
December | 660582.4089 | 1095.6995 | 2687.876 | 0 | 0.0106 | 2794580 | 277289.1385
Annual Sum or Average | 7560760 | 12730.3065 | 31789.3052 | 0 | 0.1251 | 33052600 | 3192320
Minimum of Months | 590675.76 | 984.4584 | 2428.934 | 0 | 0.0096 | 2525390 | 248407.0107
Maximum of Months | 664336.6092 | 1111.1998 | 2762.4974 | 0 | 0.0109 | 2872250 | 279295.2502
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2229160000000 | 1293154.847 | 24-JAN-16:15 | 445952.007 | 310109.712 | 88301.36 | 0 | 76745.579 | 0 | 34025.309 | 25954.136 | 162962.637 | 0 | 0 | 0 | 5604.73 | 0 | 0
February | 2002160000000 | 1278735.174 | 07-FEB-14:00 | 445952.007 | 302612.437 | 87864.54 | 0 | 71020.104 | 0 | 33864.43 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6418.129 | 0 | 0
March | 2277150000000 | 1370230.608 | 30-MAR-15:15 | 445952.007 | 310109.712 | 95785.518 | 0 | 111500.079 | 0 | 36215.017 | 25954.136 | 162962.637 | 0 | 0 | 0 | 5963.78 | 0 | 0
April | 2139220000000 | 1321466.411 | 27-APR-12:00 | 445952.007 | 302612.437 | 94728.254 | 0 | 99855.9 | 0 | 35582.645 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6732.613 | 0 | 0
May | 2191650000000 | 1353449.041 | 19-MAY-16:00 | 445952.007 | 310109.712 | 101109.908 | 0 | 120424.832 | 0 | 36585.414 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6106.718 | 0 | 0
June | 2142600000000 | 1414340.144 | 15-JUN-16:00 | 445952.007 | 310109.712 | 109713.055 | 0 | 142583.068 | 0 | 37696.164 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6331.585 | 0 | 0
July | 2252470000000 | 1369194.295 | 12-JUL-16:00 | 445952.007 | 310109.712 | 113237.679 | 0 | 174773.471 | 0 | 38638.685 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6629.143 | 0 | 0
August | 2270580000000 | 1372944.152 | 29-AUG-15:00 | 445952.007 | 310109.712 | 112269.841 | 0 | 183175.354 | 0 | 38842.344 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6687.633 | 0 | 0
September | 2138920000000 | 1399787.024 | 13-SEP-15:00 | 445952.007 | 310109.712 | 103511.346 | 0 | 141901.563 | 0 | 37449.935 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6321.453 | 0 | 0
October | 2205920000000 | 1365238.88 | 05-OCT-15:00 | 445952.007 | 310109.712 | 103268.976 | 0 | 145365.284 | 0 | 37432.823 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6335.015 | 0 | 0
November | 2139090000000 | 1325734.794 | 10-NOV-13:00 | 445952.007 | 302612.437 | 91107.985 | 0 | 105582.435 | 0 | 35787.144 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6749.587 | 0 | 0
December | 2215570000000 | 1275840.889 | 29-DEC-14:00 | 445952.007 | 302612.437 | 88518.622 | 0 | 64576.364 | 0 | 33549.898 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6337.792 | 0 | 0
Annual Sum or Average | 26204500000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2002160000000 | 1275840.889 |  | 445952.007 | 302612.437 | 87864.54 | 0 | 64576.364 | 0 | 33549.898 | 25954.136 | 162962.637 | 0 | 0 | 0 | 5604.73 | 0 | 0
Maximum of Months | 2277150000000 | 1414340.144 |  | 445952.007 | 310109.712 | 113237.679 | 0 | 183175.354 | 0 | 38842.344 | 25954.136 | 162962.637 | 0 | 0 | 0 | 6749.587 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 268990.69 | 86995.58 | 0 | 355986.28
Cost per Total Building Area ($/m2) | 12 | 3.88 | 0 | 15.88
Cost per Net Conditioned Building Area ($/m2) | 12 | 3.88 | 0 | 15.88

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 42834.54 | 1910.36 | 1910.36
Net Site Energy | 42834.54 | 1910.36 | 1910.36
Total Source Energy | 108846.36 | 4854.39 | 4854.39
Net Source Energy | 108846.36 | 4854.39 | 4854.39
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14168.34 | 0 | 0 | 0 | 0
Cooling | 2519.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.08 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2413.8 | 0 | 0 | 0 | 0 | 0
Pumps | 1273.83 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 658.74 | 0 | 0 | 0 | 0 | 12442
Humidification | 1898.41 | 0 | 0 | 0 | 0 | 706.21
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 838.26 | 0 | 0 | 0 | 4037.61
Refrigeration | 180.55 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26469.53 | 16365.02 | 0 | 0 | 0 | 17185.81
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 2.956 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 2.956 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 2.956 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 2.956 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 2.956 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 2.956 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2791653.59 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3813353.71 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2662808.04
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 540467.35 | 342165.79 | 198301.56 | 0.63 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 322598.85 | 238695.33 | 83903.51 | 0.74 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 833847.13 | 538131.83 | 295715.29 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1347325.15 | 863899.1 | 483426.05 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 62541.31 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11424.43 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16240.97 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 13557.2 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41561.88 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51276.92 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15909.35 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15909.35 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 184943.23 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29823.06 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34107.19 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13463.81 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 61180.03 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 127499.24 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 75507.97 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 75507.97 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46391.24 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29439.84 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29999.22 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37159.98 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53845.54 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 264252.96 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52851.32 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198666.6 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36158.51 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6673.63 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4252.88 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 28959.74 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6499.13 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5729.29 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11288.73 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11270.08 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64695.18 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64495.74 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10240.9 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10224.33 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11319.07 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11286.51 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 79403.71 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 79170.87 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10888.36 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10858.98 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41762.48 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 104406.21 | -
CAV_1_HEATC | Coil:Heating:Water | 117513.53 | -
CAV_2_HEATC | Coil:Heating:Water | 215414.32 | -
VAV_1_HEATC | Coil:Heating:Water | 205527.55 | -
VAV_2_HEATC | Coil:Heating:Water | 363928.72 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.7 | 28117.67 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.62 | 26469.44 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 27.47 | 45943.64 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 43.46 | 72000.71 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 25581.64 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20997.95 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 37581.82 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 600723.8143 | 981.658 | 1423.686 | 0 | 0.0106 | 935430.8983 | 249623.4377
February | 527678.1534 | 877.2995 | 1299.4377 | 0 | 0.0097 | 853863.5585 | 220704.7078
March | 561174.9385 | 952.6923 | 1446.0789 | 0 | 0.0107 | 950310.1161 | 236598.2153
April | 521355.3716 | 894.4474 | 1373.9327 | 0 | 0.0101 | 902938.2998 | 220704.0861
May | 548033.7743 | 949.2396 | 1473.6162 | 0 | 0.0109 | 968487.3171 | 232860.1885
June | 556973.416 | 972.7418 | 1523.7621 | 0 | 0.0112 | 1001480 | 237425.0684
July | 580986.2992 | 1017.4962 | 1598.627 | 0 | 0.0117 | 1050690 | 247930.4238
August | 594900.7976 | 1042.2941 | 1638.3108 | 0 | 0.012 | 1076780 | 253909.3173
September | 525197.5594 | 909.6165 | 1411.9873 | 0 | 0.0104 | 927983.3867 | 223150.4702
October | 532337.1744 | 912.6214 | 1400.7024 | 0 | 0.0103 | 920528.341 | 225289.2613
November | 526428.7213 | 892.1035 | 1351.3289 | 0 | 0.01 | 888037.011 | 221795.7457
December | 578947.328 | 959.6652 | 1416.3368 | 0 | 0.0105 | 930665.3953 | 241873.7661
Annual Sum or Average | 6654740 | 11361.8755 | 17357.8067 | 0 | 0.1283 | 11407200 | 2811860
Minimum of Months | 521355.3716 | 877.2995 | 1299.4377 | 0 | 0.0097 | 853863.5585 | 220704.0861
Maximum of Months | 600723.8143 | 1042.2941 | 1638.3108 | 0 | 0.012 | 1076780 | 253909.3173
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2170600000000 | 1220109.475 | 03-JAN-17:00 | 445952.007 | 310109.712 | 76916.081 | 0 | 1101.123 | 6881 | 38255.373 | 0 | 162962.637 | 0 | 0 | 0 | 4923.943 | 0 | 0
February | 1981330000000 | 1221704.237 | 08-FEB-17:00 | 445952.007 | 310109.712 | 79005.381 | 0 | 597.192 | 6881 | 38172.084 | 0 | 162962.637 | 0 | 0 | 0 | 4920.593 | 0 | 0
March | 2205120000000 | 1251569.413 | 31-MAR-15:00 | 445952.007 | 310109.712 | 82573.311 | 0 | 50512.084 | 0 | 42009.249 | 34949.356 | 162962.637 | 0 | 0 | 0 | 5396.5 | 0 | 0
April | 2095200000000 | 1258128.945 | 06-APR-16:00 | 445952.007 | 310109.712 | 84393.437 | 0 | 104504.008 | 0 | 44543.849 | 34949.356 | 162962.637 | 0 | 0 | 0 | 5770.987 | 0 | 0
May | 2247300000000 | 1332602.175 | 31-MAY-16:00 | 445952.007 | 310109.712 | 86395.515 | 0 | 235124.808 | 0 | 50940.898 | 34949.356 | 162962.637 | 0 | 0 | 0 | 6167.243 | 0 | 0
June | 2323850000000 | 1462540.546 | 29-JUN-16:00 | 445952.007 | 310109.712 | 99195.893 | 0 | 348980.83 | 0 | 53715.919 | 34949.356 | 162962.637 | 0 | 0 | 0 | 6674.192 | 0 | 0
July | 2438050000000 | 1517723.802 | 13-JUL-16:00 | 445952.007 | 310109.712 | 98308.377 | 0 | 403638.25 | 0 | 55182.776 | 34949.356 | 162962.637 | 0 | 0 | 0 | 6620.688 | 0 | 0
August | 2498580000000 | 1505078.489 | 25-AUG-16:00 | 445952.007 | 310109.712 | 99531.334 | 0 | 389950.004 | 0 | 55013.834 | 34949.356 | 162962.637 | 0 | 0 | 0 | 6609.606 | 0 | 0
September | 2153320000000 | 1377289.525 | 22-SEP-13:15 | 445952.007 | 302612.437 | 85115.546 | 0 | 285875.886 | 0 | 52855.423 | 34949.356 | 162962.637 | 0 | 0 | 0 | 6966.233 | 0 | 0
October | 2136020000000 | 1238121.631 | 25-OCT-15:15 | 445952.007 | 310109.712 | 83211.212 | 0 | 98434.107 | 0 | 44324.703 | 34949.356 | 162962.637 | 0 | 0 | 0 | 5660.308 | 0 | 0
November | 2060620000000 | 1256939.105 | 01-NOV-15:15 | 445952.007 | 310109.712 | 81683.653 | 0 | 88073.011 | 0 | 43739.889 | 34949.356 | 162962.637 | 0 | 0 | 0 | 5548.518 | 0 | 0
December | 2159540000000 | 1222324.556 | 20-DEC-16:30 | 445952.007 | 310109.712 | 78775.977 | 0 | 146.079 | 6881 | 38116.296 | 0 | 162962.637 | 0 | 0 | 0 | 4907.869 | 0 | 0
Annual Sum or Average | 26469500000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1981330000000 | 1220109.475 |  | 445952.007 | 302612.437 | 76916.081 | 0 | 146.079 | 0 | 38116.296 | 0 | 162962.637 | 0 | 0 | 0 | 4907.869 | 0 | 0
Maximum of Months | 2498580000000 | 1517723.802 |  | 445952.007 | 310109.712 | 99531.334 | 0 | 403638.25 | 6881 | 55182.776 | 34949.356 | 162962.637 | 0 | 0 | 0 | 6966.233 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 378421.43 | 130497.2 | 0 | 508918.63
Cost per Total Building Area ($/m2) | 16.88 | 5.82 | 0 | 22.7
Cost per Net Conditioned Building Area ($/m2) | 16.88 | 5.82 | 0 | 22.7

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 39361.56 | 1755.47 | 1755.47
Net Site Energy | 39361.56 | 1755.47 | 1755.47
Total Source Energy | 103926.9 | 4634.99 | 4634.99
Net Source Energy | 103926.9 | 4634.99 | 4634.99
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11591.36 | 0 | 0 | 0 | 0
Cooling | 1495.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2512.65 | 0 | 0 | 0 | 0 | 0
Pumps | 920.58 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 473.82 | 0 | 0 | 0 | 0 | 10601.36
Humidification | 2458.79 | 0 | 0 | 0 | 0 | 914.67
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 848 | 0 | 0 | 0 | 4037.61
Refrigeration | 178.04 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25563.79 | 13797.78 | 0 | 0 | 0 | 15553.64
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.385 | 0.305 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 2.956 | 0.385 | 0.305 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 2.956 | 0.385 | 0.305 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 2.956 | 0.385 | 0.305 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 2.956 | 0.385 | 0.305 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.385 | 0.305 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 2.956 | 0.385 | 0.305 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 2.956 | 0.385 | 0.305 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 2.956 | 0.385 | 0.305 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.385 | 0.305 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.385 | 0.305 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.385 | 0.305 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.385 | 0.305 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 186.18 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 659.24 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1968893.31 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3536305.31 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1878021.31
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 430171.73 | 271279.63 | 158892.1 | 0.63 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 259241.78 | 198898.37 | 60343.41 | 0.77 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 684671.09 | 437918.26 | 246752.83 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1137964.02 | 721852.66 | 416111.36 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 50338.31 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10361.11 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14519.34 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 11268.19 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 39907.3 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49920.84 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14222.87 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14222.87 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 179390.63 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29835.38 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31439.36 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12018.48 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57594.93 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 115286.35 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 67503.7 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67503.7 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41791.62 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29405.2 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29965.88 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 36426.93 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49773.44 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 256320.32 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50354.8 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198633.1 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34960.17 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6034.81 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3845.8 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 27478.09 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5784.99 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5187.08 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10244.3 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10223.65 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58252.05 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58093 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8889.9 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8889.9 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10031.99 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9998.68 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 73543.21 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 73304.17 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9436.47 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9404.06 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 37335.43 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 93338.58 | -
CAV_1_HEATC | Coil:Heating:Water | 108982.66 | -
CAV_2_HEATC | Coil:Heating:Water | 203086.31 | -
VAV_1_HEATC | Coil:Heating:Water | 188393.23 | -
VAV_2_HEATC | Coil:Heating:Water | 338380.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.88 | 28416.77 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.89 | 28426.87 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 27.93 | 46714.42 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 45.39 | 75188.42 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18042.18 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19472.4 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 26505.65 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 609604.1496 | 999.2058 | 1615.244 | 0 | 0.0114 | 38307300 | 254083.8842
February | 537198.5525 | 886.6036 | 1445.3757 | 0 | 0.0102 | 34279700 | 224492.6728
March | 594899.0717 | 999.986 | 1666.2711 | 0 | 0.0117 | 39521600 | 250360.1025
April | 550613.9393 | 929.3338 | 1555.9316 | 0 | 0.0109 | 36905100 | 232089.1248
May | 555920.2387 | 942.6409 | 1586.6617 | 0 | 0.0111 | 37634700 | 234746.3676
June | 542964.0959 | 926.4657 | 1570.6364 | 0 | 0.011 | 37255500 | 229835.4687
July | 550081.9995 | 942.2035 | 1604.2187 | 0 | 0.0112 | 38052600 | 233195.7258
August | 558304.619 | 955.486 | 1625.2994 | 0 | 0.0113 | 38552500 | 236604.0442
September | 531410.5605 | 904.2517 | 1528.174 | 0 | 0.0107 | 36247900 | 224703.222
October | 565913.8677 | 956.3606 | 1603.5183 | 0 | 0.0112 | 38034000 | 238654.5133
November | 559236.248 | 937.6814 | 1557.8553 | 0 | 0.0109 | 36949800 | 235123.6859
December | 598327.2184 | 986.1993 | 1605.1735 | 0 | 0.0113 | 38069400 | 249913.1228
Annual Sum or Average | 6754470 | 11366.4185 | 18964.3597 | 0 | 0.1329 | 449810000 | 2843800
Minimum of Months | 531410.5605 | 886.6036 | 1445.3757 | 0 | 0.0102 | 34279700 | 224492.6728
Maximum of Months | 609604.1496 | 999.986 | 1666.2711 | 0 | 0.0117 | 39521600 | 254083.8842
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2177100000000 | 1214273.161 | 10-JAN-17:45 | 445952.007 | 310109.712 | 82628.178 | 0 | 15965.46 | 6881 | 28489.996 | 656 | 162962.637 | 0 | 0 | 0 | 5023.683 | 0 | 0
February | 1948200000000 | 1255629.067 | 03-FEB-17:30 | 445952.007 | 310109.712 | 88341.236 | 0 | 54284.874 | 6881 | 31087.058 | 24649.03 | 162962.637 | 0 | 0 | 0 | 5464.438 | 0 | 0
March | 2246110000000 | 1295406.455 | 29-MAR-16:00 | 445952.007 | 310109.712 | 91721.543 | 0 | 99883.357 | 0 | 34279.94 | 24649.03 | 162962.637 | 0 | 0 | 0 | 5884.106 | 0 | 0
April | 2097410000000 | 1298648.106 | 06-APR-16:00 | 445952.007 | 310109.712 | 91921.173 | 0 | 104502.278 | 0 | 34462.9 | 24649.03 | 162962.637 | 0 | 0 | 0 | 5907.801 | 0 | 0
May | 2138870000000 | 1308444.863 | 04-MAY-16:00 | 445952.007 | 310109.712 | 97149.143 | 0 | 123587.507 | 0 | 35374.015 | 24649.03 | 162962.637 | 0 | 0 | 0 | 6125.536 | 0 | 0
June | 2117320000000 | 1353666.31 | 30-JUN-15:00 | 445952.007 | 310109.712 | 102824.905 | 0 | 201450.376 | 0 | 37593.772 | 24649.03 | 162962.637 | 0 | 0 | 0 | 6774.223 | 0 | 0
July | 2162620000000 | 1357521.301 | 21-JUL-16:00 | 445952.007 | 310109.712 | 111730.638 | 0 | 198414.314 | 0 | 38203.285 | 24649.03 | 162962.637 | 0 | 0 | 0 | 6754.47 | 0 | 0
August | 2191030000000 | 1345718.756 | 18-AUG-16:00 | 445952.007 | 310109.712 | 107350.865 | 0 | 172910.659 | 0 | 37164.275 | 24649.03 | 162962.637 | 0 | 0 | 0 | 6563.322 | 0 | 0
September | 2060050000000 | 1288265.718 | 01-SEP-16:00 | 445952.007 | 310109.712 | 103103.232 | 0 | 171983.906 | 0 | 36951.439 | 24649.03 | 162962.637 | 0 | 0 | 0 | 6558.209 | 0 | 0
October | 2161560000000 | 1295931.836 | 19-OCT-16:00 | 445952.007 | 310109.712 | 90201.47 | 0 | 100783.102 | 0 | 34189.096 | 24649.03 | 162962.637 | 0 | 0 | 0 | 5864.702 | 0 | 0
November | 2099940000000 | 1238603.97 | 21-NOV-11:45 | 445952.007 | 310109.712 | 81679.31 | 0 | 65152.977 | 0 | 31963.461 | 24649.03 | 162962.637 | 0 | 0 | 0 | 9540.942 | 0 | 0
December | 2163570000000 | 1220645.914 | 12-DEC-16:45 | 445952.007 | 310109.712 | 80915.174 | 0 | 543.232 | 6881 | 27093.341 | 0 | 162962.637 | 0 | 0 | 0 | 4908.928 | 0 | 0
Annual Sum or Average | 25563800000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1948200000000 | 1214273.161 |  | 445952.007 | 310109.712 | 80915.174 | 0 | 543.232 | 0 | 27093.341 | 0 | 162962.637 | 0 | 0 | 0 | 4908.928 | 0 | 0
Maximum of Months | 2246110000000 | 1357521.301 |  | 445952.007 | 310109.712 | 111730.638 | 0 | 201450.376 | 6881 | 38203.285 | 24649.03 | 162962.637 | 0 | 0 | 0 | 9540.942 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 489897.59 | 119813 | 0 | 609710.59
Cost per Total Building Area ($/m2) | 21.85 | 5.34 | 0 | 27.19
Cost per Net Conditioned Building Area ($/m2) | 21.85 | 5.34 | 0 | 27.19

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 43303.15 | 1931.26 | 1931.26
Net Site Energy | 43303.15 | 1931.26 | 1931.26
Total Source Energy | 107527.42 | 4795.57 | 4795.57
Net Source Energy | 107527.42 | 4795.57 | 4795.57
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15329.1 | 0 | 0 | 0 | 0
Cooling | 1578.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2446.86 | 0 | 0 | 0 | 0 | 0
Pumps | 1066.75 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 507.77 | 0 | 0 | 0 | 0 | 8007.48
Humidification | 2389.33 | 0 | 0 | 0 | 0 | 888.83
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 926.78 | 0 | 0 | 0 | 4037.61
Refrigeration | 175.64 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25688.86 | 17614.29 | 0 | 0 | 0 | 12933.92
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.487 | 0.409 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 2.956 | 0.487 | 0.409 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 2.956 | 0.487 | 0.409 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 2.956 | 0.487 | 0.409 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 2.956 | 0.487 | 0.409 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 2.956 | 0.487 | 0.409 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 2.956 | 0.487 | 0.409 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.487 | 0.409 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.487 | 0.409 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.487 | 0.409 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 2.956 | 0.487 | 0.409 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 2.956 | 0.487 | 0.409 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.487 | 0.409 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.487 | 0.409 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 2.956 | 0.487 | 0.409 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.487 | 0.409 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.487 | 0.409 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.487 | 0.409 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.487 | 0.409 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.487 | 0.409 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.487 | 0.409 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.487 | 0.409 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.487 | 0.409 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.487 | 0.409 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.487 | 0.409 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.487 | 0.409 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.487 | 0.409 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.487 | 0.409 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.487 | 0.409 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.487 | 0.409 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.487 | 0.409 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.487 | 0.409 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 186.18 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 659.24 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2466764.36 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 3817562.04 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2352913.69
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 516632.32 | 330635.38 | 185996.94 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 284952.53 | 219796.51 | 65156.01 | 0.77 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 754519.1 | 490957.51 | 263561.59 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1259466.23 | 815360.59 | 444105.63 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 45547.89 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10524.4 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15902.22 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12538.53 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 40528.14 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 51527.92 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15577.52 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15577.52 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 184212.05 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29825.48 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32189.48 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13303.77 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 63895.33 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 122592.32 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 73933.06 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 73933.06 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45639.42 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29398.14 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29958.84 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34699.86 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51388.33 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 259336.13 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51372.61 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198659.9 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36503.01 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6658.47 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4473.54 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 29593.05 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6344.41 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5401.35 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59668.13 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59556.04 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11675.59 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11647.13 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 67008.22 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 66856.39 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11454.45 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11418.35 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 83656.41 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 83423.18 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10713.06 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10682.38 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 40891.43 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 102228.56 | -
CAV_1_HEATC | Coil:Heating:Water | 125086.73 | -
CAV_2_HEATC | Coil:Heating:Water | 214984.2 | -
VAV_1_HEATC | Coil:Heating:Water | 207608.17 | -
VAV_2_HEATC | Coil:Heating:Water | 374526.99 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.11 | 28800.64 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.72 | 26638.21 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 26.29 | 44258.09 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 43.22 | 71597.96 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22604.48 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21021.12 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 33208.09 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 605321.127 | 988.8294 | 1433.4704 | 0 | 0.0107 | 941858.1458 | 251501.1809
February | 538167.2104 | 885.3027 | 1294.5439 | 0 | 0.0097 | 850605.5963 | 224189.9094
March | 577041.4393 | 971.163 | 1459.4 | 0 | 0.0108 | 959028.0175 | 242478.5402
April | 521216.6099 | 890.1418 | 1360.3223 | 0 | 0.0101 | 893976.6589 | 220256.539
May | 532046.4507 | 915.3413 | 1410.417 | 0 | 0.0104 | 926926.196 | 225473.8598
June | 518359.5523 | 899.3848 | 1398.8504 | 0 | 0.0103 | 919356.1843 | 220399.1074
July | 549630.0909 | 958.6306 | 1499.4841 | 0 | 0.011 | 985515.3757 | 234171.83
August | 548535.9672 | 954.4795 | 1489.196 | 0 | 0.011 | 978744.5946 | 233491.2863
September | 502286.6774 | 864.8683 | 1333.8905 | 0 | 0.0098 | 876636.0021 | 212931.4958
October | 529895.3021 | 906.4866 | 1387.9325 | 0 | 0.0103 | 912127.9277 | 224069.5877
November | 538887.5914 | 906.9673 | 1362.9613 | 0 | 0.0101 | 895654.4789 | 226447.5719
December | 587314.5932 | 967.1045 | 1415.8685 | 0 | 0.0106 | 930328.6613 | 244754.8101
Annual Sum or Average | 6548700 | 11108.6998 | 16846.3369 | 0 | 0.1247 | 11070800 | 2760170
Minimum of Months | 502286.6774 | 864.8683 | 1294.5439 | 0 | 0.0097 | 850605.5963 | 212931.4958
Maximum of Months | 605321.127 | 988.8294 | 1499.4841 | 0 | 0.011 | 985515.3757 | 251501.1809
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2185510000000 | 1223153.927 | 12-JAN-17:00 | 445952.007 | 310109.712 | 81080.062 | 0 | 2534.252 | 6881 | 33996.857 | 0 | 162962.637 | 0 | 0 | 0 | 4918.871 | 0 | 0
February | 1973770000000 | 1224260.354 | 15-FEB-17:00 | 445952.007 | 310109.712 | 81192.127 | 0 | 2121.742 | 6881 | 33943.307 | 0 | 162962.637 | 0 | 0 | 0 | 4930.05 | 0 | 0
March | 2225350000000 | 1227329.372 | 03-MAR-17:00 | 445952.007 | 310109.712 | 82303.456 | 0 | 3964.583 | 6881 | 34082.314 | 0 | 162962.637 | 0 | 0 | 0 | 4938.117 | 0 | 0
April | 2074410000000 | 1248831.777 | 27-APR-15:15 | 445952.007 | 310109.712 | 86639.64 | 0 | 55061.821 | 0 | 37928.23 | 30881.992 | 162962.637 | 0 | 0 | 0 | 5415.775 | 0 | 0
May | 2150860000000 | 1300994.478 | 12-MAY-16:00 | 445952.007 | 310109.712 | 91716.076 | 0 | 90950.945 | 0 | 39894.401 | 30881.992 | 162962.637 | 0 | 0 | 0 | 5715.317 | 0 | 0
June | 2133300000000 | 1372816.652 | 14-JUN-15:15 | 445952.007 | 310109.712 | 93389.113 | 0 | 275512.869 | 0 | 47610.052 | 30881.992 | 162962.637 | 0 | 0 | 0 | 6398.268 | 0 | 0
July | 2286810000000 | 1418023.65 | 12-JUL-08:30 | 445952.007 | 302612.437 | 88252.859 | 0 | 330222.214 | 0 | 50205.938 | 30881.992 | 162962.637 | 0 | 0 | 0 | 6933.567 | 0 | 0
August | 2271100000000 | 1391771.549 | 11-AUG-16:15 | 445952.007 | 310109.712 | 98528.702 | 0 | 288713.002 | 0 | 48130.813 | 30881.992 | 162962.637 | 0 | 0 | 0 | 6492.684 | 0 | 0
September | 2034170000000 | 1373101.336 | 08-SEP-16:00 | 445952.007 | 310109.712 | 91048.801 | 0 | 277023.856 | 0 | 48983.028 | 30881.992 | 162962.637 | 0 | 0 | 0 | 6139.302 | 0 | 0
October | 2116520000000 | 1238789.224 | 25-OCT-15:15 | 445952.007 | 310109.712 | 85590.086 | 0 | 72807.303 | 0 | 38707.752 | 30881.992 | 162962.637 | 0 | 0 | 0 | 5488.455 | 0 | 0
November | 2078300000000 | 1246153.66 | 03-NOV-16:00 | 445952.007 | 310109.712 | 85931.394 | 0 | 39905.315 | 6881 | 36853.736 | 30881.992 | 162962.637 | 0 | 0 | 0 | 5361.933 | 0 | 0
December | 2158760000000 | 1214849.06 | 21-DEC-16:30 | 445952.007 | 310109.712 | 81358.176 | 0 | 2079.585 | 6881 | 33943.321 | 0 | 162962.637 | 0 | 0 | 0 | 4919.939 | 0 | 0
Annual Sum or Average | 25688900000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1973770000000 | 1214849.06 |  | 445952.007 | 302612.437 | 81080.062 | 0 | 2079.585 | 0 | 33943.307 | 0 | 162962.637 | 0 | 0 | 0 | 4918.871 | 0 | 0
Maximum of Months | 2286810000000 | 1418023.65 |  | 445952.007 | 310109.712 | 98528.702 | 0 | 330222.214 | 6881 | 50205.938 | 30881.992 | 162962.637 | 0 | 0 | 0 | 6933.567 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 367728.58 | 140385.7 | 0 | 508114.28
Cost per Total Building Area ($/m2) | 16.4 | 6.26 | 0 | 22.66
Cost per Net Conditioned Building Area ($/m2) | 16.4 | 6.26 | 0 | 22.66

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 50332.43 | 2244.75 | 2244.75
Net Site Energy | 50332.43 | 2244.75 | 2244.75
Total Source Energy | 118278.1 | 5275.04 | 5275.04
Net Source Energy | 118278.1 | 5275.04 | 5275.04
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 22409.78 | 0 | 0 | 0 | 0
Cooling | 1039.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2523.61 | 0 | 0 | 0 | 0 | 0
Pumps | 709.02 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 335.69 | 0 | 0 | 0 | 0 | 5754.3
Humidification | 3226.2 | 0 | 0 | 0 | 0 | 1200.15
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1033.94 | 0 | 0 | 0 | 4037.61
Refrigeration | 172.37 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25530.28 | 24802.14 | 0 | 0 | 0 | 10992.05
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.616 | 0.541 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 2.956 | 0.616 | 0.541 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 2.956 | 0.616 | 0.541 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 2.956 | 0.616 | 0.541 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 2.956 | 0.616 | 0.541 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 2.956 | 0.616 | 0.541 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 2.956 | 0.616 | 0.541 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 2.956 | 0.616 | 0.541 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.616 | 0.541 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.616 | 0.541 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 2.956 | 0.616 | 0.541 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 2.956 | 0.616 | 0.541 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 2.956 | 0.616 | 0.541 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 2.956 | 0.616 | 0.541 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 2.956 | 0.616 | 0.541 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.616 | 0.541 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.616 | 0.541 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.616 | 0.541 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.616 | 0.541 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.616 | 0.541 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.616 | 0.541 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.616 | 0.541 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 2.956 | 0.616 | 0.541 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.616 | 0.541 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 2.956 | 0.616 | 0.541 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.616 | 0.541 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.616 | 0.541 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.616 | 0.541 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 2.956 | 0.616 | 0.541 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.616 | 0.541 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 2.956 | 0.616 | 0.541 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 2.956 | 0.616 | 0.541 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 186.18 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 659.24 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1973599.99 | 5.2
HEATSYS1 BOILER | Boiler:HotWater | 4313555.17 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1882510.76
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 482399.58 | 328755.52 | 153644.06 | 0.68 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 238077.39 | 196402.21 | 41675.18 | 0.82 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 650311.45 | 445652.25 | 204659.2 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1124224.29 | 765448.5 | 358775.8 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 27596.3 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10216.81 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16468.09 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 12216.21 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 46746.41 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53340.08 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16131.83 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16131.83 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 185800.97 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29821.56 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31451.53 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13575.69 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 67784.29 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 122414.84 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76563.89 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76563.89 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46563.21 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29369.34 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29931.4 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34748.74 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50469.54 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 257568.73 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50811.81 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198672.77 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42146.12 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7959.49 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6714.35 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30396.02 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6377.4 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6581.89 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 90184.94 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 90033.64 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16822 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16787.34 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 78677.34 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 78521.35 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10463.24 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10438.29 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60487.5 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60487.5 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14553.18 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14523.48 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 89882.68 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 89722.09 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10969.4 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10945.66 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42346.5 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 105866.25 | -
CAV_1_HEATC | Coil:Heating:Water | 177815.91 | -
CAV_2_HEATC | Coil:Heating:Water | 234665.92 | -
VAV_1_HEATC | Coil:Heating:Water | 255729.6 | -
VAV_2_HEATC | Coil:Heating:Water | 462232.77 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.22 | 30665.76 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.34 | 25982.81 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 24.95 | 42000.88 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 42.34 | 70148.68 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18085.31 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23752.27 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 26569.01 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.66
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 624634.3336 | 713.2275 | 3060.6428 | 0 | 0.0108 | 614085.5984 | 238685.9118
February | 555470.523 | 638.0457 | 2801.0724 | 0 | 0.0098 | 562022.2716 | 212840.4458
March | 567470.1112 | 666.2753 | 3163.8126 | 0 | 0.011 | 634866.3504 | 219661.4158
April | 502869.6408 | 601.4187 | 3033.6077 | 0 | 0.0104 | 608781.4052 | 196346.7843
May | 496642.5816 | 600.3611 | 3129.7238 | 0 | 0.0107 | 628092.7867 | 194898.7145
June | 466811.7066 | 566.2643 | 2982.8243 | 0 | 0.0102 | 598618.8035 | 183494.3306
July | 469263.4307 | 569.0031 | 2993.5687 | 0 | 0.0102 | 600774.2724 | 184421.8528
August | 474607.1104 | 574.0589 | 2997.8736 | 0 | 0.0103 | 601633.4096 | 186302.8566
September | 458399.2131 | 551.0476 | 2824.2137 | 0 | 0.0097 | 566770.5022 | 179416.2683
October | 515049.0596 | 612.9944 | 3044.5154 | 0 | 0.0105 | 610959.6372 | 200642.0643
November | 558634.7825 | 650.2795 | 2996.9338 | 0 | 0.0104 | 601357.8341 | 215376.2024
December | 601168.1947 | 692.7432 | 3077.675 | 0 | 0.0108 | 617530.7724 | 230690.0428
Annual Sum or Average | 6291020 | 7435.7193 | 36106.4638 | 0 | 0.1247 | 7245490 | 2442780
Minimum of Months | 458399.2131 | 551.0476 | 2801.0724 | 0 | 0.0097 | 562022.2716 | 179416.2683
Maximum of Months | 624634.3336 | 713.2275 | 3163.8126 | 0 | 0.011 | 634866.3504 | 238685.9118
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2163800000000 | 1216191.456 | 25-JAN-16:15 | 445952.007 | 310109.712 | 82498.058 | 0 | 32.934 | 6881 | 27137.812 | 0 | 162962.637 | 0 | 0 | 0 | 4907.731 | 0 | 0
February | 1980350000000 | 1221459.039 | 28-FEB-17:00 | 445952.007 | 310109.712 | 83406.597 | 0 | 23566.769 | 6881 | 29321.332 | 481.353 | 162962.637 | 0 | 0 | 0 | 5021.179 | 0 | 0
March | 2237020000000 | 1218490.293 | 22-MAR-15:15 | 445952.007 | 310109.712 | 86230.026 | 0 | 2869.184 | 0 | 27332.178 | 0 | 162962.637 | 0 | 0 | 0 | 4906.611 | 0 | 0
April | 2145110000000 | 1237165.866 | 21-APR-16:00 | 445952.007 | 310109.712 | 92101.597 | 0 | 36003.689 | 0 | 30082.028 | 15987.888 | 162962.637 | 0 | 0 | 0 | 5297.962 | 0 | 0
May | 2213150000000 | 1311620.98 | 24-MAY-15:15 | 445952.007 | 310109.712 | 95584.455 | 0 | 110434.143 | 0 | 35315.293 | 24707.954 | 162962.637 | 0 | 0 | 0 | 5841.603 | 0 | 0
June | 2109300000000 | 1328813.244 | 15-JUN-16:00 | 445952.007 | 310109.712 | 102097.84 | 0 | 146000 | 0 | 36937.696 | 24707.954 | 162962.637 | 0 | 0 | 0 | 6174.816 | 0 | 0
July | 2116890000000 | 1289635.365 | 20-JUL-16:00 | 445952.007 | 310109.712 | 100281.081 | 0 | 161553.4 | 0 | 37090.005 | 24707.954 | 162962.637 | 0 | 0 | 0 | 6322.134 | 0 | 0
August | 2119920000000 | 1272915.003 | 18-AUG-16:45 | 445952.007 | 310109.712 | 97260.917 | 0 | 185741.783 | 0 | 40152.776 | 24707.954 | 162962.637 | 0 | 0 | 0 | 6027.216 | 0 | 0
September | 1997080000000 | 1224807.63 | 07-SEP-15:00 | 445952.007 | 310109.712 | 90465.006 | 0 | 87392.621 | 0 | 33705.467 | 24707.954 | 162962.637 | 0 | 0 | 0 | 5751.662 | 0 | 0
October | 2152780000000 | 1213716.324 | 27-OCT-16:45 | 445952.007 | 310109.712 | 85266.464 | 0 | 1940.423 | 6881 | 27308.373 | 0 | 162962.637 | 0 | 0 | 0 | 4961.87 | 0 | 0
November | 2118950000000 | 1211631.329 | 29-NOV-17:30 | 445952.007 | 310109.712 | 83447.776 | 0 | 211.888 | 6881 | 27155.292 | 0 | 162962.637 | 0 | 0 | 0 | 4947.854 | 0 | 0
December | 2175940000000 | 1216916.341 | 13-DEC-17:00 | 445952.007 | 310109.712 | 83312.314 | 0 | 536.289 | 6881 | 27200.516 | 0 | 162962.637 | 0 | 0 | 0 | 4928.923 | 0 | 0
Annual Sum or Average | 25530300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1980350000000 | 1211631.329 |  | 445952.007 | 310109.712 | 82498.058 | 0 | 32.934 | 0 | 27137.812 | 0 | 162962.637 | 0 | 0 | 0 | 4906.611 | 0 | 0
Maximum of Months | 2237020000000 | 1328813.244 |  | 445952.007 | 310109.712 | 102097.84 | 0 | 185741.783 | 6881 | 40152.776 | 24707.954 | 162962.637 | 0 | 0 | 0 | 6322.134 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 618184.11 | 103536.32 | 0 | 721720.43
Cost per Total Building Area ($/m2) | 27.57 | 4.62 | 0 | 32.19
Cost per Net Conditioned Building Area ($/m2) | 27.57 | 4.62 | 0 | 32.19

## Picture
DOE Commercial Building Benchmark - Hospital
Second Floor
Third Floor
Forth Floor
Fifth Floor

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ER_Exam1_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam1_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam1_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam1_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Trauma1_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Trauma1_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Trauma1_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Trauma1_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam3_Mult4_Flr_1 humidity sched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ER_Exam3_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam3_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam3_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam3_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Trauma2_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Trauma2_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Trauma2_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Trauma2_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Triage_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Triage_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Triage_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Triage_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR1_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR1_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR1_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR1_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR2_Mult5_Flr_2 humidity sched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OR2_Mult5_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR2_Mult5_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR2_Mult5_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR2_Mult5_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR3_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR3_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR3_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR3_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR4_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR4_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR4_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR4_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PhysTherapy_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PhysTherapy_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PhysTherapy_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PhysTherapy_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Radiology_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Radiology_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Radiology_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Radiology_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_5 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_5 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen_Flr_5 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
CAV_1_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
CAV_2_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 57.4 | 2993
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
CRITICAL_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
ADMIN_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5
|  |  | WinterDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 60.1 | 3133.79
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
CRITICAL_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6 | 130.2 | 6789
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
ADMIN_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
CRITICAL_OCC_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1 | 119.7 | 6241.5
|  |  | SummerDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | WinterDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
ADMIN_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
CRITICAL_HTGSETP_SCH | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CRITICAL_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 532.8 | 3729.6 | 194472
ADMIN_HTGSETP_SCH | Temperature | Through 12/31 | WD | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6
|  |  | WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sat | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sun, Hol, Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
ADMIN_CLGSETP_SCH | Temperature | Through 12/31 | WD | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6
|  |  | WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sat | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sun, Hol, Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6 | 2869 | 149597.86
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6
|  |  | WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | WD | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668 | 4748 | 247574.29
|  |  | SummerDesign | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Sats | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
BLDG_OA_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_SAT_SCH | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_CAV_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6 | 109.2 | 5694
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
BLDG_CAV_SCH_HUMID | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
BLDG_OA_FRAC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 938.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0