## BuildingSummary
Building Summary Secondary School post-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Secondary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 19592 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.28
| Total | 0.34
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6384
| Net Dimensions - Total Area (m2) | 4088.16
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11902
| Net Dimensions - Total Area (m2) | 11768.6976
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Pless, et al. 2007
| South | 753.18
| East | 291.61
| North | 753.18
| West | 291.2
| Total Area (m2) | 2089.17
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 11902
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 6792
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 39184
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.60327 | See Benchmark Technical Report
HVAC
| System Type | MZ VAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | Air cooled chiller, PACU (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Fan Control | Variable, constant (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 2677.93

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 0.17901
LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 0.29153
BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.56362
OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 0.39893
GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.2801 | 1 | 1976 | 11.3864 | 5 |  | 717.2337 | 10 |  | 19760 |  | 0
AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608.0006 | 266.3502 | 3 | 416 | 11.8138 | 5 |  |  | 10 |  | 4160 |  | 0.24855
AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512.0005 | 106.4001 | 1 | 988 | 12.0812 | 5 |  |  | 8 |  | 7904 |  | 0.26438
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6 | 36 | 16.7657 | 222.2745 | 1119.4456 | 503.4582 | 8 |  | 288 | 1887.788 | 0.17006
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200.0002 | 70.0001 | 1.39 | 448.9209 | 14.3812 | 19.2674 |  |  | 10 |  | 4489.2086 |  | 0.32703
MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 1.1994
LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 1.3119
BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 1.584
OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 1.4193
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236.0002 | 83.0101 | 4.35 | 193.1034 | 16.3387 | 10 |  |  | 8 |  | 1544.8276 |  | 1.307
MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 1.0203
Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 6080.0643
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 1764.2292 | 1591.1618 | 1361.4687 | 1406.8807 | 1153.4171 | 1055.2704 | 1092.1234 | 1364.553 | 739.7105 | 805.6862 | 1344.2205 | 687.7732 | 1229.4332 | 613.2141 | 1012.5413 | 674.7211
| PSZ-AC_1:5_COOLC DXCOIL | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 364.2728 | 490.6879 | 431.701 | 419.6885 | 490.6879 | 349.6098 | 490.6879 | 327.0982 | 490.6879 | 327.0982
| PSZ-AC_2:6_COOLC DXCOIL | 157.928 | 113.5838 | 125.5576 | 112.8655 | 128.5416 | 97.4319 | 89.8159 | 93.0655 | 84.839 | 84.9412 | 93.0655 | 85.7012 | 93.0655 | 75.7361 | 94.46 | 78.5674
| PSZ-AC_3:7_COOLC DXCOIL | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 147.9096 | 196.2751 | 153.905 | 157.7871 | 196.2751 | 148.4859 | 196.2751 | 130.8393 | 196.2751 | 130.8393
| PSZ-AC_4:8_COOLC DXCOIL | 18.8824 | 15.1608 | 15.1146 | 14.6812 | 14.842 | 12.7853 | 18.8357 | 13.721 | 12.3464 | 9.9032 | 13.6415 | 11.8424 | 13.3939 | 9.6314 | 11.5851 | 8.5169
| PSZ-AC_5:9_COOLC DXCOIL | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 87.2141 | 111.4777 | 102.8655 | 91.2245 | 111.4777 | 103.9805 | 111.4777 | 88.1485 | 111.4777 | 74.3123
Heating (kW)
| HEATSYS1 BOILER | 875.1457 | 896.3951 | 827.7758 | 926.861 | 842.6093 | 798.9404 | 1058.2425 | 897.9792 | 745.6903 | 841.5238 | 1012.3157 | 774.5765 | 1012.5247 | 947.1107 | 1035.2422 | 1542.4992
| PSZ-AC_1:5_HEATC | 765.0269 | 1009.9404 | 852.0818 | 1089.4655 | 795.6607 | 921.1228 | 879.4681 | 1212.7703 | 963.6127 | 1048.8159 | 1416.7661 | 1150.2765 | 1531.1076 | 1395.2101 | 1567.2052 | 1940.738
| PSZ-AC_2:6_HEATC | 205.1433 | 210.4756 | 190.5068 | 224.2938 | 188.9374 | 178.4384 | 193.3282 | 230.0181 | 182.762 | 198.9219 | 268.7086 | 218.1653 | 290.395 | 269.7088 | 298.4681 | 390.6802
| PSZ-AC_3:7_HEATC | 306.0108 | 403.9762 | 340.8327 | 435.7862 | 318.2643 | 368.4491 | 352.8552 | 485.1081 | 385.4451 | 419.5263 | 566.7064 | 460.1106 | 612.443 | 558.084 | 626.8821 | 776.2952
| PSZ-AC_4:8_HEATC | 29.4393 | 31.2042 | 26.2466 | 32.5965 | 24.0666 | 24.0007 | 43.1517 | 33.9124 | 26.2759 | 23.7246 | 39.3871 | 29.7628 | 41.7933 | 34.6335 | 37.0015 | 50.5324
| PSZ-AC_5:9_HEATC | 173.8039 | 229.445 | 193.5816 | 247.512 | 180.7635 | 209.2668 | 199.8034 | 275.5253 | 218.92 | 238.277 | 321.8704 | 261.3275 | 347.8472 | 316.9731 | 356.0481 | 440.9098
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| PSZ-AC_1:5_COOLC DXCOIL | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.73 | 2.95 | 2.73 | 2.81 | 2.83 | 2.73 | 2.99 | 2.73 | 3.07 | 2.73 | 3.07
| PSZ-AC_2:6_COOLC DXCOIL | 2.89 | 2.9 | 2.89 | 2.9 | 2.92 | 2.9 | 3.2 | 2.9 | 2.98 | 2.97 | 2.9 | 2.97 | 2.9 | 3.16 | 2.9 | 3.35
| PSZ-AC_3:7_COOLC DXCOIL | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89 | 3.16 | 2.89 | 3.11 | 3.08 | 2.89 | 3.15 | 2.89 | 3.32 | 2.89 | 3.32
| PSZ-AC_4:8_COOLC DXCOIL | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 2.95 | 3.06 | 2.95 | 2.98 | 3 | 2.95 | 2.98 | 2.95 | 3.07 | 2.95 | 3.19
| PSZ-AC_5:9_COOLC DXCOIL | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 3.13 | 2.9 | 2.97 | 3.08 | 2.9 | 2.96 | 2.9 | 3.12 | 2.9 | 3.35
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_4:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:5 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:6 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_3:7 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_4:8 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_5:9 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_OTHER | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_2 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_POD_3 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
| PSZ-AC_1:5_FAN | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76
| PSZ-AC_2:6_FAN | 6.36 | 4.57 | 5.06 | 4.55 | 5.41 | 3.92 | 4.9 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 4 | 3.8 | 4.75
| PSZ-AC_3:7_FAN | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.95 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
| PSZ-AC_4:8_FAN | 0.76 | 0.61 | 0.61 | 0.59 | 0.6 | 0.51 | 0.97 | 0.55 | 0.54 | 0.45 | 0.55 | 0.51 | 0.54 | 0.49 | 0.47 | 0.51
| PSZ-AC_5:9_FAN | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
| VAV_OTHER_FAN | 19.03 | 15.57 | 15.46 | 15.46 | 17.8 | 14.14 | 18.05 | 13.27 | 13.58 | 13.06 | 12.79 | 11.78 | 11.86 | 13.23 | 12.32 | 14.48
| VAV_POD_1_FAN | 12.68 | 10.2 | 11.23 | 9.87 | 11.81 | 10.24 | 14.8 | 8.77 | 9.08 | 9.64 | 8.67 | 8.05 | 8.01 | 7.9 | 7.91 | 9.76
| VAV_POD_2_FAN | 12.69 | 10.24 | 11.25 | 9.9 | 11.79 | 10.27 | 14.85 | 8.79 | 9.02 | 9.63 | 8.68 | 7.96 | 8.03 | 7.9 | 7.9 | 9.66
| VAV_POD_3_FAN | 13.38 | 10.89 | 11.94 | 10.57 | 12.42 | 10.96 | 14.91 | 9.44 | 9.77 | 10.25 | 9.34 | 8.71 | 8.67 | 8.46 | 8.57 | 10.35
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.09033 | 0.11897 | 0.088739 | 0.10392 | 0.066281 | 0.10343 | 0.15292 | 0.083396 | 0.037004 | 0.072302 | 0.08205 | 0.037009 | 0.065681 | 0.078704 | 0.063022 | 0.096467
| Total Cost ($/m2) | 18.18 | 20.1 | 15.22 | 14.68 | 8.46 | 15.84 | 17.69 | 11.16 | 4.79 | 8.24 | 10.48 | 4.5 | 8.16 | 9.25 | 7.32 | 11.17
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011426 | 0.0080753 | 0.008265 | 0.0096845 | 0.0085654 | 0.0077264 | 0.0085706 | 0.0096955 | 0.0069155 | 0.0084102 | 0.0083506 | 0.0069375 | 0.0078772 | 0.0081343 | 0.0078696 | 0.0041294
| Total Cost ($/m2) | 0.44 | 1.11 | 0.85 | 2.37 | 0.82 | 1.15 | 1.85 | 3.73 | 1.84 | 3.16 | 4.29 | 2.58 | 5.32 | 4.44 | 6.36 | 5.8
Total Utility Costs
| Cost Intensity ($/m2) | 18.62 | 21.2 | 16.07 | 17.04 | 9.28 | 16.99 | 19.53 | 14.89 | 6.63 | 11.39 | 14.77 | 7.08 | 13.48 | 13.69 | 13.69 | 16.97
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1673411.1111 | 1100291.6667 | 1116808.3333 | 574791.6667 | 311108.3333 | 786841.6667 | 95733.3333 | 441997.2222 | 339613.8889 | 75150 | 317866.6667 | 201025 | 245747.2222 | 118377.7778 | 89786.1111 | 42811.1111
| Interior Lighting | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667
| Exterior Lighting | 48986.1111 | 48966.6667 | 48958.3333 | 48950 | 48913.8889 | 48902.7778 | 48927.7778 | 48897.2222 | 48916.6667 | 48819.4444 | 48905.5556 | 48877.7778 | 48875 | 48863.8889 | 48833.3333 | 48536.1111
| Interior Equipment | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 370741.6667 | 321591.6667 | 353883.3333 | 310669.4444 | 308627.7778 | 330308.3333 | 295650 | 301638.8889 | 318236.1111 | 283194.4444 | 307680.5556 | 307363.8889 | 311113.8889 | 309316.6667 | 311752.7778 | 349027.7778
| Pumps | 23633.3333 | 13616.6667 | 14475 | 9200 | 7188.8889 | 10750 | 3791.6667 | 7427.7778 | 7072.2222 | 3308.3333 | 6475 | 4988.8889 | 6797.2222 | 4994.4444 | 5652.7778 | 9197.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 43633.3333 | 41647.2222 | 41763.8889 | 39800 | 39863.8889 | 40419.4444 | 38158.3333 | 38616.6667 | 38591.6667 | 37375 | 37775 | 37572.2222 | 37391.6667 | 36713.8889 | 36127.7778 | 35175
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3944050 | 3309758.3333 | 3359533.3333 | 2767055.5556 | 2499344.4444 | 3000863.8889 | 2265905.5556 | 2622222.2222 | 2536072.2222 | 2231491.6667 | 2502347.2222 | 2383472.2222 | 2433566.6667 | 2301908.3333 | 2275797.2222 | 2268391.6667
Gas (MJ)
| Heating | 211510 | 2074380 | 1444470 | 4115450 | 1231630 | 2294290 | 3522210 | 6813980 | 4506680 | 6618800 | 9312400 | 6519540 | 12444690 | 9901780 | 14993580 | 26582850
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 188470 | 256650 | 225520 | 317240 | 296690 | 270010 | 347960 | 365490 | 356170 | 382460 | 406520 | 402650 | 443070 | 446410 | 497680 | 562320
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 753370 | 2684420 | 2023380 | 4786080 | 1881710 | 2917700 | 4223560 | 7532870 | 5216250 | 7354650 | 10072310 | 7275580 | 13241150 | 10701580 | 15844650 | 27498560
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 14951950 | 14599550 | 14117700 | 14747470 | 10879360 | 13720810 | 12380820 | 16972870 | 14346110 | 15388020 | 19080760 | 15856070 | 22001990 | 18988460 | 24037520 | 35664760
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 307.4867 | 202.1769 | 205.2118 | 105.6171 | 57.1657 | 144.581 | 17.5909 | 81.2163 | 62.4035 | 13.8087 | 58.4075 | 36.938 | 45.1557 | 21.7517 | 16.4981 | 7.8665
| Interior Lighting (elec) | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792
| Exterior Lighting (elec) | 9.0011 | 8.9976 | 8.996 | 8.9945 | 8.9879 | 8.9858 | 8.9904 | 8.9848 | 8.9884 | 8.9705 | 8.9863 | 8.9812 | 8.9807 | 8.9787 | 8.9731 | 8.9184
| Interior Equipment (elec) | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 68.1232 | 59.092 | 65.0255 | 57.085 | 56.7099 | 60.6937 | 54.3252 | 55.4257 | 58.4754 | 52.0365 | 56.5358 | 56.4776 | 57.1667 | 56.8365 | 57.2841 | 64.1333
| Pumps (elec) | 4.3426 | 2.502 | 2.6598 | 1.6905 | 1.3209 | 1.9753 | 0.69671 | 1.3648 | 1.2995 | 0.6079 | 1.1898 | 0.9167 | 1.249 | 0.91772 | 1.0387 | 1.69
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 8.0176 | 7.6526 | 7.6741 | 7.3132 | 7.3249 | 7.427 | 7.0115 | 7.0958 | 7.0912 | 6.8676 | 6.9411 | 6.9038 | 6.8707 | 6.7461 | 6.6384 | 6.4634
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 724.7131 | 608.163 | 617.3091 | 508.4422 | 459.2507 | 551.4041 | 416.3567 | 481.8293 | 465.9994 | 410.0332 | 459.8025 | 437.9594 | 447.1641 | 422.9721 | 418.1743 | 416.8135
Gas (MJ/m2)
| Heating (gas) | 10.7957 | 105.8789 | 73.7275 | 210.0577 | 62.8639 | 117.1034 | 179.778 | 347.794 | 230.0265 | 337.8318 | 475.3165 | 332.7654 | 635.1924 | 505.3991 | 765.2909 | 1356.8217
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 9.6197 | 13.0997 | 11.5108 | 16.1923 | 15.1434 | 13.7816 | 17.7603 | 18.6551 | 18.1794 | 19.5212 | 20.7493 | 20.5518 | 22.6148 | 22.7853 | 25.4022 | 28.7015
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 38.4529 | 137.0161 | 103.2758 | 244.2875 | 96.0448 | 148.923 | 215.5757 | 384.487 | 266.2439 | 375.3905 | 514.1032 | 371.3546 | 675.8447 | 546.2219 | 808.7306 | 1403.5606
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 763.1661 | 745.1792 | 720.5849 | 752.7292 | 555.296 | 700.3272 | 631.9324 | 866.3164 | 732.2433 | 785.4236 | 973.9057 | 809.3135 | 1123.0089 | 969.1946 | 1226.9049 | 1820.3736
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1087.2875 | 930.4465 | 709.9746 | 565.569 | 842.9694 | 557.2495 | 523.6057 | 515.7224 | 527.3196 | 499.6681 | 502.0579 | 544.0242 | 503.0821 | 507.4347 | 503.9276 | 521.9018
| Feb | 1137.7074 | 873.725 | 797.9437 | 545.9204 | 802.0175 | 612.0698 | 635.2766 | 510.6893 | 613.8552 | 518.408 | 500.1781 | 518.5283 | 501.5424 | 528.5612 | 503.2428 | 513.509
| Mar | 1177.4309 | 937.5973 | 1010.8494 | 734.9606 | 773.9513 | 720.5357 | 550.1125 | 737.2831 | 626.3489 | 594.0535 | 623.0843 | 654.0964 | 521.4584 | 601.0578 | 500.5584 | 513.2835
| Apr | 1244.3994 | 1045.5076 | 1040.7718 | 904.0563 | 888.068 | 1021.876 | 660.6149 | 748.6033 | 806.5509 | 539.23 | 630.5833 | 723.5058 | 624.4455 | 568.1858 | 525.8493 | 505.3369
| May | 1380.4681 | 1346.1947 | 1251.5736 | 1094.0203 | 890.2391 | 1178.7871 | 727.8016 | 1050.69 | 942.1024 | 734.4146 | 1014.7936 | 842.7767 | 981.8156 | 703.8243 | 695.872 | 607.6825
| Jun | 1478.5663 | 1343.8873 | 1544.9349 | 1221.8502 | 872.5572 | 1425.7494 | 748.4603 | 1357.2933 | 1063.9945 | 787.5588 | 1340.5372 | 977.0588 | 1235.6606 | 963.3208 | 1025.0713 | 795.1281
| Jul | 1134.1719 | 1187.4516 | 1343.0687 | 1122.8006 | 623.7291 | 1179.7374 | 607.814 | 1151.1437 | 872.5311 | 632.7038 | 1029.3636 | 782.6413 | 983.8095 | 732.683 | 800.3154 | 517.0025
| Aug | 1218.3786 | 1125.3842 | 1296.6597 | 1020.0693 | 793.5089 | 1128.8983 | 565.9671 | 1153.8009 | 845.8016 | 572.3865 | 1042.7246 | 813.568 | 939.4823 | 685.443 | 725.193 | 512.8111
| Sep | 1402.708 | 1417.2416 | 1392.2168 | 1183.7659 | 1079.9165 | 1181.6975 | 1042.5191 | 1058.3691 | 899.7602 | 866.7836 | 1013.4076 | 899.1759 | 972.7425 | 779.037 | 872.9526 | 521.1657
| Oct | 1349.4523 | 1170.5775 | 1054.4215 | 989.2178 | 948.2015 | 1021.5493 | 713.3367 | 913.5667 | 790.2077 | 619.5269 | 778.5249 | 811.1515 | 662.8475 | 666.8661 | 554.0219 | 508.5361
| Nov | 1212.8939 | 1029.6581 | 920.4848 | 645.9228 | 857.4556 | 643.7386 | 552.2067 | 766.8055 | 587.8947 | 516.4334 | 772.288 | 595.7376 | 558.0534 | 510.295 | 501.522 | 514.2643
| Dec | 1061.0915 | 918.5377 | 684.186 | 558.4681 | 865.7415 | 613.7043 | 526.1186 | 500.0723 | 519.129 | 499.6838 | 499.9178 | 511.6267 | 500.7754 | 507.085 | 501.4714 | 521.3153
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:39 | 26-JAN-15:00 | 23-JAN-16:30 | 26-JAN-12:00 | 18-JAN-14:00 | 27-JAN-14:00 | 09-JAN-11:50 | 25-JAN-14:00 | 09-JAN-11:39 | 27-JAN-11:09 | 27-JAN-12:00 | 04-JAN-11:09 | 05-JAN-08:09 | 09-JAN-11:09 | 02-JAN-11:09
| Feb | 23-FEB-11:00 | 23-FEB-15:09 | 28-FEB-15:00 | 22-FEB-15:00 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-16:10 | 15-FEB-12:00 | 14-FEB-16:10 | 21-FEB-12:00 | 28-FEB-11:39 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-09:39
| Mar | 13-MAR-15:09 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-15:39 | 30-MAR-11:00 | 31-MAR-15:00 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-15:09 | 29-MAR-15:00 | 31-MAR-15:09 | 30-MAR-15:00 | 23-MAR-13:00 | 30-MAR-15:00 | 07-MAR-11:09 | 14-MAR-07:19
| Apr | 03-APR-13:00 | 21-APR-14:00 | 26-APR-14:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 14-APR-13:00 | 07-APR-14:39 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 24-APR-11:00
| May | 24-MAY-14:00 | 18-MAY-13:00 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-11:20 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-15:09 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:00 | 29-JUN-13:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-15:09 | 20-JUN-14:00
| Jul | 13-JUL-14:00 | 18-JUL-11:00 | 11-JUL-15:00 | 03-JUL-15:00 | 24-JUL-13:50 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-12:00 | 17-JUL-14:00 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-14:00 | 21-JUL-15:00
| Aug | 21-AUG-13:00 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-11:00 | 04-AUG-14:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:50 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-13:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-15:09 | 20-SEP-15:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-15:09 | 13-SEP-14:00 | 06-SEP-10:00 | 05-SEP-13:00 | 14-SEP-15:09 | 07-SEP-15:00 | 07-SEP-14:00 | 07-SEP-14:00
| Oct | 06-OCT-13:00 | 30-OCT-13:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:09 | 31-OCT-12:00 | 03-OCT-11:00 | 11-OCT-15:00 | 17-OCT-15:09 | 31-OCT-11:00 | 05-OCT-15:09 | 06-OCT-15:09 | 06-OCT-15:00 | 06-OCT-14:00 | 30-OCT-07:10
| Nov | 01-NOV-11:00 | 27-NOV-12:00 | 13-NOV-15:39 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-12:00 | 14-NOV-12:00 | 03-NOV-13:00 | 08-NOV-16:10 | 03-NOV-10:39 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-11:39 | 09-NOV-11:50 | 27-NOV-10:09
| Dec | 15-DEC-16:10 | 19-DEC-15:09 | 11-DEC-15:00 | 13-DEC-16:10 | 19-DEC-12:00 | 05-DEC-14:30 | 07-DEC-14:00 | 06-DEC-11:39 | 08-DEC-14:00 | 13-DEC-11:09 | 14-DEC-11:39 | 21-DEC-14:30 | 20-DEC-11:09 | 18-DEC-08:09 | 20-DEC-11:09 | 29-DEC-11:09
Source Energy
| Total Source Energy (GJ) | 47919.37 | 46207.14 | 40463.87 | 38736.54 | 29902.54 | 41828.85 | 29858.84 | 41983.32 | 35989.03 | 22025.4 | 42942.91 | 36415.02 | 44570.34 | 40491.3 | 45461.24 | 59198.11
| Total Source Energy (MJ/m2) | 2445.86 | 2358.47 | 2065.33 | 1977.16 | 1526.26 | 2135 | 1524.03 | 2142.88 | 1836.92 | 1124.2 | 2191.86 | 1858.67 | 2274.93 | 2066.73 | 2320.4 | 3021.55
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
| Total Building | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
Emissions
| Carbon Equivalent (kg) | 1095240 | 1152410 | 1050650 | 938660.2651 | 326020.3965 | 1064730 | 340969.0534 | 843458.8294 | 1130040 | 295152.9106 | 1515760 | 1104840 | 1071770 | 1034180 | 1064710 | 1134170
| CO2 (kg) | 2543880 | 2910130 | 2490420 | 2183860 | 877862.9615 | 2549220 | 927036.9755 | 1979330 | 2685700 | 769260.826 | 3602950 | 2647740 | 2610240 | 2514080 | 2621380 | 3031620
| NOX (kg) | 4452.8131 | 3768.2366 | 4126.7429 | 3961.9053 | 756.3602 | 4069.259 | 804.7982 | 3529.0878 | 4482.0728 | 968.2114 | 6081.4758 | 4324.6277 | 4130.6422 | 3979.2139 | 4026.5984 | 3303.852
| SO2 (kg) | 16882.3158 | 15788.2658 | 13509.8977 | 9713.6448 | 7273.2996 | 16507.9345 | 6594.6435 | 9574.1763 | 11075.9241 | 1726.7345 | 16866.5114 | 10410.0935 | 5747.1552 | 6149.2427 | 5375.4894 | 11554.3849
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.077 | 0.0446 | 0.0368 | 0.036 | 0.0035 | 0.0312 | 0.0034 | 0.0394 | 0.0437 | 0.0075 | 0.0519 | 0.0413 | 0.0433 | 0.0438 | 0.0409 | 0.0421
| Water for Electricity (m3) | 2089.39 | 5385.36 | 99792.9 | 17276.4 | 43882.9 | 82325.7 | 39784.2 | 595.3429 | 11515.8 | 22798.7 | 3882.24 | 10822.9 | 3775.53 | 145813 | 3530.76 | 2317.57

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14951.95 | 763.17 | 763.17
Net Site Energy | 14951.95 | 763.17 | 763.17
Total Source Energy | 47919.37 | 2445.86 | 2445.86
Net Source Energy | 47919.37 | 2445.86 | 2445.86
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 211.51 | 0 | 0 | 0 | 0
Cooling | 6024.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1334.67 | 0 | 0 | 0 | 0 | 0
Pumps | 85.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 188.47 | 0 | 0 | 0 | 2677.93
Refrigeration | 157.08 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14198.58 | 753.37 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 753.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1764229.2 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 875145.65 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 157928.03 | 106772.49 | 51155.54 | 0.68 | 2.89
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18882.36 | 12766.05 | 6116.31 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 464861.53 | 312520 | 152341.53 | 0.67 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 383945.71 | 250144.56 | 133801.14 | 0.65 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 384241.14 | 250333.99 | 133907.15 | 0.65 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 283617.21 | 188640.55 | 94976.66 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9436.72 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11356 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9108.97 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11908.47 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8986.3 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11859.06 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8990.9 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11877.46 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9608.59 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12545.54 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9601.68 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12549.22 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9714.95 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12604.88 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7595.09 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13987.76 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6849.16 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13940.83 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6918.4 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14096.27 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42083.58 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4390.62 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8427.82 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31603.96 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57075.08 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12072.82 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9603.58 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16339.45 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27424.43 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17559.04 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27302.51 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17614.14 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30760.54 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18080.2 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29004.88 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18047.98 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29020.1 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18726.39 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32823.5 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18566.83 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28891.3 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 765026.92 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 205143.29 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 306010.77 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 29439.32 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 173803.92 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 42228.87 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 37728.52 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 37755.81 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 39795.32 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.36 | 11930.85 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.76 | 881.98 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.03 | 32034.19 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.68 | 21485.3 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.69 | 21500.83 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.38 | 22662.28 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 16166.72 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4818.92 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 181126.1926 | 312.652 | 1167.4682 | 0 | 0.0053 | 144485.0932 | 77541.871
February | 165951.2804 | 289.3597 | 1092.4975 | 0 | 0.005 | 135209.0269 | 71336.1267
March | 197010.4696 | 342.9886 | 1292.8181 | 0 | 0.0059 | 160000.585 | 84634.4603
April | 200448.9331 | 351.2048 | 1332.9326 | 0 | 0.0061 | 164966.9039 | 86335.037
May | 250846.9783 | 440.2407 | 1673.8433 | 0 | 0.0076 | 207159.3799 | 108115.4438
June | 270596.3368 | 475.2722 | 1808.5465 | 0 | 0.0082 | 223830.8953 | 116664.6272
July | 208499.5138 | 366.4022 | 1395.0623 | 0 | 0.0064 | 172657.0469 | 89911.9167
August | 219536.3116 | 385.7621 | 1468.6308 | 0 | 0.0067 | 181762.0794 | 94667.8081
September | 248392.3009 | 436.2043 | 1659.6015 | 0 | 0.0076 | 205396.9861 | 107084.6891
October | 230849.8589 | 404.9414 | 1538.8015 | 0 | 0.007 | 190446.0851 | 99476.2118
November | 201773.5305 | 353.4514 | 1341.1569 | 0 | 0.0061 | 165984.7112 | 86898.1188
December | 168848.5658 | 294.3335 | 1110.9569 | 0 | 0.0051 | 137493.5298 | 72573.7409
Annual Sum or Average | 2543880 | 4452.8131 | 16882.3158 | 0 | 0.077 | 2089390 | 1095240
Minimum of Months | 165951.2804 | 289.3597 | 1092.4975 | 0 | 0.005 | 135209.0269 | 71336.1267
Maximum of Months | 270596.3368 | 475.2722 | 1808.5465 | 0 | 0.0082 | 223830.8953 | 116664.6272
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 981856000000 | 1087287.489 | 06-JAN-12:00 | 270589.05 | 151653.867 | 100086.518 | 0 | 550962.513 | 0 | 8678.069 | 0 | 0 | 0 | 0 | 0 | 5317.473 | 0 | 0
February | 918820000000 | 1137707.439 | 23-FEB-11:00 | 270589.05 | 151653.867 | 105424.341 | 0 | 595553.843 | 0 | 9149.066 | 0 | 0 | 0 | 0 | 0 | 5337.271 | 0 | 0
March | 1087290000000 | 1177430.946 | 13-MAR-15:09 | 270589.05 | 133019.064 | 106860.91 | 0 | 652534.831 | 0 | 9054.827 | 0 | 0 | 0 | 0 | 0 | 5372.263 | 0 | 0
April | 1121040000000 | 1244399.424 | 03-APR-13:00 | 270589.05 | 145652.643 | 118659.915 | 0 | 693816.026 | 0 | 10292.66 | 0 | 0 | 0 | 0 | 0 | 5389.13 | 0 | 0
May | 1407760000000 | 1380468.084 | 24-MAY-14:00 | 270589.05 | 137835.548 | 124274.101 | 0 | 830997.197 | 0 | 11251.35 | 0 | 0 | 0 | 0 | 0 | 5520.84 | 0 | 0
June | 1521060000000 | 1478566.279 | 27-JUN-14:00 | 270589.05 | 137835.548 | 127522.371 | 0 | 924065.769 | 0 | 13062.259 | 0 | 0 | 0 | 0 | 0 | 5491.282 | 0 | 0
July | 1173300000000 | 1134171.897 | 13-JUL-14:00 | 150327.25 | 78000.308 | 105190.879 | 0 | 785777.841 | 0 | 9665.595 | 0 | 0 | 0 | 0 | 0 | 5210.025 | 0 | 0
August | 1235170000000 | 1218378.618 | 21-AUG-13:00 | 150327.25 | 84617.158 | 108505.839 | 0 | 859287.164 | 0 | 10374.882 | 0 | 0 | 0 | 0 | 0 | 5266.325 | 0 | 0
September | 1395790000000 | 1402708.025 | 07-SEP-13:00 | 270589.05 | 145652.643 | 124070.264 | 0 | 845052.11 | 0 | 11873.511 | 0 | 0 | 0 | 0 | 0 | 5470.447 | 0 | 0
October | 1294190000000 | 1349452.329 | 06-OCT-13:00 | 270589.05 | 145652.643 | 123842.017 | 0 | 792499.082 | 0 | 11442.296 | 0 | 0 | 0 | 0 | 0 | 5427.242 | 0 | 0
November | 1127960000000 | 1212893.895 | 01-NOV-11:00 | 270589.05 | 151653.867 | 110018.506 | 0 | 665456.766 | 0 | 9819.372 | 0 | 0 | 0 | 0 | 0 | 5356.334 | 0 | 0
December | 934345000000 | 1061091.468 | 15-DEC-16:10 | 270589.05 | 133019.064 | 96010.225 | 0 | 547906.247 | 0 | 8299.207 | 0 | 0 | 0 | 0 | 0 | 5267.675 | 0 | 0
Annual Sum or Average | 14198600000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 918820000000 | 1061091.468 |  | 150327.25 | 78000.308 | 96010.225 | 0 | 547906.247 | 0 | 8299.207 | 0 | 0 | 0 | 0 | 0 | 5210.025 | 0 | 0
Maximum of Months | 1521060000000 | 1478566.279 |  | 270589.05 | 151653.867 | 127522.371 | 0 | 924065.769 | 0 | 13062.259 | 0 | 0 | 0 | 0 | 0 | 5520.84 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 356267.36 | 8608.38 | 0 | 364875.74
Cost per Total Building Area ($/m2) | 18.18 | 0.44 | 0 | 18.62
Cost per Net Conditioned Building Area ($/m2) | 18.18 | 0.44 | 0 | 18.62

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14599.55 | 745.18 | 745.18
Net Site Energy | 14599.55 | 745.18 | 745.18
Total Source Energy | 46207.14 | 2358.47 | 2358.47
Net Source Energy | 46207.14 | 2358.47 | 2358.47
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2074.38 | 0 | 0 | 0 | 0
Cooling | 3961.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1157.73 | 0 | 0 | 0 | 0 | 0
Pumps | 49.02 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 256.65 | 0 | 0 | 0 | 2677.93
Refrigeration | 149.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11915.13 | 2684.42 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 753.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1591161.84 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 896395.1 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 113583.84 | 76792.13 | 36791.71 | 0.68 | 2.9
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15160.8 | 10249.96 | 4910.84 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 378125.42 | 251617.21 | 126508.21 | 0.67 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 319205.67 | 205377.82 | 113827.85 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 320044.64 | 205938.22 | 114106.43 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 337748.54 | 217750.05 | 119998.49 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6499.41 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8571 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6606.42 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9156.7 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6538.25 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9129.07 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6541.54 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9147.33 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6544.43 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9190.4 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6536.27 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9193.27 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6606.27 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9230.97 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5906.67 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11701.46 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5177.55 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11651.76 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5222.94 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11793.11 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36601.92 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3582.11 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7321.02 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21927.99 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 44445.49 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11564.41 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8569.78 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13803.94 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24277.09 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15134.57 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24225.83 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15193.57 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27719.88 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13777.3 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23786.91 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13739.14 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23804.69 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14153.63 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27482.43 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15788.22 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25535.13 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1009940.45 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 210475.58 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 403976.18 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 31204.16 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 229445.01 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 91064.28 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 59971.14 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 60153.38 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 63980.57 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.57 | 8724.63 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 708.15 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.57 | 26376.14 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.2 | 17554.55 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.24 | 17607.9 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 10.89 | 18444.42 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 14580.8 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4935.93 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 216335.2966 | 270.2263 | 1035.0273 | 0 | 0.003 | 353002.0874 | 84392.957
February | 192058.9237 | 239.2382 | 909.5766 | 0 | 0.0026 | 310212.9804 | 74837.056
March | 209929.5299 | 270.6846 | 1122.864 | 0 | 0.0032 | 383002.7905 | 82984.511
April | 213657.0259 | 278.8365 | 1189.6582 | 0 | 0.0034 | 405801.3206 | 84889.221
May | 285413.5851 | 373.8457 | 1608.2826 | 0 | 0.0045 | 548603.2294 | 113574.7923
June | 337593.1604 | 442.7392 | 1909.9664 | 0 | 0.0054 | 651513.3492 | 134409.1031
July | 260705.7599 | 342.0394 | 1476.8567 | 0 | 0.0042 | 503774.8052 | 103814.5862
August | 263197.1277 | 345.2556 | 1490.2358 | 0 | 0.0042 | 508338.3658 | 104799.9076
September | 277740.4853 | 364.1117 | 1569.4774 | 0 | 0.0044 | 535367.7159 | 110562.2216
October | 246352.9397 | 321.8586 | 1376.6386 | 0 | 0.0039 | 469583.2705 | 97925.1561
November | 207118.2586 | 268.07 | 1121.9755 | 0 | 0.0032 | 382704.3674 | 82003.4368
December | 200023.7685 | 251.3308 | 977.7067 | 0 | 0.0028 | 333460.1449 | 78220.4796
Annual Sum or Average | 2910130 | 3768.2366 | 15788.2658 | 0 | 0.0446 | 5385360 | 1152410
Minimum of Months | 192058.9237 | 239.2382 | 909.5766 | 0 | 0.0026 | 310212.9804 | 74837.056
Maximum of Months | 337593.1604 | 442.7392 | 1909.9664 | 0 | 0.0054 | 651513.3492 | 134409.1031
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 781018000000 | 930446.478 | 03-JAN-12:39 | 270589.05 | 151653.867 | 84666.404 | 0 | 413758.598 | 0 | 4494.068 | 0 | 0 | 0 | 0 | 0 | 5284.491 | 0 | 0
February | 686347000000 | 873725.015 | 23-FEB-15:09 | 270589.05 | 137835.548 | 97463.915 | 0 | 358588.646 | 0 | 3890.381 | 0 | 0 | 0 | 0 | 0 | 5357.476 | 0 | 0
March | 847394000000 | 937597.252 | 29-MAR-11:00 | 270589.05 | 151653.867 | 90223.739 | 0 | 415165.588 | 0 | 4651.833 | 0 | 0 | 0 | 0 | 0 | 5313.175 | 0 | 0
April | 897836000000 | 1045507.559 | 21-APR-14:00 | 270589.05 | 137835.548 | 101982.154 | 0 | 523669.654 | 0 | 6066.434 | 0 | 0 | 0 | 0 | 0 | 5364.721 | 0 | 0
May | 1213790000000 | 1346194.655 | 18-MAY-13:00 | 270589.05 | 145652.643 | 106874.384 | 0 | 808062.468 | 0 | 9509.062 | 0 | 0 | 0 | 0 | 0 | 5507.048 | 0 | 0
June | 1441470000000 | 1343887.343 | 13-JUN-14:00 | 270589.05 | 137835.548 | 113247.712 | 0 | 807387.82 | 0 | 9255.23 | 0 | 0 | 0 | 0 | 0 | 5571.984 | 0 | 0
July | 1114600000000 | 1187451.561 | 18-JUL-11:00 | 150327.25 | 88818.015 | 86211.236 | 0 | 849078.274 | 0 | 7748.181 | 0 | 0 | 0 | 0 | 0 | 5268.604 | 0 | 0
August | 1124700000000 | 1125384.232 | 31-AUG-13:00 | 150327.25 | 84617.158 | 94891.928 | 0 | 783173.475 | 0 | 7061.777 | 0 | 0 | 0 | 0 | 0 | 5312.645 | 0 | 0
September | 1184500000000 | 1417241.552 | 15-SEP-14:00 | 270589.05 | 137835.548 | 108366.75 | 0 | 884052.55 | 0 | 10886.038 | 0 | 0 | 0 | 0 | 0 | 5511.616 | 0 | 0
October | 1038950000000 | 1170577.479 | 30-OCT-13:00 | 270589.05 | 145652.643 | 96352.378 | 0 | 645186.265 | 0 | 7459.974 | 0 | 0 | 0 | 0 | 0 | 5337.169 | 0 | 0
November | 846734000000 | 1029658.074 | 27-NOV-12:00 | 270589.05 | 151653.867 | 90691.117 | 0 | 505615.426 | 0 | 5809.985 | 0 | 0 | 0 | 0 | 0 | 5298.628 | 0 | 0
December | 737781000000 | 918537.729 | 19-DEC-15:09 | 270589.05 | 137835.548 | 89894.752 | 0 | 410329.13 | 0 | 4585.761 | 0 | 0 | 0 | 0 | 0 | 5303.488 | 0 | 0
Annual Sum or Average | 11915100000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 686347000000 | 873725.015 |  | 150327.25 | 84617.158 | 84666.404 | 0 | 358588.646 | 0 | 3890.381 | 0 | 0 | 0 | 0 | 0 | 5268.604 | 0 | 0
Maximum of Months | 1441470000000 | 1417241.552 |  | 270589.05 | 151653.867 | 113247.712 | 0 | 884052.55 | 0 | 10886.038 | 0 | 0 | 0 | 0 | 0 | 5571.984 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 393752.42 | 21677.61 | 0 | 415430.03
Cost per Total Building Area ($/m2) | 20.1 | 1.11 | 0 | 21.2
Cost per Net Conditioned Building Area ($/m2) | 20.1 | 1.11 | 0 | 21.2

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14117.7 | 720.59 | 720.59
Net Site Energy | 14117.7 | 720.59 | 720.59
Total Source Energy | 40463.87 | 2065.33 | 2065.33
Net Source Energy | 40463.87 | 2065.33 | 2065.33
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1444.47 | 0 | 0 | 0 | 0
Cooling | 4020.51 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1273.98 | 0 | 0 | 0 | 0 | 0
Pumps | 52.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 225.52 | 0 | 0 | 0 | 2677.93
Refrigeration | 150.35 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12094.32 | 2023.38 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 753.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1361468.72 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 827775.77 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 125557.64 | 84887.41 | 40670.23 | 0.68 | 2.89
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15114.61 | 10218.73 | 4895.87 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 371614.08 | 243494.5 | 128119.58 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 278881.68 | 180170.96 | 98710.72 | 0.65 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 279568.89 | 180625.57 | 98943.32 | 0.65 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 294383.67 | 190519.1 | 103864.57 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6189.6 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8894.52 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7788.96 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10179.83 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7712.01 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10148.24 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7715.72 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10166.67 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7546.65 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10075.94 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7537.94 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10078.33 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7618.12 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10120.65 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5388.12 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10103.75 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4671.4 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10043.6 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4730.81 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10200.82 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33874.59 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4228.67 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7249.56 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21424.28 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40743.65 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9935.37 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6073.87 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16709.84 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25848.96 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18016.39 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25799.61 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18073.94 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29259.91 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14792.6 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23921.8 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14752.49 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23926.43 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15215.26 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27617.71 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17830.86 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25875.03 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 852081.84 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 190506.76 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 340832.73 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 26246.59 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 193581.64 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 66969.7 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 48617.11 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 48738.32 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 51689.07 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.06 | 9485.39 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.61 | 705.99 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.46 | 26201.1 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.23 | 19020.87 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.25 | 19068.29 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.94 | 20222.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12475.98 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4558.09 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 165153.033 | 260.9543 | 803.953 | 0 | 0.0022 | 5937880 | 68388.618
February | 149427.5952 | 237.5679 | 737.9717 | 0 | 0.002 | 5450630 | 62024.5731
March | 186089.861 | 306.966 | 999.4076 | 0 | 0.0027 | 7382210 | 78365.8989
April | 185053.4568 | 309.1281 | 1021.8497 | 0 | 0.0028 | 7548170 | 78320.9665
May | 229264.2102 | 385.3414 | 1283.0515 | 0 | 0.0035 | 9477730 | 97271.1389
June | 299850.5583 | 505.0817 | 1686.0415 | 0 | 0.0046 | 12454600 | 127330.473
July | 240865.7883 | 405.9413 | 1355.9373 | 0 | 0.0037 | 10016200 | 102304.6562
August | 242706.5372 | 408.9601 | 1365.6959 | 0 | 0.0037 | 10088300 | 103078.0517
September | 256049.8911 | 431.0959 | 1438.2632 | 0 | 0.0039 | 10624300 | 108709.8491
October | 202119.9161 | 338.463 | 1122.0628 | 0 | 0.0031 | 8288470 | 85627.5786
November | 168768.4027 | 278.0537 | 903.9254 | 0 | 0.0025 | 6676900 | 71037.1766
December | 165068.9727 | 259.1895 | 791.7382 | 0 | 0.0022 | 5847570 | 68188.7836
Annual Sum or Average | 2490420 | 4126.7429 | 13509.8977 | 0 | 0.0368 | 99792900 | 1050650
Minimum of Months | 149427.5952 | 237.5679 | 737.9717 | 0 | 0.002 | 5450630 | 62024.5731
Maximum of Months | 299850.5583 | 505.0817 | 1686.0415 | 0 | 0.0046 | 12454600 | 127330.473
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 719636000000 | 709974.581 | 26-JAN-15:00 | 270589.05 | 137835.548 | 87762.479 | 0 | 206399.066 | 0 | 2316.076 | 0 | 0 | 0 | 0 | 0 | 5072.363 | 0 | 0
February | 660585000000 | 797943.714 | 28-FEB-15:00 | 270589.05 | 137835.548 | 95301.48 | 0 | 285785.761 | 0 | 3255.952 | 0 | 0 | 0 | 0 | 0 | 5175.924 | 0 | 0
March | 894680000000 | 1010849.411 | 17-MAR-14:00 | 270589.05 | 137835.548 | 109854.111 | 0 | 480774.206 | 0 | 6392.788 | 0 | 0 | 0 | 0 | 0 | 5403.708 | 0 | 0
April | 914795000000 | 1040771.817 | 26-APR-14:00 | 270589.05 | 137835.548 | 109110.046 | 0 | 511314.317 | 0 | 6476.003 | 0 | 0 | 0 | 0 | 0 | 5446.852 | 0 | 0
May | 1148650000000 | 1251573.6 | 30-MAY-15:00 | 270589.05 | 133019.064 | 120145.175 | 0 | 712059.178 | 0 | 10451.715 | 0 | 0 | 0 | 0 | 0 | 5309.418 | 0 | 0
June | 1509430000000 | 1544934.868 | 08-JUN-15:00 | 270589.05 | 133019.064 | 129439.465 | 0 | 995265.406 | 0 | 11305.489 | 0 | 0 | 0 | 0 | 0 | 5316.394 | 0 | 0
July | 1213900000000 | 1343068.69 | 11-JUL-15:00 | 150327.25 | 73183.824 | 121429.095 | 0 | 981957.507 | 0 | 11039.402 | 0 | 0 | 0 | 0 | 0 | 5131.611 | 0 | 0
August | 1222640000000 | 1296659.682 | 01-AUG-15:00 | 150327.25 | 73183.824 | 121728.257 | 0 | 935189.97 | 0 | 11147.05 | 0 | 0 | 0 | 0 | 0 | 5083.33 | 0 | 0
September | 1287600000000 | 1392216.806 | 08-SEP-13:00 | 270589.05 | 145652.643 | 123928.913 | 0 | 835425.26 | 0 | 11057.691 | 0 | 0 | 0 | 0 | 0 | 5563.249 | 0 | 0
October | 1004510000000 | 1054421.517 | 02-OCT-15:00 | 270589.05 | 133019.064 | 105832.594 | 0 | 533949.85 | 0 | 5808.518 | 0 | 0 | 0 | 0 | 0 | 5222.442 | 0 | 0
November | 809201000000 | 920484.775 | 13-NOV-15:39 | 270589.05 | 137835.548 | 101609.259 | 0 | 400544.466 | 0 | 4571.418 | 0 | 0 | 0 | 0 | 0 | 5335.034 | 0 | 0
December | 708691000000 | 684185.963 | 11-DEC-15:00 | 270589.05 | 137835.548 | 84966.752 | 0 | 183707.371 | 0 | 2030.619 | 0 | 0 | 0 | 0 | 0 | 5056.623 | 0 | 0
Annual Sum or Average | 12094300000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 660585000000 | 684185.963 |  | 150327.25 | 73183.824 | 84966.752 | 0 | 183707.371 | 0 | 2030.619 | 0 | 0 | 0 | 0 | 0 | 5056.623 | 0 | 0
Maximum of Months | 1509430000000 | 1544934.868 |  | 270589.05 | 145652.643 | 129439.465 | 0 | 995265.406 | 0 | 11305.489 | 0 | 0 | 0 | 0 | 0 | 5563.249 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 298120.09 | 16723.28 | 0 | 314843.37
Cost per Total Building Area ($/m2) | 15.22 | 0.85 | 0 | 16.07
Cost per Net Conditioned Building Area ($/m2) | 15.22 | 0.85 | 0 | 16.07

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14747.47 | 752.73 | 752.73
Net Site Energy | 14747.47 | 752.73 | 752.73
Total Source Energy | 38736.54 | 1977.16 | 1977.16
Net Source Energy | 38736.54 | 1977.16 | 1977.16
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4115.45 | 0 | 0 | 0 | 0
Cooling | 2069.25 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1118.41 | 0 | 0 | 0 | 0 | 0
Pumps | 33.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 317.24 | 0 | 0 | 0 | 2677.93
Refrigeration | 143.28 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9961.4 | 4786.08 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.255 | 0.129 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.255 | 0.129 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.255 | 0.129 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.255 | 0.129 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.255 | 0.129 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.255 | 0.129 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.255 | 0.129 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.255 | 0.129 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.255 | 0.129 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.255 | 0.129 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 4.092 | 0.255 | 0.129 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.255 | 0.129 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.255 | 0.129 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.255 | 0.129 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 4.092 | 0.255 | 0.129 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.255 | 0.129 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.255 | 0.129 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.255 | 0.129 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.255 | 0.129 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.255 | 0.129 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.255 | 0.129 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.255 | 0.129 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.255 | 0.129 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.255 | 0.129 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.255 | 0.129 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.255 | 0.129 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.255 | 0.129 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 753.18 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 1335.99 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1406880.66 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 926860.95 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 112865.53 | 76306.49 | 36559.04 | 0.68 | 2.9
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14681.23 | 9925.74 | 4755.5 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 348230.67 | 228415.25 | 119815.42 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 298410.87 | 188811.83 | 109599.03 | 0.63 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 299332.47 | 189418.1 | 109914.36 | 0.63 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 275766.4 | 177121.88 | 98644.53 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7034.41 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8851.73 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5689.08 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8404.06 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5632.75 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8379.54 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5635.92 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8397.32 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5464.43 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8227.15 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5455.84 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8229.43 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5516.53 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8264.68 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5221.95 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11593.61 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4497.9 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11540.06 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4540.71 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11680.79 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36267.09 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3160.52 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7386.23 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18558.77 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42798.32 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11313.03 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8928.08 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12472.21 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24108.17 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13819.01 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24069.15 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13878.5 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27575.74 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12409.53 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23059.42 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12370.43 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23072.78 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12729.58 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26725.56 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14468.35 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25403.88 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1089465.52 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 224293.75 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 435786.21 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 32596.48 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 247512.05 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 105305.23 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 67206.38 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 67446.8 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 71985.88 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.55 | 8669.46 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 685.75 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.46 | 26191.9 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.87 | 16972.98 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.9 | 17033.7 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.57 | 18180.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12892.11 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5103.69 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 198561.3727 | 322.311 | 697.3272 | 0 | 0.0027 | 1239860 | 81843.6321
February | 176562.5672 | 287.7769 | 625.8298 | 0 | 0.0024 | 1112750 | 72884.6157
March | 171813.5358 | 306.9818 | 741.0842 | 0 | 0.0028 | 1318020 | 73412.6959
April | 161090.8077 | 300.9872 | 759.3643 | 0 | 0.0028 | 1350670 | 70046.8
May | 187875.5107 | 357.955 | 919.5584 | 0 | 0.0034 | 1635670 | 82332.8415
June | 226512.9346 | 434.5669 | 1123.3604 | 0 | 0.0041 | 1998210 | 99541.7201
July | 168341.6876 | 323.3578 | 836.794 | 0 | 0.0031 | 1488480 | 74014.4946
August | 175743.187 | 337.5192 | 873.3124 | 0 | 0.0032 | 1553430 | 77263.5546
September | 201841.8789 | 387.0461 | 1000.0803 | 0 | 0.0037 | 1778920 | 88682.4877
October | 164891.9456 | 307.5819 | 774.7949 | 0 | 0.0028 | 1378110 | 71652.7778
November | 165997.3066 | 290.1346 | 684.3531 | 0 | 0.0026 | 1217060 | 70331.3718
December | 184625.1839 | 305.687 | 677.7858 | 0 | 0.0026 | 1205190 | 76653.2734
Annual Sum or Average | 2183860 | 3961.9053 | 9713.6448 | 0 | 0.036 | 17276400 | 938660.2651
Minimum of Months | 161090.8077 | 287.7769 | 625.8298 | 0 | 0.0024 | 1112750 | 70046.8
Maximum of Months | 226512.9346 | 434.5669 | 1123.3604 | 0 | 0.0041 | 1998210 | 99541.7201
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 714892000000 | 565568.966 | 23-JAN-16:30 | 270589.05 | 133019.064 | 77135.068 | 0 | 78431.713 | 0 | 1800.178 | 0 | 0 | 0 | 0 | 0 | 4593.893 | 0 | 0
February | 641603000000 | 545920.37 | 22-FEB-15:00 | 270589.05 | 137835.548 | 78590.162 | 0 | 52191.751 | 0 | 1889.98 | 0 | 0 | 0 | 0 | 0 | 4823.879 | 0 | 0
March | 759959000000 | 734960.631 | 28-MAR-15:39 | 270589.05 | 133019.064 | 86793.587 | 0 | 237023.375 | 0 | 2648.725 | 0 | 0 | 0 | 0 | 0 | 4886.831 | 0 | 0
April | 778783000000 | 904056.252 | 14-APR-15:00 | 270589.05 | 133019.064 | 92673.184 | 0 | 398522.452 | 0 | 4153.638 | 0 | 0 | 0 | 0 | 0 | 5098.865 | 0 | 0
May | 943112000000 | 1094020.283 | 15-MAY-14:00 | 270589.05 | 137835.548 | 107587.741 | 0 | 564467.159 | 0 | 8139.037 | 0 | 0 | 0 | 0 | 0 | 5401.748 | 0 | 0
June | 1152150000000 | 1221850.249 | 19-JUN-15:09 | 270589.05 | 133019.064 | 110730.513 | 0 | 692865.179 | 0 | 9119.64 | 0 | 0 | 0 | 0 | 0 | 5526.803 | 0 | 0
July | 858241000000 | 1122800.58 | 03-JUL-15:00 | 150327.25 | 73183.824 | 99980.373 | 0 | 785049.063 | 0 | 8955.126 | 0 | 0 | 0 | 0 | 0 | 5304.944 | 0 | 0
August | 895696000000 | 1020069.347 | 17-AUG-13:00 | 150327.25 | 84617.158 | 88060.325 | 0 | 685035.18 | 0 | 6789.085 | 0 | 0 | 0 | 0 | 0 | 5240.349 | 0 | 0
September | 1025710000000 | 1183765.918 | 11-SEP-13:00 | 270589.05 | 145652.643 | 108392.465 | 0 | 644196.57 | 0 | 9527.325 | 0 | 0 | 0 | 0 | 0 | 5407.864 | 0 | 0
October | 794606000000 | 989217.774 | 12-OCT-15:00 | 270589.05 | 133019.064 | 93380.025 | 0 | 482445.376 | 0 | 4558.495 | 0 | 0 | 0 | 0 | 0 | 5225.764 | 0 | 0
November | 701744000000 | 645922.849 | 22-NOV-15:09 | 270589.05 | 137835.548 | 85685.273 | 0 | 144356.082 | 0 | 2361.622 | 0 | 0 | 0 | 0 | 0 | 5095.275 | 0 | 0
December | 694903000000 | 558468.087 | 13-DEC-16:10 | 270589.05 | 133019.064 | 73589.384 | 0 | 75794.063 | 0 | 791.514 | 0 | 0 | 0 | 0 | 0 | 4685.012 | 0 | 0
Annual Sum or Average | 9961400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 641603000000 | 545920.37 |  | 150327.25 | 73183.824 | 73589.384 | 0 | 52191.751 | 0 | 791.514 | 0 | 0 | 0 | 0 | 0 | 4593.893 | 0 | 0
Maximum of Months | 1152150000000 | 1221850.249 |  | 270589.05 | 145652.643 | 110730.513 | 0 | 785049.063 | 0 | 9527.325 | 0 | 0 | 0 | 0 | 0 | 5526.803 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 287561.9 | 46350.63 | 0 | 333912.53
Cost per Total Building Area ($/m2) | 14.68 | 2.37 | 0 | 17.04
Cost per Net Conditioned Building Area ($/m2) | 14.68 | 2.37 | 0 | 17.04

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10879.36 | 555.3 | 555.3
Net Site Energy | 10879.36 | 555.3 | 555.3
Total Source Energy | 29902.54 | 1526.26 | 1526.26
Net Source Energy | 29902.54 | 1526.26 | 1526.26
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1231.63 | 0 | 0 | 0 | 0
Cooling | 1119.99 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.09 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1111.06 | 0 | 0 | 0 | 0 | 0
Pumps | 25.88 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 296.69 | 0 | 0 | 0 | 2677.93
Refrigeration | 143.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8997.64 | 1881.71 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.44 | 0.272 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.44 | 0.272 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.44 | 0.272 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.44 | 0.272 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.44 | 0.272 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.44 | 0.272 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.44 | 0.272 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.44 | 0.272 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.44 | 0.272 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.44 | 0.272 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.44 | 0.272 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.44 | 0.272 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.44 | 0.272 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.44 | 0.272 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.44 | 0.272 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.44 | 0.272 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.44 | 0.272 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.44 | 0.272 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.44 | 0.272 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.44 | 0.272 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.44 | 0.272 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.44 | 0.272 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.44 | 0.272 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.44 | 0.272 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.44 | 0.272 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.44 | 0.272 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.44 | 0.272 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 753.18 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1153417.07 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 842609.35 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 128541.58 | 88314.06 | 40227.53 | 0.69 | 2.92
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14842.01 | 10034.44 | 4807.58 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 416054.5 | 287195.65 | 128858.85 | 0.69 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 280519.02 | 190578.06 | 89940.96 | 0.68 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 280198.16 | 190355.88 | 89842.27 | 0.68 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 294875.7 | 200432.32 | 94443.38 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6419.26 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8072.25 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7963.5 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11218.86 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7851.56 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11172.87 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7855.61 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11193.74 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7008.77 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10209.96 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6999.67 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10215.22 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7110.38 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10268.41 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6446.69 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13913.64 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5677.26 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13839.44 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5728.15 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13968.49 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38642.93 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4901.7 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10127.07 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24139.32 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52122.48 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11330.33 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9832.4 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19117.27 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33590.07 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20151.37 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33388.39 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20212.27 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36887.05 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23217.66 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23244.64 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26963.03 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19271.33 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32806.17 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 795660.69 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 188937.37 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 318264.28 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 24066.63 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 180763.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 50319.69 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 40277.29 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 40236.55 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 42370.16 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.41 | 10145.21 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 693.26 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.8 | 29966.83 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.81 | 20002.44 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.79 | 19982.21 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.42 | 21041.8 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10569.47 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4639.77 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 79846.152 | 69.197 | 589.5956 | 0 | 0.0003 | 3557010 | 29433.7204
February | 70956.6387 | 61.4823 | 525.8716 | 0 | 0.0003 | 3172570 | 26162.6254
March | 80217.0101 | 69.356 | 621.3864 | 0 | 0.0003 | 3748930 | 29659.0675
April | 70550.0026 | 60.8018 | 581.5749 | 0 | 0.0003 | 3508880 | 26191.8365
May | 75794.4088 | 65.1857 | 649.1311 | 0 | 0.0003 | 3916560 | 28213.0456
June | 76282.6473 | 65.5123 | 669.9956 | 0 | 0.0003 | 4042510 | 28445.6824
July | 55180.1735 | 47.3232 | 496.4794 | 0 | 0.0002 | 2995620 | 20612.6898
August | 63614.9559 | 54.5498 | 573.6562 | 0 | 0.0003 | 3461290 | 23767.4454
September | 78290.5525 | 67.1609 | 701.1917 | 0 | 0.0003 | 4230780 | 29235.7998
October | 76723.7121 | 65.9128 | 669.9955 | 0 | 0.0003 | 4042500 | 28598.3357
November | 74627.7952 | 64.3362 | 611.6 | 0 | 0.0003 | 3690020 | 27694.7729
December | 75778.9128 | 65.5422 | 582.8217 | 0 | 0.0003 | 3516240 | 28005.3751
Annual Sum or Average | 877862.9615 | 756.3602 | 7273.2996 | 0 | 0.0035 | 43882900 | 326020.3965
Minimum of Months | 55180.1735 | 47.3232 | 496.4794 | 0 | 0.0002 | 2995620 | 20612.6898
Maximum of Months | 80217.0101 | 69.356 | 701.1917 | 0 | 0.0003 | 4230780 | 29659.0675
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 729321000000 | 842969.376 | 26-JAN-12:00 | 270589.05 | 151653.867 | 100194.12 | 0 | 311668.457 | 0 | 3654.208 | 0 | 0 | 0 | 0 | 0 | 5209.674 | 0 | 0
February | 650497000000 | 802017.498 | 13-FEB-11:00 | 270589.05 | 151653.867 | 96945.328 | 0 | 274427.641 | 0 | 3218.972 | 0 | 0 | 0 | 0 | 0 | 5182.639 | 0 | 0
March | 768671000000 | 773951.309 | 30-MAR-11:00 | 270589.05 | 151653.867 | 96451.703 | 0 | 247122.268 | 0 | 3013.216 | 0 | 0 | 0 | 0 | 0 | 5121.205 | 0 | 0
April | 719452000000 | 888068.015 | 11-APR-15:00 | 270589.05 | 133019.064 | 93474.124 | 0 | 382684.732 | 0 | 3209.696 | 0 | 0 | 0 | 0 | 0 | 5091.349 | 0 | 0
May | 803042000000 | 890239.079 | 30-MAY-11:20 | 270589.05 | 151653.867 | 91678.825 | 0 | 365629.124 | 0 | 5488.025 | 0 | 0 | 0 | 0 | 0 | 5200.189 | 0 | 0
June | 828866000000 | 872557.194 | 28-JUN-12:00 | 270589.05 | 145652.643 | 95052.183 | 0 | 350874.519 | 0 | 5162.52 | 0 | 0 | 0 | 0 | 0 | 5226.278 | 0 | 0
July | 614214000000 | 623729.081 | 24-JUL-13:50 | 150327.25 | 84617.158 | 84002.369 | 0 | 296078.234 | 0 | 3774.121 | 0 | 0 | 0 | 0 | 0 | 4929.949 | 0 | 0
August | 709694000000 | 793508.926 | 08-AUG-11:00 | 150327.25 | 88818.015 | 84793.639 | 0 | 459640.627 | 0 | 4913.91 | 0 | 0 | 0 | 0 | 0 | 5015.485 | 0 | 0
September | 867470000000 | 1079916.528 | 25-SEP-15:09 | 270589.05 | 133019.064 | 120954.864 | 0 | 541041.533 | 0 | 9000.207 | 0 | 0 | 0 | 0 | 0 | 5311.81 | 0 | 0
October | 828864000000 | 948201.468 | 19-OCT-10:00 | 270589.05 | 151653.867 | 102509.537 | 0 | 413792.578 | 0 | 4308.771 | 0 | 0 | 0 | 0 | 0 | 5347.664 | 0 | 0
November | 756592000000 | 857455.59 | 20-NOV-12:00 | 270589.05 | 151653.867 | 100465.666 | 0 | 322965.315 | 0 | 6531.272 | 0 | 0 | 0 | 0 | 0 | 5250.419 | 0 | 0
December | 720962000000 | 865741.525 | 19-DEC-12:00 | 270589.05 | 151653.867 | 101611.798 | 0 | 332775.587 | 0 | 3887.837 | 0 | 0 | 0 | 0 | 0 | 5223.387 | 0 | 0
Annual Sum or Average | 8997640000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 614214000000 | 623729.081 |  | 150327.25 | 84617.158 | 84002.369 | 0 | 247122.268 | 0 | 3013.216 | 0 | 0 | 0 | 0 | 0 | 4929.949 | 0 | 0
Maximum of Months | 867470000000 | 1079916.528 |  | 270589.05 | 151653.867 | 120954.864 | 0 | 541041.533 | 0 | 9000.207 | 0 | 0 | 0 | 0 | 0 | 5347.664 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 165658.38 | 16117.64 | 0 | 181776.02
Cost per Total Building Area ($/m2) | 8.46 | 0.82 | 0 | 9.28
Cost per Net Conditioned Building Area ($/m2) | 8.46 | 0.82 | 0 | 9.28

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13720.81 | 700.33 | 700.33
Net Site Energy | 13720.81 | 700.33 | 700.33
Total Source Energy | 41828.85 | 2135 | 2135
Net Source Energy | 41828.85 | 2135 | 2135
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2294.29 | 0 | 0 | 0 | 0
Cooling | 2832.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1189.11 | 0 | 0 | 0 | 0 | 0
Pumps | 38.7 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 270.01 | 0 | 0 | 0 | 2677.93
Refrigeration | 145.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10803.11 | 2917.7 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.251 | 0.11 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.251 | 0.11 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.251 | 0.11 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.251 | 0.11 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.251 | 0.11 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.251 | 0.11 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.251 | 0.11 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.251 | 0.11 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 753.18 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1055270.39 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 798940.44 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 97431.88 | 65872.06 | 31559.82 | 0.68 | 2.9
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12785.3 | 8643.92 | 4141.37 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 310729.34 | 203421.09 | 107308.25 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 235697.47 | 151859.52 | 83837.95 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 236390.16 | 152319.34 | 84070.82 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 250103.13 | 161456.45 | 88646.68 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6473.19 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7482.98 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6680.18 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9022.88 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6618.68 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8997.4 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6622.16 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9015.26 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6459.04 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8882.59 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6449.43 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8884.29 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6513.06 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8920.89 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4572.59 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9278.06 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3864.4 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9217.54 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3913.24 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9364.81 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30855.23 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3389.95 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6299.24 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17104.11 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35871.03 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9471.33 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5548.43 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14199.37 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23142.59 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15494.22 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23114 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15550.44 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26564.69 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12519.4 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21342.96 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12479.06 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21344.1 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12891.94 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24981 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15298.26 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23164.31 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 921122.77 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 178438.35 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 368449.11 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 24000.65 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 209266.82 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 74759.81 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 54133.45 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 54302.93 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 57974.49 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.92 | 7483.96 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 597.19 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.14 | 23954.51 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.24 | 17612.28 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.27 | 17667.41 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 10.96 | 18576.17 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9670.09 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4399.31 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 197854.8606 | 293.7783 | 1073.9666 | 0 | 0.0021 | 5355090 | 80345.7147
February | 160597.6984 | 249.4675 | 975.2122 | 0 | 0.0019 | 4863160 | 66360.4522
March | 188042.4711 | 293.7838 | 1157.7004 | 0 | 0.0022 | 5773260 | 77875.9654
April | 183456.9244 | 296.607 | 1223.3431 | 0 | 0.0023 | 6101000 | 77014.9676
May | 228000.3627 | 371.2916 | 1545.4504 | 0 | 0.0029 | 7707490 | 95991.5671
June | 299666.3313 | 489.6895 | 2047.1273 | 0 | 0.0038 | 10209500 | 126339.8898
July | 237808.872 | 388.8727 | 1627.0523 | 0 | 0.003 | 8114520 | 100288.2616
August | 246150.0563 | 402.4653 | 1683.6775 | 0 | 0.0032 | 8396920 | 103800.9789
September | 248994.6159 | 406.6914 | 1699.1409 | 0 | 0.0032 | 8474020 | 104956.3644
October | 201381.5864 | 326.3001 | 1349.5725 | 0 | 0.0025 | 6730550 | 84613.8344
November | 172327.3085 | 270.9024 | 1076.6525 | 0 | 0.002 | 5369150 | 71541.337
December | 184941.2429 | 279.4094 | 1049.0388 | 0 | 0.002 | 5231010 | 75601.1688
Annual Sum or Average | 2549220 | 4069.259 | 16507.9345 | 0 | 0.0312 | 82325700 | 1064730
Minimum of Months | 160597.6984 | 249.4675 | 975.2122 | 0 | 0.0019 | 4863160 | 66360.4522
Maximum of Months | 299666.3313 | 489.6895 | 2047.1273 | 0 | 0.0038 | 10209500 | 126339.8898
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 702717000000 | 557249.475 | 18-JAN-14:00 | 270589.05 | 145652.643 | 77819.61 | 0 | 57056.902 | 0 | 1216.144 | 0 | 0 | 0 | 0 | 0 | 4915.126 | 0 | 0
February | 638164000000 | 612069.816 | 08-FEB-15:00 | 270589.05 | 137835.548 | 80489.404 | 0 | 116638.713 | 0 | 1560.216 | 0 | 0 | 0 | 0 | 0 | 4956.885 | 0 | 0
March | 757590000000 | 720535.659 | 31-MAR-15:00 | 270589.05 | 133019.064 | 81201.451 | 0 | 228906.092 | 0 | 1940.454 | 0 | 0 | 0 | 0 | 0 | 4879.548 | 0 | 0
April | 800598000000 | 1021875.988 | 21-APR-15:09 | 270589.05 | 133019.064 | 106172.912 | 0 | 499324.031 | 0 | 7523.655 | 0 | 0 | 0 | 0 | 0 | 5247.276 | 0 | 0
May | 1011410000000 | 1178787.141 | 31-MAY-15:00 | 270589.05 | 133019.064 | 118050.84 | 0 | 643443.565 | 0 | 8404.483 | 0 | 0 | 0 | 0 | 0 | 5280.139 | 0 | 0
June | 1339740000000 | 1425749.353 | 27-JUN-15:00 | 270589.05 | 133019.064 | 129642.004 | 0 | 877397.819 | 0 | 9784.76 | 0 | 0 | 0 | 0 | 0 | 5316.656 | 0 | 0
July | 1064820000000 | 1179737.38 | 24-JUL-15:00 | 150327.25 | 73183.824 | 116489.519 | 0 | 826184.887 | 0 | 8525.698 | 0 | 0 | 0 | 0 | 0 | 5026.202 | 0 | 0
August | 1101880000000 | 1128898.301 | 04-AUG-14:00 | 150327.25 | 78000.308 | 114631.901 | 0 | 771832.504 | 0 | 8830.887 | 0 | 0 | 0 | 0 | 0 | 5275.452 | 0 | 0
September | 1112000000000 | 1181697.483 | 20-SEP-15:00 | 270589.05 | 133019.064 | 118386.08 | 0 | 646042.275 | 0 | 8383.715 | 0 | 0 | 0 | 0 | 0 | 5277.3 | 0 | 0
October | 883210000000 | 1021549.295 | 03-OCT-15:09 | 270589.05 | 133019.064 | 105852.754 | 0 | 499264.957 | 0 | 7588.089 | 0 | 0 | 0 | 0 | 0 | 5235.381 | 0 | 0
November | 704562000000 | 643738.603 | 10-NOV-12:00 | 270589.05 | 151653.867 | 87164.037 | 0 | 127289.572 | 0 | 2037.446 | 0 | 0 | 0 | 0 | 0 | 5004.63 | 0 | 0
December | 686434000000 | 613704.256 | 05-DEC-14:30 | 270589.05 | 145652.643 | 80120.457 | 0 | 110746.906 | 0 | 1579.722 | 0 | 0 | 0 | 0 | 0 | 5015.478 | 0 | 0
Annual Sum or Average | 10803100000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 638164000000 | 557249.475 |  | 150327.25 | 73183.824 | 77819.61 | 0 | 57056.902 | 0 | 1216.144 | 0 | 0 | 0 | 0 | 0 | 4879.548 | 0 | 0
Maximum of Months | 1339740000000 | 1425749.353 |  | 270589.05 | 151653.867 | 129642.004 | 0 | 877397.819 | 0 | 9784.76 | 0 | 0 | 0 | 0 | 0 | 5316.656 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 310390.09 | 22543.21 | 0 | 332933.3
Cost per Total Building Area ($/m2) | 15.84 | 1.15 | 0 | 16.99
Cost per Net Conditioned Building Area ($/m2) | 15.84 | 1.15 | 0 | 16.99

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12380.82 | 631.93 | 631.93
Net Site Energy | 12380.82 | 631.93 | 631.93
Total Source Energy | 29858.84 | 1524.03 | 1524.03
Net Source Energy | 29858.84 | 1524.03 | 1524.03
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3522.21 | 0 | 0 | 0 | 0
Cooling | 344.64 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1064.34 | 0 | 0 | 0 | 0 | 0
Pumps | 13.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 347.96 | 0 | 0 | 0 | 2677.93
Refrigeration | 137.37 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8157.26 | 4223.56 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 753.18 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 1335.99 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1092123.41 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 1058242.46 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 364272.8 | 277260.94 | 87011.86 | 0.76 | 2.95
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 89815.9 | 68543.99 | 21271.91 | 0.76 | 3.2
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 147909.57 | 112135.6 | 35773.97 | 0.76 | 3.16
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18835.7 | 14018.79 | 4816.91 | 0.74 | 3.06
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87214.12 | 64910.61 | 22303.51 | 0.74 | 3.13
VAV_OTHER_COOLC | Coil:Cooling:Water | 413832.45 | 289926.34 | 123906.1 | 0.7 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 345581.51 | 239904.12 | 105677.39 | 0.69 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 346813.21 | 240770.75 | 106042.46 | 0.69 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 348029.79 | 241635.81 | 106393.98 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6439.78 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7899.96 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8822.68 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12200.37 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8761.43 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12172.87 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8763.01 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12178.98 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6692.63 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9865.93 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6673.03 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9864.78 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6733.46 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9887.27 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7859.07 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14541.69 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6543.7 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14397.71 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6561.22 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14399.76 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 48160.06 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5484.62 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10702.35 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16719.47 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 43400.41 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10900.45 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8891.06 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28247.02 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 45066.1 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30671.14 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 44953.64 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30699.08 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 45023.01 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18039.42 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30212.78 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17959.95 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30210.92 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18267.58 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30366.96 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24447.1 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38410.47 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 879468.07 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 193328.17 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 352855.23 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 43151.69 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 199803.42 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 67060.47 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 65466.63 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 65705.16 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 65947.19 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.9 | 9350.15 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.95 | 14915.01 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.97 | 1104.49 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.05 | 30391.51 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.8 | 25076.51 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.85 | 25167.88 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.91 | 25260.58 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10007.8 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5827.13 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 102556.207 | 89.9447 | 566.4533 | 0 | 0.0003 | 3416590 | 37223.1026
February | 76725.1238 | 66.7816 | 514.7618 | 0 | 0.0003 | 3105320 | 28125.2122
March | 92398.2284 | 80.5732 | 593.1411 | 0 | 0.0003 | 3578030 | 33788.8325
April | 76736.8765 | 66.5989 | 549.3603 | 0 | 0.0003 | 3314200 | 28234.8385
May | 77080.0434 | 66.6133 | 602.543 | 0 | 0.0003 | 3635260 | 28515.8676
June | 74730.6072 | 64.4971 | 599.528 | 0 | 0.0003 | 3617130 | 27693.5251
July | 51514.6744 | 44.4658 | 412.3001 | 0 | 0.0002 | 2487530 | 19087.2269
August | 55417.5387 | 47.8446 | 441.7525 | 0 | 0.0002 | 2665220 | 20527.8728
September | 71247.1238 | 61.3256 | 601.1134 | 0 | 0.0003 | 3626810 | 26492.7226
October | 75499.3771 | 65.1907 | 600.3097 | 0 | 0.0003 | 3621830 | 27961.9824
November | 78916.208 | 68.5021 | 562.8662 | 0 | 0.0003 | 3395670 | 29030.3149
December | 94214.9673 | 82.4608 | 550.514 | 0 | 0.0003 | 3320620 | 34287.5553
Annual Sum or Average | 927036.9755 | 804.7982 | 6594.6435 | 0 | 0.0034 | 39784200 | 340969.0534
Minimum of Months | 51514.6744 | 44.4658 | 412.3001 | 0 | 0.0002 | 2487530 | 19087.2269
Maximum of Months | 102556.207 | 89.9447 | 602.543 | 0 | 0.0003 | 3635260 | 37223.1026
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 700530000000 | 523605.689 | 27-JAN-14:00 | 270589.05 | 145652.643 | 79732.73 | 0 | 22204.062 | 0 | 762.981 | 0 | 0 | 0 | 0 | 0 | 4664.223 | 0 | 0
February | 636708000000 | 635276.587 | 15-FEB-16:10 | 270589.05 | 133019.064 | 80074.173 | 0 | 144709.137 | 0 | 2041.635 | 0 | 0 | 0 | 0 | 0 | 4843.529 | 0 | 0
March | 733630000000 | 550112.478 | 01-MAR-12:00 | 270589.05 | 151653.867 | 79311.375 | 0 | 42235.655 | 0 | 1424.985 | 0 | 0 | 0 | 0 | 0 | 4897.546 | 0 | 0
April | 679535000000 | 660614.942 | 13-APR-14:00 | 270589.05 | 137835.548 | 86776.804 | 0 | 158423.615 | 0 | 1972.105 | 0 | 0 | 0 | 0 | 0 | 5017.821 | 0 | 0
May | 745365000000 | 727801.591 | 17-MAY-13:00 | 270589.05 | 145652.643 | 83529.951 | 0 | 219720.391 | 0 | 3051.847 | 0 | 0 | 0 | 0 | 0 | 5257.708 | 0 | 0
June | 741648000000 | 748460.305 | 15-JUN-12:00 | 270589.05 | 145652.643 | 83836.374 | 0 | 240073.823 | 0 | 3027.197 | 0 | 0 | 0 | 0 | 0 | 5281.219 | 0 | 0
July | 510037000000 | 607814.046 | 03-JUL-12:00 | 150327.25 | 84617.158 | 78497.849 | 0 | 286817.441 | 0 | 2465.686 | 0 | 0 | 0 | 0 | 0 | 5088.661 | 0 | 0
August | 546469000000 | 565967.129 | 15-AUG-11:00 | 150327.25 | 88818.015 | 76534.359 | 0 | 243227.804 | 0 | 2071.94 | 0 | 0 | 0 | 0 | 0 | 4987.761 | 0 | 0
September | 743633000000 | 1042519.052 | 28-SEP-14:00 | 270589.05 | 137835.548 | 104271.545 | 0 | 517072.365 | 0 | 7232.367 | 0 | 0 | 0 | 0 | 0 | 5518.178 | 0 | 0
October | 742611000000 | 713336.702 | 31-OCT-12:00 | 270589.05 | 145652.643 | 86504.554 | 0 | 202368.567 | 0 | 3020.572 | 0 | 0 | 0 | 0 | 0 | 5201.315 | 0 | 0
November | 696240000000 | 552206.69 | 14-NOV-12:00 | 270589.05 | 151653.867 | 79793.122 | 0 | 43346.306 | 0 | 1968.085 | 0 | 0 | 0 | 0 | 0 | 4856.259 | 0 | 0
December | 680852000000 | 526118.635 | 07-DEC-14:00 | 270589.05 | 145652.643 | 78977.455 | 0 | 24911.177 | 0 | 1232.436 | 0 | 0 | 0 | 0 | 0 | 4755.873 | 0 | 0
Annual Sum or Average | 8157260000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 510037000000 | 523605.689 |  | 150327.25 | 84617.158 | 76534.359 | 0 | 22204.062 | 0 | 762.981 | 0 | 0 | 0 | 0 | 0 | 4664.223 | 0 | 0
Maximum of Months | 745365000000 | 1042519.052 |  | 270589.05 | 151653.867 | 104271.545 | 0 | 517072.365 | 0 | 7232.367 | 0 | 0 | 0 | 0 | 0 | 5518.178 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 346500.91 | 36198.3 | 0 | 382699.2
Cost per Total Building Area ($/m2) | 17.69 | 1.85 | 0 | 19.53
Cost per Net Conditioned Building Area ($/m2) | 17.69 | 1.85 | 0 | 19.53

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16972.87 | 866.32 | 866.32
Net Site Energy | 16972.87 | 866.32 | 866.32
Total Source Energy | 41983.32 | 2142.88 | 2142.88
Net Source Energy | 41983.32 | 2142.88 | 2142.88
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6813.98 | 0 | 0 | 0 | 0
Cooling | 1591.19 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1085.9 | 0 | 0 | 0 | 0 | 0
Pumps | 26.74 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 365.49 | 0 | 0 | 0 | 2677.93
Refrigeration | 139.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9440 | 7532.87 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.355 | 0.274 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.355 | 0.274 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.355 | 0.274 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.354 | 0.355 | 0.274 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.355 | 0.274 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.354 | 0.355 | 0.274 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.355 | 0.274 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.355 | 0.274 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.355 | 0.274 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.355 | 0.274 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.354 | 0.355 | 0.274 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.355 | 0.274 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.355 | 0.274 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.355 | 0.274 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.354 | 0.355 | 0.274 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.355 | 0.274 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.355 | 0.274 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.355 | 0.274 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.355 | 0.274 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.355 | 0.274 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.355 | 0.274 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.355 | 0.274 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.355 | 0.274 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.355 | 0.274 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.354 | 0.355 | 0.274 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.355 | 0.274 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.354 | 0.355 | 0.274 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 753.18 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 1335.99 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1364552.97 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 897979.21 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 93065.5 | 62920.02 | 30145.48 | 0.68 | 2.9
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13720.99 | 9276.53 | 4444.46 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 324082.59 | 214612.84 | 109469.75 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 275708.6 | 176739.86 | 98968.75 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 276312.33 | 177140.1 | 99172.23 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 294043.5 | 188927.61 | 105115.89 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7361.5 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8976.14 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5678.15 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8003.96 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5617.95 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7975.54 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5621.63 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7994.7 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5402.68 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7784.12 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5393.74 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7786.87 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5456.99 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7825.54 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5058.59 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9930.61 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4319.36 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9872.39 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4371.81 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10017.56 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31479.57 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2966.75 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6556.55 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17896.81 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36720.28 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10948.75 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6977.82 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11897.92 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21475.97 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13125.03 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21394.94 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13192.67 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24903.52 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11646.56 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20108.64 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11644.03 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20124.87 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12009.19 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23794.85 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13813.09 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22402.43 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1212770.34 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 230018.08 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 485108.14 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 33912.42 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 275525.26 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 104213.62 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 68813.47 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 68985.54 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 74088.48 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.75 | 7148.57 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 640.9 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.27 | 22491.38 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.77 | 16443.99 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.79 | 16485.11 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.44 | 17704.53 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12504.24 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4944.66 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 215540.032 | 327.3573 | 728.1609 | 0 | 0.0031 | 45257.7953 | 86642.1304
February | 180621.5487 | 282.0178 | 652.6777 | 0 | 0.0028 | 40570.2733 | 73309.2099
March | 174405.1086 | 293.5467 | 747.4654 | 0 | 0.0031 | 46472.6443 | 72727.8059
April | 135299.5658 | 247.3404 | 688.1639 | 0 | 0.0028 | 42793.7405 | 58213.9952
May | 146797.3187 | 282.9452 | 827.1801 | 0 | 0.0034 | 51443.5908 | 64494.696
June | 188311.1194 | 372.7823 | 1115.3318 | 0 | 0.0045 | 69367.2653 | 83631.598
July | 140118.4817 | 278.263 | 834.773 | 0 | 0.0034 | 51918.3755 | 62309.3419
August | 152373.284 | 302.4518 | 906.9643 | 0 | 0.0037 | 56408.2376 | 67745.3847
September | 148861.0751 | 293.0223 | 872.4866 | 0 | 0.0035 | 54263.1862 | 65959.0979
October | 147975.8427 | 276.3865 | 785.064 | 0 | 0.0032 | 48821.5582 | 64205.0616
November | 155221.487 | 269.6103 | 711.3648 | 0 | 0.0029 | 44231.5848 | 65491.8296
December | 193801.1507 | 303.3643 | 704.5438 | 0 | 0.003 | 43794.6302 | 78728.6783
Annual Sum or Average | 1979330 | 3529.0878 | 9574.1763 | 0 | 0.0394 | 595342.8821 | 843458.8294
Minimum of Months | 135299.5658 | 247.3404 | 652.6777 | 0 | 0.0028 | 40570.2733 | 58213.9952
Maximum of Months | 215540.032 | 372.7823 | 1115.3318 | 0 | 0.0045 | 69367.2653 | 86642.1304
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 717626000000 | 515722.368 | 09-JAN-11:50 | 270589.05 | 151653.867 | 71012.425 | 0 | 15216.964 | 0 | 700.661 | 0 | 0 | 0 | 0 | 0 | 6549.401 | 0 | 0
February | 643299000000 | 510689.321 | 15-FEB-12:00 | 270589.05 | 151653.867 | 71398.638 | 0 | 11949.254 | 0 | 462.482 | 0 | 0 | 0 | 0 | 0 | 4636.03 | 0 | 0
March | 736889000000 | 737283.113 | 09-MAR-15:00 | 270589.05 | 137835.548 | 78523.487 | 0 | 242586.808 | 0 | 2507.446 | 0 | 0 | 0 | 0 | 0 | 5240.776 | 0 | 0
April | 678555000000 | 748603.282 | 04-APR-15:00 | 270589.05 | 133019.064 | 79470.028 | 0 | 258216.074 | 0 | 2347.889 | 0 | 0 | 0 | 0 | 0 | 4961.177 | 0 | 0
May | 815710000000 | 1050690.049 | 31-MAY-15:00 | 270589.05 | 133019.064 | 86745.695 | 0 | 549447.84 | 0 | 5580.696 | 0 | 0 | 0 | 0 | 0 | 5307.704 | 0 | 0
June | 1099920000000 | 1357293.348 | 30-JUN-14:00 | 270589.05 | 137835.548 | 108422.065 | 0 | 824974.592 | 0 | 9916.459 | 0 | 0 | 0 | 0 | 0 | 5555.634 | 0 | 0
July | 823239000000 | 1151143.651 | 25-JUL-12:00 | 150327.25 | 84617.158 | 88110.639 | 0 | 815447.901 | 0 | 7322.64 | 0 | 0 | 0 | 0 | 0 | 5318.063 | 0 | 0
August | 894432000000 | 1153800.943 | 09-AUG-14:00 | 150327.25 | 78000.308 | 88690.195 | 0 | 823021.008 | 0 | 8496.585 | 0 | 0 | 0 | 0 | 0 | 5265.597 | 0 | 0
September | 860419000000 | 1058369.052 | 08-SEP-14:00 | 270589.05 | 137835.548 | 105665.902 | 0 | 533141.195 | 0 | 5633.758 | 0 | 0 | 0 | 0 | 0 | 5503.6 | 0 | 0
October | 774134000000 | 913566.652 | 03-OCT-11:00 | 270589.05 | 151653.867 | 90914.325 | 0 | 390417.464 | 0 | 4696.585 | 0 | 0 | 0 | 0 | 0 | 5295.361 | 0 | 0
November | 701354000000 | 766805.546 | 03-NOV-13:00 | 270589.05 | 145652.643 | 87900.308 | 0 | 253876.294 | 0 | 3582.031 | 0 | 0 | 0 | 0 | 0 | 5205.22 | 0 | 0
December | 694425000000 | 500072.253 | 06-DEC-11:39 | 270589.05 | 151653.867 | 71433.124 | 0 | 0 | 0 | 221.907 | 0 | 0 | 0 | 0 | 0 | 6174.305 | 0 | 0
Annual Sum or Average | 9440000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 643299000000 | 500072.253 |  | 150327.25 | 78000.308 | 71012.425 | 0 | 0 | 0 | 221.907 | 0 | 0 | 0 | 0 | 0 | 4636.03 | 0 | 0
Maximum of Months | 1099920000000 | 1357293.348 |  | 270589.05 | 151653.867 | 108422.065 | 0 | 824974.592 | 0 | 9916.459 | 0 | 0 | 0 | 0 | 0 | 6549.401 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 218682 | 73034.61 | 0 | 291716.6
Cost per Total Building Area ($/m2) | 11.16 | 3.73 | 0 | 14.89
Cost per Net Conditioned Building Area ($/m2) | 11.16 | 3.73 | 0 | 14.89

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14346.11 | 732.24 | 732.24
Net Site Energy | 14346.11 | 732.24 | 732.24
Total Source Energy | 35989.03 | 1836.92 | 1836.92
Net Source Energy | 35989.03 | 1836.92 | 1836.92
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4506.68 | 0 | 0 | 0 | 0
Cooling | 1222.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1145.65 | 0 | 0 | 0 | 0 | 0
Pumps | 25.46 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 356.17 | 0 | 0 | 0 | 2677.93
Refrigeration | 138.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9129.86 | 5216.25 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.362 | 0.225 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.362 | 0.225 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.362 | 0.225 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.362 | 0.225 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.362 | 0.225 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.362 | 0.225 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.362 | 0.225 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.362 | 0.225 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.362 | 0.225 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.362 | 0.225 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 4.092 | 0.362 | 0.225 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.362 | 0.225 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.362 | 0.225 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.362 | 0.225 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 4.092 | 0.362 | 0.225 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.362 | 0.225 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.362 | 0.225 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.362 | 0.225 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.362 | 0.225 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.362 | 0.225 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.362 | 0.225 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.362 | 0.225 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.362 | 0.225 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.362 | 0.225 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.362 | 0.225 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.362 | 0.225 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.362 | 0.225 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 753.18 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 1335.99 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 739710.51 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 745690.26 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 431701 | 306322.49 | 125378.51 | 0.71 | 2.81
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 84838.99 | 59374.4 | 25464.59 | 0.7 | 2.98
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 153905.05 | 114436.82 | 39468.23 | 0.74 | 3.11
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12346.44 | 8600.56 | 3745.88 | 0.7 | 2.98
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 102865.51 | 71656.36 | 31209.15 | 0.7 | 2.97
VAV_OTHER_COOLC | Coil:Cooling:Water | 223586.15 | 139917.93 | 83668.22 | 0.63 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 198031.61 | 122043.72 | 75987.89 | 0.62 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 196988.49 | 121325.56 | 75662.93 | 0.62 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 212352.49 | 131025.78 | 81326.71 | 0.62 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6659.86 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8200.36 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4960.89 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7390.42 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4889.75 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7359.26 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4894.55 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7381.04 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4704.05 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7197.36 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4693.74 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7200.59 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4772.79 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7245.19 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3955.79 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8949.72 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3258.69 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8899.81 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3305.25 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9041.78 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27837.83 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2712.52 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6048.58 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16339.78 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33093.07 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9707.87 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5977.45 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18131.51 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9837.95 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18109.35 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9910.37 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21638.94 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17167.56 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17186.92 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9635.89 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20880.78 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10715.8 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19306.21 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 963612.67 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 182762 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 385445.07 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 26275.88 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 218919.96 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 83280.03 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 55690.67 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 55291.72 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 59926.86 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.75 | 7148.57 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 624.98 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.58 | 23009.66 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.08 | 17037.03 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.02 | 16914.98 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.77 | 16812.08 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6778.42 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4106.09 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 242043.1928 | 377.2778 | 853.8999 | 0 | 0.0034 | 887624.8571 | 99227.7947
February | 207834.1503 | 330.442 | 768.3226 | 0 | 0.0031 | 798720.9482 | 85839.7446
March | 231852.4346 | 375.4212 | 893.8742 | 0 | 0.0036 | 929293.2012 | 96425.9899
April | 201861.1701 | 340.178 | 850.3387 | 0 | 0.0033 | 884132.7357 | 85259.3047
May | 242034.5875 | 419.5405 | 1082.689 | 0 | 0.0042 | 1125800 | 103371.1
June | 268741.9864 | 468.7409 | 1217.8876 | 0 | 0.0047 | 1266400 | 115062.6751
July | 198045.6993 | 346.0506 | 900.8532 | 0 | 0.0035 | 936739.4573 | 84854.5212
August | 194361.8086 | 339.404 | 882.9614 | 0 | 0.0034 | 918133.5296 | 83255.5567
September | 230197.6857 | 400.9212 | 1040.0161 | 0 | 0.0041 | 1081440 | 98501.8975
October | 214154.4614 | 362.3815 | 910.1708 | 0 | 0.0036 | 946352.913 | 90597.402
November | 216639.0867 | 351.9384 | 841.4515 | 0 | 0.0033 | 874801.9396 | 90211.7611
December | 237936.5176 | 369.7768 | 833.459 | 0 | 0.0034 | 866367.5539 | 97436.34
Annual Sum or Average | 2685700 | 4482.0728 | 11075.9241 | 0 | 0.0437 | 11515800 | 1130040
Minimum of Months | 194361.8086 | 330.442 | 768.3226 | 0 | 0.0031 | 798720.9482 | 83255.5567
Maximum of Months | 268741.9864 | 468.7409 | 1217.8876 | 0 | 0.0047 | 1266400 | 115062.6751
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 703720000000 | 527319.615 | 25-JAN-14:00 | 270589.05 | 145652.643 | 80764.505 | 0 | 24844.268 | 0 | 793.942 | 0 | 0 | 0 | 0 | 0 | 4675.207 | 0 | 0
February | 633236000000 | 613855.238 | 14-FEB-16:10 | 270589.05 | 133019.064 | 83821.848 | 0 | 120204.044 | 0 | 1495.781 | 0 | 0 | 0 | 0 | 0 | 4725.45 | 0 | 0
March | 736755000000 | 626348.901 | 02-MAR-15:09 | 270589.05 | 137835.548 | 91394.409 | 0 | 119518.082 | 0 | 2026.746 | 0 | 0 | 0 | 0 | 0 | 4985.067 | 0 | 0
April | 700951000000 | 806550.874 | 21-APR-15:00 | 270589.05 | 133019.064 | 103763.176 | 0 | 290163.284 | 0 | 4055.713 | 0 | 0 | 0 | 0 | 0 | 4960.586 | 0 | 0
May | 892546000000 | 942102.416 | 31-MAY-15:00 | 270589.05 | 133019.064 | 109580.864 | 0 | 417354.141 | 0 | 6403.862 | 0 | 0 | 0 | 0 | 0 | 5155.435 | 0 | 0
June | 1004020000000 | 1063994.468 | 29-JUN-13:00 | 270589.05 | 145652.643 | 116144.223 | 0 | 519163.327 | 0 | 6893.091 | 0 | 0 | 0 | 0 | 0 | 5552.135 | 0 | 0
July | 742658000000 | 872531.088 | 31-JUL-14:00 | 150327.25 | 78000.308 | 105952.072 | 0 | 526329.796 | 0 | 6763.159 | 0 | 0 | 0 | 0 | 0 | 5158.504 | 0 | 0
August | 727907000000 | 845801.644 | 01-AUG-13:00 | 150327.25 | 84617.158 | 102574.641 | 0 | 496101.62 | 0 | 6886.575 | 0 | 0 | 0 | 0 | 0 | 5294.4 | 0 | 0
September | 857377000000 | 899760.229 | 20-SEP-15:09 | 270589.05 | 133019.064 | 108951.661 | 0 | 375993.529 | 0 | 6056.144 | 0 | 0 | 0 | 0 | 0 | 5150.779 | 0 | 0
October | 750280000000 | 790207.716 | 11-OCT-15:00 | 270589.05 | 133019.064 | 97900.355 | 0 | 278683.572 | 0 | 5051.981 | 0 | 0 | 0 | 0 | 0 | 4963.694 | 0 | 0
November | 693554000000 | 587894.745 | 08-NOV-16:10 | 270589.05 | 133019.064 | 84407.473 | 0 | 93897.535 | 0 | 1328.54 | 0 | 0 | 0 | 0 | 0 | 4653.083 | 0 | 0
December | 686867000000 | 519129.008 | 08-DEC-14:00 | 270589.05 | 145652.643 | 79742.241 | 0 | 17860.856 | 0 | 650.649 | 0 | 0 | 0 | 0 | 0 | 4633.569 | 0 | 0
Annual Sum or Average | 9129860000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 633236000000 | 519129.008 |  | 150327.25 | 78000.308 | 79742.241 | 0 | 17860.856 | 0 | 650.649 | 0 | 0 | 0 | 0 | 0 | 4633.569 | 0 | 0
Maximum of Months | 1004020000000 | 1063994.468 |  | 270589.05 | 145652.643 | 116144.223 | 0 | 526329.796 | 0 | 6893.091 | 0 | 0 | 0 | 0 | 0 | 5552.135 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 93844.1 | 36073.03 | 0 | 129917.12
Cost per Total Building Area ($/m2) | 4.79 | 1.84 | 0 | 6.63
Cost per Net Conditioned Building Area ($/m2) | 4.79 | 1.84 | 0 | 6.63

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15388.02 | 785.42 | 785.42
Net Site Energy | 15388.02 | 785.42 | 785.42
Total Source Energy | 22025.4 | 1124.2 | 1124.2
Net Source Energy | 22025.4 | 1124.2 | 1124.2
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6618.8 | 0 | 0 | 0 | 0
Cooling | 270.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1019.5 | 0 | 0 | 0 | 0 | 0
Pumps | 11.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 382.46 | 0 | 0 | 0 | 2677.93
Refrigeration | 134.55 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8033.37 | 7354.65 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 4.092 | 0.392 | 0.253 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 4.092 | 0.392 | 0.253 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 4.092 | 0.392 | 0.253 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 4.092 | 0.392 | 0.253 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 4.092 | 0.392 | 0.253 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 4.092 | 0.392 | 0.253 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 4.092 | 0.392 | 0.253 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 4.092 | 0.392 | 0.253 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 753.18 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 1335.99 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 805686.19 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 841523.76 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 419688.46 | 301145.09 | 118543.37 | 0.72 | 2.83
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 84941.22 | 59418.46 | 25522.76 | 0.7 | 2.97
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 157787.13 | 116110 | 41677.13 | 0.74 | 3.08
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9903.2 | 6988.59 | 2914.61 | 0.71 | 3
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91224.51 | 66639.09 | 24585.42 | 0.73 | 3.08
VAV_OTHER_COOLC | Coil:Cooling:Water | 301283.45 | 207170.2 | 94113.26 | 0.69 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 228550.88 | 155533.07 | 73017.81 | 0.68 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 228419.56 | 155430.83 | 72988.73 | 0.68 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 242555.11 | 165107.65 | 77447.46 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6458.8 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7926.54 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6126.75 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8789.89 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6052 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8756.31 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6055.76 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8776.14 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4911.07 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7554.29 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4899.11 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7555.77 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4973.05 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7597.91 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4270.08 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9647.89 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3523.02 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9550.9 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3564.99 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9684.41 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28056.88 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4106.3 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7817.45 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14582.13 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33882.46 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9367.74 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5839.41 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17548.47 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28783.42 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18615.93 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28571.85 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18684.69 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32087.45 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17390.04 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17401.08 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21058.39 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17021.27 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26707.55 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1048815.86 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 198921.93 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 419526.35 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 23724.61 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 238276.99 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 82556.93 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 60917.5 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 60867.37 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 64816.67 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.75 | 7148.57 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 518.45 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.06 | 22123.93 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.64 | 16576.06 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.63 | 16562.42 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.25 | 17637.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7383 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4633.79 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 101248.912 | 115.3973 | 150.4147 | 0 | 0.0007 | 1983650 | 37558.3723
February | 76726.0395 | 90.6946 | 134.7151 | 0 | 0.0006 | 1777550 | 28809.346
March | 85904.9854 | 102.4598 | 156.6746 | 0 | 0.0007 | 2067530 | 32353.9015
April | 63725.012 | 80.0327 | 141.9353 | 0 | 0.0006 | 1873990 | 24431.6996
May | 52516.3265 | 72.2208 | 156.9719 | 0 | 0.0006 | 2073740 | 20805.3748
June | 45833.1576 | 66.6361 | 160.0202 | 0 | 0.0006 | 2114540 | 18543.9227
July | 29517.7206 | 44.3272 | 112.0718 | 0 | 0.0004 | 1481110 | 12093.9739
August | 31088.179 | 46.7048 | 118.1569 | 0 | 0.0005 | 1561530 | 12739.4747
September | 44873.1614 | 64.6263 | 152.7477 | 0 | 0.0006 | 2018360 | 18089.7439
October | 56818.8023 | 74.9851 | 149.7042 | 0 | 0.0006 | 1977270 | 22172.2546
November | 82970.2857 | 98.2602 | 146.8568 | 0 | 0.0007 | 1937810 | 31173.7168
December | 98038.2439 | 111.8665 | 146.4652 | 0 | 0.0007 | 1931600 | 36381.1298
Annual Sum or Average | 769260.826 | 968.2114 | 1726.7345 | 0 | 0.0075 | 22798700 | 295152.9106
Minimum of Months | 29517.7206 | 44.3272 | 112.0718 | 0 | 0.0004 | 1481110 | 12093.9739
Maximum of Months | 101248.912 | 115.3973 | 160.0202 | 0 | 0.0007 | 2114540 | 37558.3723
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 698960000000 | 499668.065 | 09-JAN-11:39 | 270589.05 | 151653.867 | 70867.43 | 0 | 0 | 0 | 422.273 | 0 | 0 | 0 | 0 | 0 | 6135.445 | 0 | 0
February | 626340000000 | 518407.978 | 21-FEB-12:00 | 270589.05 | 151653.867 | 71387.698 | 0 | 19471.571 | 0 | 592.186 | 0 | 0 | 0 | 0 | 0 | 4713.605 | 0 | 0
March | 728518000000 | 594053.478 | 29-MAR-15:00 | 270589.05 | 133019.064 | 77422.274 | 0 | 107129.56 | 0 | 1215.51 | 0 | 0 | 0 | 0 | 0 | 4678.02 | 0 | 0
April | 660320000000 | 539229.958 | 14-APR-13:00 | 270589.05 | 145652.643 | 77343.846 | 0 | 39796.54 | 0 | 1022.721 | 0 | 0 | 0 | 0 | 0 | 4825.157 | 0 | 0
May | 730705000000 | 734414.555 | 05-MAY-15:00 | 270589.05 | 133019.064 | 80668.373 | 0 | 242661.129 | 0 | 2519.165 | 0 | 0 | 0 | 0 | 0 | 4957.774 | 0 | 0
June | 745080000000 | 787558.83 | 28-JUN-14:00 | 270589.05 | 137835.548 | 96897.234 | 0 | 272906.624 | 0 | 4105.892 | 0 | 0 | 0 | 0 | 0 | 5224.483 | 0 | 0
July | 521886000000 | 632703.849 | 24-JUL-14:00 | 150327.25 | 78000.308 | 79607.113 | 0 | 316897.91 | 0 | 2804.309 | 0 | 0 | 0 | 0 | 0 | 5066.958 | 0 | 0
August | 550224000000 | 572386.471 | 07-AUG-14:00 | 150327.25 | 78000.308 | 79479.431 | 0 | 257064.87 | 0 | 2535.337 | 0 | 0 | 0 | 0 | 0 | 4979.275 | 0 | 0
September | 711191000000 | 866783.583 | 13-SEP-14:00 | 270589.05 | 137835.548 | 104388.065 | 0 | 343358.966 | 0 | 5324.178 | 0 | 0 | 0 | 0 | 0 | 5287.777 | 0 | 0
October | 696713000000 | 619526.895 | 17-OCT-15:09 | 270589.05 | 133019.064 | 79060.649 | 0 | 130664.994 | 0 | 1399.236 | 0 | 0 | 0 | 0 | 0 | 4793.902 | 0 | 0
November | 682808000000 | 516433.359 | 03-NOV-10:39 | 270589.05 | 151653.867 | 71171.419 | 0 | 15473.795 | 0 | 653.219 | 0 | 0 | 0 | 0 | 0 | 6892.009 | 0 | 0
December | 680620000000 | 499683.822 | 13-DEC-11:09 | 270589.05 | 151653.867 | 70867.43 | 0 | 0 | 0 | 579.66 | 0 | 0 | 0 | 0 | 0 | 5993.816 | 0 | 0
Annual Sum or Average | 8033370000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 521886000000 | 499668.065 |  | 150327.25 | 78000.308 | 70867.43 | 0 | 0 | 0 | 422.273 | 0 | 0 | 0 | 0 | 0 | 4678.02 | 0 | 0
Maximum of Months | 745080000000 | 866783.583 |  | 270589.05 | 151653.867 | 104388.065 | 0 | 343358.966 | 0 | 5324.178 | 0 | 0 | 0 | 0 | 0 | 6892.009 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 161340.53 | 61854.01 | 0 | 223194.53
Cost per Total Building Area ($/m2) | 8.24 | 3.16 | 0 | 11.39
Cost per Net Conditioned Building Area ($/m2) | 8.24 | 3.16 | 0 | 11.39

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19080.76 | 973.91 | 973.91
Net Site Energy | 19080.76 | 973.91 | 973.91
Total Source Energy | 42942.91 | 2191.86 | 2191.86
Net Source Energy | 42942.91 | 2191.86 | 2191.86
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9312.4 | 0 | 0 | 0 | 0
Cooling | 1144.32 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1107.65 | 0 | 0 | 0 | 0 | 0
Pumps | 23.31 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 406.52 | 0 | 0 | 0 | 2677.93
Refrigeration | 135.99 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9008.45 | 10072.31 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 753.18 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 1335.99 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1344220.52 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 1012315.66 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 93065.5 | 62920.02 | 30145.48 | 0.68 | 2.9
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13641.48 | 9222.77 | 4418.7 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 288570.92 | 190401.7 | 98169.22 | 0.66 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 269734.87 | 171874.62 | 97860.25 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 270114.08 | 172119.43 | 97994.65 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 287787.7 | 183819.31 | 103968.38 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8759.97 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10687.69 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5846.58 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7993.94 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5779.15 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7962.18 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5783.13 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7982.12 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5498.1 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7705.69 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5489.02 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7708.92 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5559.38 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7750.82 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4985.48 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9223.49 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4241.74 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9161.02 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4298.3 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9308.6 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29391.17 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3773.51 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7581.44 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23271.89 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34253.04 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10661 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6073.09 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11899.96 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20573.57 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13061.96 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20458.41 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13130.34 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23964.23 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18882 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11448.39 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18900.61 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11742.02 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22583.6 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.35 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21275.45 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1416766.07 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 268708.6 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 566706.43 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 39387.12 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 321870.37 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 122699.15 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 83190.92 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 83314.19 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 89622.94 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.75 | 7148.57 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 637.19 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.79 | 21668.57 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.67 | 16266.97 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.68 | 16291.08 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 9.34 | 17524.68 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 12317.92 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5574.24 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 362033.6041 | 551.4399 | 1337.2526 | 0 | 0.0043 | 307710.8955 | 146604.4143
February | 310854.9701 | 481.4298 | 1195.8341 | 0 | 0.0038 | 275184.8233 | 126639.2988
March | 330684.0969 | 529.125 | 1373.9371 | 0 | 0.0043 | 316201.1671 | 136341.4613
April | 256217.1612 | 440.4858 | 1247.4673 | 0 | 0.0038 | 287147.3095 | 108556.1901
May | 284650.1903 | 507.8696 | 1496.8163 | 0 | 0.0045 | 344570.5091 | 122371.9176
June | 358724.54 | 649.5549 | 1943.4181 | 0 | 0.0059 | 447392.1358 | 155127.1637
July | 259800.4595 | 471.4206 | 1413.4296 | 0 | 0.0043 | 325385.3557 | 112443.0883
August | 252834.2288 | 458.4364 | 1373.47 | 0 | 0.0041 | 316185.8129 | 109395.206
September | 283304.2758 | 510.8361 | 1521.9178 | 0 | 0.0046 | 350356.1788 | 122306.5298
October | 270644.1607 | 473.2429 | 1365.3934 | 0 | 0.0042 | 314303.6371 | 115429.2577
November | 299418.4561 | 488.1842 | 1298.5082 | 0 | 0.004 | 298857.3193 | 124319.4206
December | 333787.4449 | 519.4505 | 1299.067 | 0 | 0.0041 | 298945.3519 | 136221.2182
Annual Sum or Average | 3602950 | 6081.4758 | 16866.5114 | 0 | 0.0519 | 3882240 | 1515760
Minimum of Months | 252834.2288 | 440.4858 | 1195.8341 | 0 | 0.0038 | 275184.8233 | 108556.1901
Maximum of Months | 362033.6041 | 649.5549 | 1943.4181 | 0 | 0.0059 | 447392.1358 | 155127.1637
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 714020000000 | 502057.934 | 27-JAN-11:09 | 270589.05 | 151653.867 | 71057.694 | 0 | 0 | 0 | 2844.553 | 0 | 0 | 0 | 0 | 0 | 5912.769 | 0 | 0
February | 638546000000 | 500178.069 | 28-FEB-11:39 | 270589.05 | 151653.867 | 71384.295 | 0 | 0 | 0 | 133.242 | 0 | 0 | 0 | 0 | 0 | 6417.615 | 0 | 0
March | 733721000000 | 623084.279 | 31-MAR-15:09 | 270589.05 | 133019.064 | 74581.645 | 0 | 139001.654 | 0 | 1077.523 | 0 | 0 | 0 | 0 | 0 | 4815.343 | 0 | 0
April | 666304000000 | 630583.299 | 07-APR-14:39 | 270589.05 | 137835.548 | 83128.162 | 0 | 130926.617 | 0 | 3061.092 | 0 | 0 | 0 | 0 | 0 | 5042.83 | 0 | 0
May | 799550000000 | 1014793.554 | 30-MAY-15:00 | 270589.05 | 133019.064 | 88605.101 | 0 | 512081.629 | 0 | 5121.84 | 0 | 0 | 0 | 0 | 0 | 5376.87 | 0 | 0
June | 1038140000000 | 1340537.17 | 08-JUN-12:00 | 270589.05 | 145652.643 | 103470.341 | 0 | 805024.101 | 0 | 10276.156 | 0 | 0 | 0 | 0 | 0 | 5524.878 | 0 | 0
July | 755032000000 | 1029363.56 | 13-JUL-12:00 | 150327.25 | 84617.158 | 82740.001 | 0 | 700229.943 | 0 | 6173.234 | 0 | 0 | 0 | 0 | 0 | 5275.975 | 0 | 0
August | 733685000000 | 1042724.573 | 04-AUG-15:50 | 150327.25 | 73183.824 | 85755.314 | 0 | 720788.01 | 0 | 7482.03 | 0 | 0 | 0 | 0 | 0 | 5188.145 | 0 | 0
September | 812975000000 | 1013407.563 | 06-SEP-10:00 | 270589.05 | 151653.867 | 97499.635 | 0 | 482343.152 | 0 | 5914.81 | 0 | 0 | 0 | 0 | 0 | 5407.049 | 0 | 0
October | 729318000000 | 778524.859 | 31-OCT-11:00 | 270589.05 | 151653.867 | 86758.054 | 0 | 260544.898 | 0 | 3785.254 | 0 | 0 | 0 | 0 | 0 | 5193.735 | 0 | 0
November | 693476000000 | 772288.004 | 02-NOV-14:39 | 270589.05 | 137835.548 | 86990.201 | 0 | 267863.373 | 0 | 3822.964 | 0 | 0 | 0 | 0 | 0 | 5186.867 | 0 | 0
December | 693680000000 | 499917.776 | 14-DEC-11:39 | 270589.05 | 151653.867 | 71057.694 | 0 | 0 | 0 | 651.379 | 0 | 0 | 0 | 0 | 0 | 5965.786 | 0 | 0
Annual Sum or Average | 9008450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 638546000000 | 499917.776 |  | 150327.25 | 73183.824 | 71057.694 | 0 | 0 | 0 | 133.242 | 0 | 0 | 0 | 0 | 0 | 4815.343 | 0 | 0
Maximum of Months | 1038140000000 | 1340537.17 |  | 270589.05 | 151653.867 | 103470.341 | 0 | 805024.101 | 0 | 10276.156 | 0 | 0 | 0 | 0 | 0 | 6417.615 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 205317.81 | 84109.8 | 0 | 289427.6
Cost per Total Building Area ($/m2) | 10.48 | 4.29 | 0 | 14.77
Cost per Net Conditioned Building Area ($/m2) | 10.48 | 4.29 | 0 | 14.77

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15856.07 | 809.31 | 809.31
Net Site Energy | 15856.07 | 809.31 | 809.31
Total Source Energy | 36415.02 | 1858.67 | 1858.67
Net Source Energy | 36415.02 | 1858.67 | 1858.67
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6519.54 | 0 | 0 | 0 | 0
Cooling | 723.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1106.51 | 0 | 0 | 0 | 0 | 0
Pumps | 17.96 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 402.65 | 0 | 0 | 0 | 2677.93
Refrigeration | 135.26 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8580.5 | 7275.58 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.354 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.354 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.354 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.354 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.354 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.354 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.354 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.354 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 753.18 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 1335.99 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 687773.19 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 774576.52 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 349609.79 | 270941.18 | 78668.61 | 0.77 | 2.99
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 85701.17 | 59746 | 25955.17 | 0.7 | 2.97
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 148485.86 | 112101.15 | 36384.71 | 0.75 | 3.15
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11842.44 | 8215.74 | 3626.7 | 0.69 | 2.98
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 103980.49 | 72136.91 | 31843.57 | 0.69 | 2.96
VAV_OTHER_COOLC | Coil:Cooling:Water | 250908.75 | 154260.99 | 96647.76 | 0.61 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 176350.94 | 106711.66 | 69639.28 | 0.61 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 174600.81 | 105612.05 | 68988.76 | 0.6 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 190158.85 | 115263.65 | 74895.21 | 0.61 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7701.75 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9485.17 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4369.62 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6408.06 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4304.08 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6376.91 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4309.24 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6399.15 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4068.35 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6159.38 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4057.38 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6161.91 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4129.78 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6207.07 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3534.79 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7307.11 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3053.5 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7254.04 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3105.96 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7395.88 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23547.34 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3290.3 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6771.5 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20079.18 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29790.7 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9502.72 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4763.77 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9656.36 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15680.62 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15657.86 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19179.54 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14354.04 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14369.65 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9618.19 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18035.53 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9958.64 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.92 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1150276.54 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 218165.3 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 460110.62 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 29762.84 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 261327.5 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 91253.85 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 62332.13 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 61669.37 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 67448.02 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.75 | 7148.57 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 593.04 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.78 | 19957.3 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.05 | 15094.02 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.96 | 14933.52 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.71 | 16332.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6302.49 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4265.15 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 256755.3564 | 391.6166 | 859.2907 | 0 | 0.0035 | 893157.9617 | 104416.2547
February | 227042.2146 | 347.4795 | 766.2516 | 0 | 0.0031 | 796462.1144 | 92448.6661
March | 245056.4812 | 387.3518 | 893.6341 | 0 | 0.0036 | 928972.5558 | 100990.5579
April | 206428.2998 | 341.1134 | 832.983 | 0 | 0.0033 | 866040.7601 | 86525.109
May | 220659.9907 | 372.6255 | 933.6829 | 0 | 0.0037 | 970794.4656 | 93274.5756
June | 233546.5977 | 403.7918 | 1039.1143 | 0 | 0.0041 | 1080480 | 99644.3592
July | 171835.2289 | 299.9256 | 779.8608 | 0 | 0.003 | 810925.1051 | 73592.3513
August | 177770.0871 | 310.0308 | 805.4227 | 0 | 0.0031 | 837503.6244 | 76109.2076
September | 213109.8225 | 366.0014 | 934.8913 | 0 | 0.0037 | 972092.8934 | 90683.9352
October | 213575.3607 | 358.8695 | 894.0051 | 0 | 0.0035 | 929527.2911 | 90104.0522
November | 228378.5449 | 361.3318 | 834.6677 | 0 | 0.0033 | 867677.0485 | 94150.9562
December | 253583.1615 | 384.4899 | 836.2892 | 0 | 0.0034 | 869230.0316 | 102901.7476
Annual Sum or Average | 2647740 | 4324.6277 | 10410.0935 | 0 | 0.0413 | 10822900 | 1104840
Minimum of Months | 171835.2289 | 299.9256 | 766.2516 | 0 | 0.003 | 796462.1144 | 73592.3513
Maximum of Months | 256755.3564 | 403.7918 | 1039.1143 | 0 | 0.0041 | 1080480 | 104416.2547
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 708106000000 | 544024.206 | 27-JAN-12:00 | 270589.05 | 151653.867 | 79992.618 | 0 | 36046.024 | 0 | 921.256 | 0 | 0 | 0 | 0 | 0 | 4821.391 | 0 | 0
February | 631445000000 | 518528.28 | 07-FEB-14:00 | 270589.05 | 145652.643 | 78517.825 | 0 | 18498.302 | 0 | 640.548 | 0 | 0 | 0 | 0 | 0 | 4629.912 | 0 | 0
March | 736501000000 | 654096.38 | 30-MAR-15:00 | 270589.05 | 133019.064 | 88167.688 | 0 | 155774.868 | 0 | 1772.786 | 0 | 0 | 0 | 0 | 0 | 4772.925 | 0 | 0
April | 686608000000 | 723505.827 | 25-APR-14:00 | 270589.05 | 137835.548 | 101276.077 | 0 | 205461.147 | 0 | 3195.978 | 0 | 0 | 0 | 0 | 0 | 5148.027 | 0 | 0
May | 769658000000 | 842776.732 | 23-MAY-15:00 | 270589.05 | 133019.064 | 104454.963 | 0 | 325048.981 | 0 | 4600.107 | 0 | 0 | 0 | 0 | 0 | 5064.568 | 0 | 0
June | 856618000000 | 977058.819 | 28-JUN-11:00 | 270589.05 | 151653.867 | 104775.757 | 0 | 439233.487 | 0 | 5335.746 | 0 | 0 | 0 | 0 | 0 | 5470.911 | 0 | 0
July | 642911000000 | 782641.286 | 17-JUL-14:00 | 150327.25 | 78000.308 | 103145.592 | 0 | 440689.522 | 0 | 5329.867 | 0 | 0 | 0 | 0 | 0 | 5148.748 | 0 | 0
August | 663983000000 | 813567.996 | 30-AUG-13:00 | 150327.25 | 84617.158 | 99156.808 | 0 | 468894.71 | 0 | 5328.184 | 0 | 0 | 0 | 0 | 0 | 5243.885 | 0 | 0
September | 770687000000 | 899175.886 | 05-SEP-13:00 | 270589.05 | 145652.643 | 105170.251 | 0 | 367053.262 | 0 | 5282.623 | 0 | 0 | 0 | 0 | 0 | 5428.056 | 0 | 0
October | 736940000000 | 811151.482 | 05-OCT-15:09 | 270589.05 | 133019.064 | 101650.584 | 0 | 296805.101 | 0 | 4039.087 | 0 | 0 | 0 | 0 | 0 | 5048.596 | 0 | 0
November | 687905000000 | 595737.639 | 10-NOV-13:00 | 270589.05 | 145652.643 | 84572.353 | 0 | 88471.993 | 0 | 1470.848 | 0 | 0 | 0 | 0 | 0 | 4980.752 | 0 | 0
December | 689136000000 | 511626.747 | 21-DEC-14:30 | 270589.05 | 145652.643 | 77581.389 | 0 | 12664.126 | 0 | 517.631 | 0 | 0 | 0 | 0 | 0 | 4621.908 | 0 | 0
Annual Sum or Average | 8580500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 631445000000 | 511626.747 |  | 150327.25 | 78000.308 | 77581.389 | 0 | 12664.126 | 0 | 517.631 | 0 | 0 | 0 | 0 | 0 | 4621.908 | 0 | 0
Maximum of Months | 856618000000 | 977058.819 |  | 270589.05 | 151653.867 | 105170.251 | 0 | 468894.71 | 0 | 5335.746 | 0 | 0 | 0 | 0 | 0 | 5470.911 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 88208.85 | 50474.46 | 0 | 138683.31
Cost per Total Building Area ($/m2) | 4.5 | 2.58 | 0 | 7.08
Cost per Net Conditioned Building Area ($/m2) | 4.5 | 2.58 | 0 | 7.08

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22001.99 | 1123.01 | 1123.01
Net Site Energy | 22001.99 | 1123.01 | 1123.01
Total Source Energy | 44570.34 | 2274.93 | 2274.93
Net Source Energy | 44570.34 | 2274.93 | 2274.93
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12444.69 | 0 | 0 | 0 | 0
Cooling | 884.69 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1120.01 | 0 | 0 | 0 | 0 | 0
Pumps | 24.47 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 443.07 | 0 | 0 | 0 | 2677.93
Refrigeration | 134.61 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8760.84 | 13241.15 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 753.18 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 1335.99 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1229433.21 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 1012524.74 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 93065.5 | 62920.02 | 30145.48 | 0.68 | 2.9
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13393.88 | 9055.38 | 4338.5 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 261918.07 | 170249.94 | 91668.13 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 249799.55 | 157028.52 | 92771.03 | 0.63 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 250207.55 | 157290.67 | 92916.88 | 0.63 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 267344.45 | 168470.22 | 98874.23 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9281.52 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11140.45 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5452.31 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7241.18 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5384.51 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7209.08 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5388.58 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7229.51 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5046.81 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6898.33 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5037.58 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6901.56 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5106.67 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6943.28 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4703.99 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7893.46 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3959.56 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7827.68 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4017.43 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7976.4 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26151.61 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4094.37 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7798.57 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25333.66 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33310.91 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10471.12 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 5025.09 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12448.66 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18714.97 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12640.45 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18590.11 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12704.4 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22094.54 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12108.93 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16678.73 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12128.14 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16697.32 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12240.51 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20371.77 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13274.35 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19275.03 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1531107.56 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 290394.98 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 612443.02 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 41793.32 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 347847.23 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 124966.55 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 84443.48 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 84594.3 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 91305.28 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.75 | 7148.57 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 625.62 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 11.86 | 20095.23 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.01 | 15035.14 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.03 | 15061.99 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.67 | 16256.88 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 11266.05 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5575.39 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 323599.6349 | 438.7519 | 473.6965 | 0 | 0.0038 | 310822.5453 | 125860.2513
February | 267708.2747 | 372.3978 | 422.5735 | 0 | 0.0033 | 277348.4885 | 105022.9717
March | 248048.1647 | 372.1951 | 479.9311 | 0 | 0.0037 | 315183.7904 | 99905.0031
April | 178691.5038 | 295.8921 | 436.1493 | 0 | 0.0032 | 286589.4091 | 74624.6898
May | 188866.8954 | 332.081 | 523.9584 | 0 | 0.0038 | 344375.291 | 80722.7245
June | 218366.5577 | 394.2255 | 639.2569 | 0 | 0.0047 | 420196.8853 | 94313.276
July | 151453.8622 | 274.5416 | 447.0076 | 0 | 0.0033 | 293831.5928 | 65520.1327
August | 161190.5615 | 292.202 | 475.7797 | 0 | 0.0035 | 312744.3762 | 69733.3251
September | 168995.2053 | 300.4612 | 479.641 | 0 | 0.0035 | 315260.5755 | 72546.8228
October | 188032.3033 | 311.0427 | 457.9174 | 0 | 0.0034 | 300891.5545 | 78495.3074
November | 230948.3886 | 348.1975 | 452.2528 | 0 | 0.0035 | 297016.2069 | 93176.5435
December | 284338.4929 | 398.6537 | 458.9909 | 0 | 0.0036 | 301272.2348 | 111845.5248
Annual Sum or Average | 2610240 | 4130.6422 | 5747.1552 | 0 | 0.0433 | 3775530 | 1071770
Minimum of Months | 151453.8622 | 274.5416 | 422.5735 | 0 | 0.0032 | 277348.4885 | 65520.1327
Maximum of Months | 323599.6349 | 438.7519 | 639.2569 | 0 | 0.0047 | 420196.8853 | 125860.2513
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 721240000000 | 503082.133 | 04-JAN-11:09 | 270589.05 | 151653.867 | 70767.349 | 0 | 0 | 0 | 4165.185 | 0 | 0 | 0 | 0 | 0 | 5906.682 | 0 | 0
February | 643566000000 | 501542.448 | 03-FEB-11:09 | 270589.05 | 151653.867 | 70767.349 | 0 | 0 | 0 | 2612.294 | 0 | 0 | 0 | 0 | 0 | 5919.889 | 0 | 0
March | 731360000000 | 521458.394 | 23-MAR-13:00 | 270589.05 | 145652.643 | 75494.459 | 0 | 24272.013 | 0 | 722.132 | 0 | 0 | 0 | 0 | 0 | 4728.096 | 0 | 0
April | 665009000000 | 624445.48 | 14-APR-15:00 | 270589.05 | 133019.064 | 76490.784 | 0 | 138404.202 | 0 | 1177.63 | 0 | 0 | 0 | 0 | 0 | 4764.751 | 0 | 0
May | 799097000000 | 981815.641 | 31-MAY-11:00 | 270589.05 | 151653.867 | 98939.341 | 0 | 449216.383 | 0 | 6029.281 | 0 | 0 | 0 | 0 | 0 | 5387.719 | 0 | 0
June | 975035000000 | 1235660.612 | 29-JUN-14:00 | 270589.05 | 137835.548 | 107206.723 | 0 | 704896.476 | 0 | 9632.769 | 0 | 0 | 0 | 0 | 0 | 5500.046 | 0 | 0
July | 681814000000 | 983809.512 | 13-JUL-15:00 | 150327.25 | 73183.824 | 82197.596 | 0 | 666505.696 | 0 | 6444.117 | 0 | 0 | 0 | 0 | 0 | 5151.028 | 0 | 0
August | 725700000000 | 939482.256 | 25-AUG-15:00 | 150327.25 | 73183.824 | 83436.209 | 0 | 621172.737 | 0 | 6348.082 | 0 | 0 | 0 | 0 | 0 | 5014.154 | 0 | 0
September | 731538000000 | 972742.476 | 14-SEP-15:09 | 270589.05 | 133019.064 | 100815.966 | 0 | 456998.917 | 0 | 5968.189 | 0 | 0 | 0 | 0 | 0 | 5351.29 | 0 | 0
October | 698196000000 | 662847.454 | 06-OCT-15:09 | 270589.05 | 133019.064 | 81056.054 | 0 | 170320.88 | 0 | 3000.47 | 0 | 0 | 0 | 0 | 0 | 4861.937 | 0 | 0
November | 689204000000 | 558053.441 | 02-NOV-14:00 | 270589.05 | 137835.548 | 82255.726 | 0 | 61341.281 | 0 | 1197.268 | 0 | 0 | 0 | 0 | 0 | 4834.568 | 0 | 0
December | 699080000000 | 500775.436 | 20-DEC-11:09 | 270589.05 | 151653.867 | 70767.349 | 0 | 0 | 0 | 1847.459 | 0 | 0 | 0 | 0 | 0 | 5917.711 | 0 | 0
Annual Sum or Average | 8760840000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 643566000000 | 500775.436 |  | 150327.25 | 73183.824 | 70767.349 | 0 | 0 | 0 | 722.132 | 0 | 0 | 0 | 0 | 0 | 4728.096 | 0 | 0
Maximum of Months | 975035000000 | 1235660.612 |  | 270589.05 | 151653.867 | 107206.723 | 0 | 704896.476 | 0 | 9632.769 | 0 | 0 | 0 | 0 | 0 | 5919.889 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 159839.64 | 104302.54 | 0 | 264142.18
Cost per Total Building Area ($/m2) | 8.16 | 5.32 | 0 | 13.48
Cost per Net Conditioned Building Area ($/m2) | 8.16 | 5.32 | 0 | 13.48

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 18988.46 | 969.19 | 969.19
Net Site Energy | 18988.46 | 969.19 | 969.19
Total Source Energy | 40491.3 | 2066.73 | 2066.73
Net Source Energy | 40491.3 | 2066.73 | 2066.73
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9901.78 | 0 | 0 | 0 | 0
Cooling | 426.16 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1113.54 | 0 | 0 | 0 | 0 | 0
Pumps | 17.98 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 446.41 | 0 | 0 | 0 | 2677.93
Refrigeration | 132.17 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8286.87 | 10701.58 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.385 | 0.305 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.385 | 0.305 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.385 | 0.305 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.385 | 0.305 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.385 | 0.305 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.385 | 0.305 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.385 | 0.305 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.385 | 0.305 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 753.18 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 1335.99 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 613214.09 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 947110.73 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 327098.16 | 261238.67 | 65859.49 | 0.8 | 3.07
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 75736.12 | 57004.25 | 18731.87 | 0.75 | 3.16
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130839.27 | 104495.47 | 26343.8 | 0.8 | 3.32
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9631.38 | 7136.34 | 2495.04 | 0.74 | 3.07
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88148.52 | 65313.34 | 22835.19 | 0.74 | 3.12
VAV_OTHER_COOLC | Coil:Cooling:Water | 239330.64 | 154372.87 | 84957.77 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 146582.79 | 93608.81 | 52973.98 | 0.64 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 146592.69 | 93594.53 | 52998.16 | 0.64 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 156263.24 | 99799.79 | 56463.44 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8975.95 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11068.05 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4494.51 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6493.92 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4485.89 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6461.49 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4487.24 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6483.51 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4469.09 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6037.15 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4473.42 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6039.41 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4485.6 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6085.29 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3503.43 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7638.28 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3722.72 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7651.65 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3767.58 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7699.07 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23399.39 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4010.83 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7817.61 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24754.67 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33923.79 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9381.87 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4989.59 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12064.5 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16852.18 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11815.03 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16786.86 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11821.02 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20312.96 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11718.99 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14893.28 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11738.64 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14899.24 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11860.05 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17997.04 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11399.89 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17440.64 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1395210.11 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 269708.79 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 558084.04 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 34633.47 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 316973.14 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 127333.83 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 76077.28 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 76029.1 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 81408.13 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4 | 7635.36 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 568.94 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 13.23 | 22410.42 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.9 | 14825.29 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.9 | 14815.9 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.46 | 15864.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5619.26 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5215.19 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 285619.7016 | 405.8667 | 531.5078 | 0 | 0.0039 | 12594900 | 113025.0996
February | 237504.3739 | 346.968 | 476.231 | 0 | 0.0035 | 11287300 | 94900.6959
March | 236318.0937 | 365.5171 | 547.2026 | 0 | 0.0039 | 12973900 | 96387.2338
April | 197227.595 | 314.2018 | 489.7659 | 0 | 0.0035 | 11613800 | 81327.5083
May | 194388.4497 | 327.0736 | 545.624 | 0 | 0.0038 | 12941500 | 81838.2259
June | 205175.7436 | 355.5019 | 613.0725 | 0 | 0.0043 | 14542900 | 87373.2114
July | 141430.9088 | 248.9834 | 436.8145 | 0 | 0.003 | 10362400 | 60607.6619
August | 142122.5797 | 247.9024 | 430.6376 | 0 | 0.003 | 10215500 | 60681.8678
September | 181676.9311 | 311.1213 | 529.603 | 0 | 0.0037 | 12562400 | 77012.0779
October | 196003.6106 | 322.0032 | 521.9922 | 0 | 0.0037 | 12379700 | 81765.3947
November | 226752.5955 | 346.9267 | 511.3278 | 0 | 0.0037 | 12122600 | 92118.8815
December | 269862.8968 | 387.1475 | 515.4635 | 0 | 0.0038 | 12215600 | 107144.721
Annual Sum or Average | 2514080 | 3979.2139 | 6149.2427 | 0 | 0.0438 | 145813000 | 1034180
Minimum of Months | 141430.9088 | 247.9024 | 430.6376 | 0 | 0.003 | 10215500 | 60607.6619
Maximum of Months | 285619.7016 | 405.8667 | 613.0725 | 0 | 0.0043 | 14542900 | 113025.0996
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 715799000000 | 507434.675 | 05-JAN-08:09 | 270589.05 | 145652.643 | 71396.505 | 0 | 0 | 11207 | 4695 | 0 | 0 | 0 | 0 | 0 | 3894.477 | 0 | 0
February | 641484000000 | 528561.223 | 02-FEB-14:00 | 270589.05 | 145652.643 | 76393.661 | 0 | 30250.055 | 0 | 867.633 | 0 | 0 | 0 | 0 | 0 | 4808.182 | 0 | 0
March | 737337000000 | 601057.765 | 30-MAR-15:00 | 270589.05 | 133019.064 | 82348.171 | 0 | 108781.829 | 0 | 1622.659 | 0 | 0 | 0 | 0 | 0 | 4696.992 | 0 | 0
April | 660042000000 | 568185.805 | 06-APR-15:00 | 270589.05 | 133019.064 | 77131.092 | 0 | 81735.441 | 0 | 1089.634 | 0 | 0 | 0 | 0 | 0 | 4621.525 | 0 | 0
May | 735496000000 | 703824.292 | 16-MAY-15:00 | 270589.05 | 133019.064 | 87669.612 | 0 | 204429.459 | 0 | 3229.865 | 0 | 0 | 0 | 0 | 0 | 4887.242 | 0 | 0
June | 826508000000 | 963320.81 | 30-JUN-15:00 | 270589.05 | 133019.064 | 116136.976 | 0 | 433109.752 | 0 | 5178.208 | 0 | 0 | 0 | 0 | 0 | 5287.76 | 0 | 0
July | 588920000000 | 732682.994 | 21-JUL-15:00 | 150327.25 | 73183.824 | 110595.511 | 0 | 388827.913 | 0 | 4798.529 | 0 | 0 | 0 | 0 | 0 | 4949.966 | 0 | 0
August | 580574000000 | 685442.967 | 09-AUG-15:00 | 150327.25 | 73183.824 | 104286.441 | 0 | 348119.039 | 0 | 4627.353 | 0 | 0 | 0 | 0 | 0 | 4899.061 | 0 | 0
September | 713948000000 | 779037.037 | 07-SEP-15:00 | 270589.05 | 133019.064 | 105790.747 | 0 | 260048.82 | 0 | 4603.817 | 0 | 0 | 0 | 0 | 0 | 4985.539 | 0 | 0
October | 703571000000 | 666866.147 | 06-OCT-15:00 | 270589.05 | 133019.064 | 90859.61 | 0 | 164354.083 | 0 | 3231.921 | 0 | 0 | 0 | 0 | 0 | 4812.419 | 0 | 0
November | 688955000000 | 510295.047 | 21-NOV-11:39 | 270589.05 | 151653.867 | 72105.849 | 0 | 8823.963 | 0 | 393.731 | 0 | 0 | 0 | 0 | 0 | 6728.588 | 0 | 0
December | 694241000000 | 507084.984 | 18-DEC-08:09 | 270589.05 | 145652.643 | 71396.505 | 0 | 0 | 11207 | 4366.56 | 0 | 0 | 0 | 0 | 0 | 3873.226 | 0 | 0
Annual Sum or Average | 8286870000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 580574000000 | 507084.984 |  | 150327.25 | 73183.824 | 71396.505 | 0 | 0 | 0 | 393.731 | 0 | 0 | 0 | 0 | 0 | 3873.226 | 0 | 0
Maximum of Months | 826508000000 | 963320.81 |  | 270589.05 | 151653.867 | 116136.976 | 0 | 433109.752 | 11207 | 5178.208 | 0 | 0 | 0 | 0 | 0 | 6728.588 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 181168.99 | 87050.31 | 0 | 268219.3
Cost per Total Building Area ($/m2) | 9.25 | 4.44 | 0 | 13.69
Cost per Net Conditioned Building Area ($/m2) | 9.25 | 4.44 | 0 | 13.69

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 24037.52 | 1226.9 | 1226.9
Net Site Energy | 24037.52 | 1226.9 | 1226.9
Total Source Energy | 45461.24 | 2320.4 | 2320.4
Net Source Energy | 45461.24 | 2320.4 | 2320.4
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14993.58 | 0 | 0 | 0 | 0
Cooling | 323.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1122.31 | 0 | 0 | 0 | 0 | 0
Pumps | 20.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 497.68 | 0 | 0 | 0 | 2677.93
Refrigeration | 130.06 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8192.87 | 15844.65 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.487 | 0.409 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.487 | 0.409 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.487 | 0.409 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.487 | 0.409 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 2.956 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.487 | 0.409 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.487 | 0.409 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.487 | 0.409 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 2.956 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.487 | 0.409 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.487 | 0.409 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.487 | 0.409 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.487 | 0.409 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.487 | 0.409 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.487 | 0.409 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 753.18 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 1335.99 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1012541.26 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 1035242.2 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 2.73
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 94459.96 | 63862.79 | 30597.16 | 0.68 | 2.9
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 2.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11585.08 | 7832.48 | 3752.6 | 0.68 | 2.95
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 2.9
VAV_OTHER_COOLC | Coil:Cooling:Water | 241848.4 | 158350.18 | 83498.23 | 0.65 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 228054.28 | 144801.83 | 83252.45 | 0.63 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 228041.01 | 144788.11 | 83252.9 | 0.63 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 170504.15 | 110478.9 | 60025.26 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9562.31 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11353.12 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5356.03 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7390.79 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5261.96 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7346.57 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5267.61 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7369.99 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4885.58 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6826.86 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4889.86 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6831.25 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4900.26 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6885.41 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3916.56 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7278.39 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3852.6 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7197.06 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3893.22 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7351.24 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23633.97 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4299.59 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7889.95 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26100.53 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33540.58 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9258.38 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4086.96 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13131.79 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19734.54 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12896.04 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19547.24 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12901.17 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23037.15 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12796.71 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15437.85 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12816.08 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15443.44 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12922.56 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18115.62 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12673.75 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19320.21 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1567205.23 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 298468.11 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 626882.09 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 37001.52 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 356048.14 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 133608.85 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 85725.59 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 85708.85 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 92881.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.8 | 7255.68 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 541.13 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 12.32 | 20876.62 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.91 | 14831.25 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 7.9 | 14828.35 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 8.57 | 16069.31 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 9278.54 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5700.48 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 325730.2674 | 440.8529 | 474.25 | 0 | 0.0038 | 311179.8 | 126613.627
February | 276952.342 | 381.6491 | 425.4176 | 0 | 0.0034 | 279190.0001 | 108304.6006
March | 276836.601 | 399.5198 | 483.9492 | 0 | 0.0038 | 317732.1165 | 109982.7883
April | 200677.7158 | 314.8827 | 433.1041 | 0 | 0.0033 | 284509.7375 | 82141.786
May | 188102.9281 | 314.1872 | 467.948 | 0 | 0.0035 | 307496.2459 | 78814.1959
June | 181007.4184 | 322.3531 | 515.4762 | 0 | 0.0038 | 338816.574 | 77754.6095
July | 133808.9544 | 241.1997 | 390.5117 | 0 | 0.0029 | 256690.0742 | 57757.1158
August | 131316.8293 | 232.0692 | 368.1357 | 0 | 0.0027 | 241964.4043 | 56238.0623
September | 169657.3062 | 290.563 | 445.4571 | 0 | 0.0033 | 292748.9477 | 71772.3957
October | 198820.5765 | 319.7037 | 454.2825 | 0 | 0.0034 | 298461.5243 | 82120.983
November | 240733.049 | 358.0473 | 455.4505 | 0 | 0.0035 | 299088.6454 | 96655.576
December | 297738.5587 | 411.5707 | 461.5068 | 0 | 0.0037 | 302883.5006 | 116555.3524
Annual Sum or Average | 2621380 | 4026.5984 | 5375.4894 | 0 | 0.0409 | 3530760 | 1064710
Minimum of Months | 131316.8293 | 232.0692 | 368.1357 | 0 | 0.0027 | 241964.4043 | 56238.0623
Maximum of Months | 325730.2674 | 440.8529 | 515.4762 | 0 | 0.0038 | 338816.574 | 126613.627
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 722069000000 | 503927.602 | 09-JAN-11:09 | 270589.05 | 151653.867 | 70834.208 | 0 | 0 | 0 | 4961.094 | 0 | 0 | 0 | 0 | 0 | 5889.383 | 0 | 0
February | 647839000000 | 503242.798 | 01-FEB-11:09 | 270589.05 | 151653.867 | 70834.208 | 0 | 0 | 0 | 4242.879 | 0 | 0 | 0 | 0 | 0 | 5922.794 | 0 | 0
March | 737273000000 | 500558.44 | 07-MAR-11:09 | 270589.05 | 151653.867 | 70834.208 | 0 | 0 | 0 | 1542.761 | 0 | 0 | 0 | 0 | 0 | 5938.554 | 0 | 0
April | 660183000000 | 525849.325 | 04-APR-14:00 | 270589.05 | 137835.548 | 77301.203 | 0 | 34503.991 | 0 | 901.4 | 0 | 0 | 0 | 0 | 0 | 4718.133 | 0 | 0
May | 713522000000 | 695871.984 | 31-MAY-15:00 | 270589.05 | 133019.064 | 87375.472 | 0 | 197036.01 | 0 | 3009.27 | 0 | 0 | 0 | 0 | 0 | 4843.119 | 0 | 0
June | 786198000000 | 1025071.279 | 14-JUN-15:09 | 270589.05 | 133019.064 | 103062.253 | 0 | 504908.97 | 0 | 8165.123 | 0 | 0 | 0 | 0 | 0 | 5326.82 | 0 | 0
July | 595630000000 | 800315.351 | 06-JUL-14:00 | 150327.25 | 78000.308 | 92531.827 | 0 | 467938.587 | 0 | 6358.87 | 0 | 0 | 0 | 0 | 0 | 5158.51 | 0 | 0
August | 561460000000 | 725193.02 | 11-AUG-14:00 | 150327.25 | 78000.308 | 79324.35 | 0 | 407087.05 | 0 | 5367.129 | 0 | 0 | 0 | 0 | 0 | 5086.934 | 0 | 0
September | 679302000000 | 872952.593 | 07-SEP-14:00 | 270589.05 | 137835.548 | 105529.041 | 0 | 346481.356 | 0 | 7292.836 | 0 | 0 | 0 | 0 | 0 | 5224.764 | 0 | 0
October | 692557000000 | 554021.888 | 06-OCT-14:00 | 270589.05 | 137835.548 | 86828.622 | 0 | 52613.146 | 0 | 1374.572 | 0 | 0 | 0 | 0 | 0 | 4780.951 | 0 | 0
November | 694013000000 | 501522.028 | 09-NOV-11:50 | 270589.05 | 151653.867 | 71595.44 | 0 | 1232.236 | 0 | 178.156 | 0 | 0 | 0 | 0 | 0 | 6273.279 | 0 | 0
December | 702818000000 | 501471.415 | 20-DEC-11:09 | 270589.05 | 151653.867 | 70834.208 | 0 | 0 | 0 | 2462.64 | 0 | 0 | 0 | 0 | 0 | 5931.65 | 0 | 0
Annual Sum or Average | 8192870000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 561460000000 | 500558.44 |  | 150327.25 | 78000.308 | 70834.208 | 0 | 0 | 0 | 178.156 | 0 | 0 | 0 | 0 | 0 | 4718.133 | 0 | 0
Maximum of Months | 786198000000 | 1025071.279 |  | 270589.05 | 151653.867 | 105529.041 | 0 | 504908.97 | 0 | 8165.123 | 0 | 0 | 0 | 0 | 0 | 6273.279 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 143426.09 | 124691.77 | 0 | 268117.86
Cost per Total Building Area ($/m2) | 7.32 | 6.36 | 0 | 13.69
Cost per Net Conditioned Building Area ($/m2) | 7.32 | 6.36 | 0 | 13.69

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 35664.76 | 1820.37 | 1820.37
Net Site Energy | 35664.76 | 1820.37 | 1820.37
Total Source Energy | 59198.11 | 3021.55 | 3021.55
Net Source Energy | 59198.11 | 3021.55 | 3021.55
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 26582.85 | 0 | 0 | 0 | 0
Cooling | 154.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 174.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1256.5 | 0 | 0 | 0 | 0 | 0
Pumps | 33.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 562.32 | 0 | 0 | 0 | 2677.93
Refrigeration | 126.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8166.21 | 27498.56 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.616 | 0.541 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.616 | 0.541 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.616 | 0.541 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.616 | 0.541 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.616 | 0.541 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 2.956 | 0.616 | 0.541 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.616 | 0.541 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.616 | 0.541 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 2.956 | 0.616 | 0.541 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.616 | 0.541 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 2.956 | 0.616 | 0.541 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.616 | 0.541 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 2.956 | 0.616 | 0.541 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 2.956 | 0.616 | 0.541 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 2.956 | 0.616 | 0.541 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 2.956 | 0.616 | 0.541 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.616 | 0.541 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 2.956 | 0.616 | 0.541 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.616 | 0.541 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.616 | 0.541 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 2.956 | 0.616 | 0.541 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 2.956 | 0.616 | 0.541 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 2.956 | 0.616 | 0.541 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.616 | 0.541 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.616 | 0.541 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 2.956 | 0.616 | 0.541 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 2.956 | 0.616 | 0.541 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 753.18 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 1335.99 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 674721.11 | 2.5
HEATSYS1 BOILER | Boiler:HotWater | 1542499.23 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 327098.16 | 261238.67 | 65859.49 | 0.8 | 3.07
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 78567.42 | 62748.28 | 15819.14 | 0.8 | 3.35
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130839.27 | 104495.47 | 26343.8 | 0.8 | 3.32
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8516.9 | 6802.07 | 1714.83 | 0.8 | 3.19
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74312.34 | 59349.94 | 14962.4 | 0.8 | 3.35
VAV_OTHER_COOLC | Coil:Cooling:Water | 309027.15 | 217831.81 | 91195.34 | 0.7 | -
VAV_POD_1_COOLC | Coil:Cooling:Water | 211708.22 | 148414.34 | 63293.87 | 0.7 | -
VAV_POD_2_COOLC | Coil:Cooling:Water | 209576.72 | 146887.59 | 62689.13 | 0.7 | -
VAV_POD_3_COOLC | Coil:Cooling:Water | 225507.1 | 157708.91 | 67798.19 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11842.55 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13618.22 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6701.31 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9205.37 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6563.75 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9139.79 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6574.91 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9168.91 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6548.91 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7107.47 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6553.36 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7108.47 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6563.92 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7112.85 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4986.63 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8351.72 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5217.89 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8359.74 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5251 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8385.05 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27733.69 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5643.4 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9198.74 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31179.81 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38008.8 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8015.55 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4435.01 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21281.21 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33881.43 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21799.37 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33282.16 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21911.3 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36877.96 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17368.26 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19799.93 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17388.42 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19805.34 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17496.11 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19877.72 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18854.2 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29243.22 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1940738.03 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 390680.15 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 776295.21 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 50532.45 | 0.8
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 440909.81 | 0.78
VAV_OTHER_HEATC | Coil:Heating:Water | 195057.6 | -
VAV_POD_1_HEATC | Coil:Heating:Water | 131467.81 | -
VAV_POD_2_HEATC | Coil:Heating:Water | 130086.33 | -
VAV_POD_3_HEATC | Coil:Heating:Water | 139422.44 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.75 | 9053.16 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 596.78 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
VAV_OTHER_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 14.48 | 24529.32 | 1 | Fan Energy
VAV_POD_1_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.76 | 16786.98 | 1 | Fan Energy
VAV_POD_2_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 9.66 | 16610.58 | 1 | Fan Energy
VAV_POD_3_FAN | Fan:VariableVolume | 0.59 | 1017.59 | 10.35 | 17802.7 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6182.89 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8493.66 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 419521.6794 | 431.224 | 1055.5995 | 0 | 0.0041 | 211584.0143 | 152952.3989
February | 357137.2781 | 369.4268 | 947.3185 | 0 | 0.0037 | 189900.2002 | 130565.9662
March | 324760.241 | 346.0115 | 1072.2355 | 0 | 0.004 | 215023.2608 | 120279.7704
April | 220569.9806 | 245.4652 | 947.1124 | 0 | 0.0034 | 189999.9097 | 83301.3022
May | 170885.0941 | 203.2769 | 1007.927 | 0 | 0.0035 | 202265.8647 | 66553.7045
June | 162280.0678 | 199.0237 | 1082.3417 | 0 | 0.0037 | 217220.9671 | 64123.0428
July | 107732.4547 | 132.399 | 724.2566 | 0 | 0.0025 | 145355.8374 | 42611.3129
August | 118970.498 | 142.839 | 729.2801 | 0 | 0.0025 | 146353.1929 | 46537.5203
September | 171327.8042 | 199.6534 | 923.7134 | 0 | 0.0032 | 185351.0847 | 66087.4792
October | 251383.1949 | 276.2305 | 1005.6602 | 0 | 0.0036 | 201727.4116 | 94395.7772
November | 345990.7575 | 363.0661 | 1025.9013 | 0 | 0.0039 | 205695.0948 | 127286.404
December | 381058.8498 | 395.2359 | 1033.0388 | 0 | 0.004 | 207092.4327 | 139475.2538
Annual Sum or Average | 3031620 | 3303.852 | 11554.3849 | 0 | 0.0421 | 2317570 | 1134170
Minimum of Months | 107732.4547 | 132.399 | 724.2566 | 0 | 0.0025 | 145355.8374 | 42611.3129
Maximum of Months | 419521.6794 | 431.224 | 1082.3417 | 0 | 0.0041 | 217220.9671 | 152952.3989
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 745539000000 | 521901.768 | 02-JAN-11:09 | 270589.05 | 151653.867 | 74083.928 | 0 | 0 | 11207 | 8541.885 | 0 | 0 | 0 | 0 | 0 | 5826.038 | 0 | 0
February | 669134000000 | 513509.03 | 03-FEB-09:39 | 270589.05 | 145652.643 | 74083.928 | 0 | 0 | 11207 | 8009.077 | 0 | 0 | 0 | 0 | 0 | 3967.332 | 0 | 0
March | 757658000000 | 513283.498 | 14-MAR-07:19 | 270589.05 | 145652.643 | 74083.928 | 0 | 0 | 11207 | 7836.715 | 0 | 0 | 0 | 0 | 0 | 3914.162 | 0 | 0
April | 669485000000 | 505336.892 | 24-APR-11:00 | 270589.05 | 151653.867 | 78564.816 | 0 | 0 | 0 | 206.72 | 0 | 0 | 0 | 0 | 0 | 4322.439 | 0 | 0
May | 712706000000 | 607682.54 | 24-MAY-14:00 | 270589.05 | 137835.548 | 99526.629 | 0 | 92725.075 | 0 | 2139.079 | 0 | 0 | 0 | 0 | 0 | 4867.16 | 0 | 0
June | 765402000000 | 795128.128 | 20-JUN-14:00 | 270589.05 | 137835.548 | 108334.045 | 0 | 269218.46 | 0 | 3979.916 | 0 | 0 | 0 | 0 | 0 | 5171.11 | 0 | 0
July | 512177000000 | 517002.458 | 21-JUL-15:00 | 150327.25 | 73183.824 | 79465.341 | 0 | 207615.336 | 0 | 1717.274 | 0 | 0 | 0 | 0 | 0 | 4693.433 | 0 | 0
August | 515691000000 | 512811.14 | 15-AUG-13:00 | 150327.25 | 84617.158 | 81322.298 | 0 | 188197.625 | 0 | 3422.196 | 0 | 0 | 0 | 0 | 0 | 4924.614 | 0 | 0
September | 653105000000 | 521165.732 | 07-SEP-14:00 | 270589.05 | 137835.548 | 81927.658 | 0 | 25378.145 | 0 | 828.622 | 0 | 0 | 0 | 0 | 0 | 4606.71 | 0 | 0
October | 710808000000 | 508536.064 | 30-OCT-07:10 | 270589.05 | 145652.643 | 74083.928 | 0 | 0 | 11207 | 3123.376 | 0 | 0 | 0 | 0 | 0 | 3880.066 | 0 | 0
November | 724789000000 | 514264.308 | 27-NOV-10:09 | 270589.05 | 151653.867 | 74083.928 | 0 | 0 | 11207 | 2774.054 | 0 | 0 | 0 | 0 | 0 | 3956.409 | 0 | 0
December | 729713000000 | 521315.323 | 29-DEC-11:09 | 270589.05 | 151653.867 | 74083.928 | 0 | 0 | 11207 | 7904.102 | 0 | 0 | 0 | 0 | 0 | 5877.376 | 0 | 0
Annual Sum or Average | 8166210000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 512177000000 | 505336.892 |  | 150327.25 | 73183.824 | 74083.928 | 0 | 0 | 0 | 206.72 | 0 | 0 | 0 | 0 | 0 | 3880.066 | 0 | 0
Maximum of Months | 765402000000 | 795128.128 |  | 270589.05 | 151653.867 | 108334.045 | 0 | 269218.46 | 11207 | 8541.885 | 0 | 0 | 0 | 0 | 0 | 5877.376 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 218825.05 | 113553.9 | 0 | 332378.95
Cost per Total Building Area ($/m2) | 11.17 | 5.8 | 0 | 16.97
Cost per Net Conditioned Building Area ($/m2) | 11.17 | 5.8 | 0 | 16.97

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 586.61
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1366.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5 | 2255.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5 | 1494.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
Showers_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8 | 1848.37
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Gym_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Gym_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Gym_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Gym_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720