## BuildingSummary
Building Summary Strip Mall post-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Strip Mall
| Available Fuel Types | gas, electricity
| Principal Building Activity | Strip Mall
Form
| Total Floor Area (m2) | 2090 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 4
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 10 stores
| Floor to Ceiling Height (m) | 5.1816
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1184.13
| Net Dimensions - Total Area (m2) | 1059.67
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2090
| Net Dimensions - Total Area (m2) | 2090
| Roof to Skin Ratio | 0.64
Window
| Dimensions - Total Area (m2) | South: 124 East: 0.00 North: 0.00 West: 0.00 Total: 124
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2090
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.23 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
LGStore1 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 276.3003 | 20.75 | 6.1939 | 56.2472 | 60.2778 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.4124
SMStore1 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 60.2778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore2 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore3 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore4 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
LGStore2 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 157.8901 | 20.75 | 6.1939 | 56.2472 | 29.0625 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.1446
SMStore5 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore6 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore7 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore8 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 197.3602 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.6801
Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 337.4831
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 38.6269 | 26.0931 | 28.3018 | 25.9568 | 20.5034 | 21.6046 | 12.9533 | 27.6441 | 19.6253 | 16.0944 | 37.2597 | 27.1447 | 42.0192 | 30.5624 | 44.9119 | 39.4239
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 84.0018 | 68.2657 | 63.7557 | 62.9566 | 51.6833 | 52.1103 | 35.3382 | 58.9171 | 41.5666 | 37.3665 | 61.842 | 40.3415 | 60.0397 | 50.1041 | 68.3162 | 66.3147
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 33.5194 | 31.6519 | 29.027 | 30.0323 | 24.3562 | 24.2829 | 17.4351 | 22.8458 | 20.0227 | 18.6683 | 22.3894 | 18.5399 | 23.3568 | 20.3949 | 27.2475 | 27.1028
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 27.2089 | 24.9133 | 24.5566 | 25.1796 | 20.3762 | 20.0351 | 13.6745 | 22.1584 | 15.4345 | 14.8397 | 25.1055 | 17.4688 | 26.4006 | 20.3346 | 30.3582 | 27.0535
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 26.5994 | 24.2804 | 23.8947 | 24.526 | 19.9937 | 19.6037 | 13.294 | 21.5197 | 14.9806 | 14.4486 | 25.1019 | 17.6397 | 28.506 | 20.3319 | 30.564 | 27.0514
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 26.5032 | 24.1694 | 23.7648 | 24.4107 | 19.9273 | 19.5132 | 13.2137 | 21.4012 | 14.894 | 14.3679 | 25.1156 | 17.6913 | 28.5201 | 20.3438 | 30.5786 | 27.0624
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 47.4092 | 42.9397 | 42.271 | 43.2503 | 36.3502 | 35.6879 | 23.2908 | 37.6056 | 26.5742 | 25.5864 | 49.9425 | 36.6209 | 56.748 | 41.3969 | 60.855 | 53.9021
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 24.7172 | 22.3375 | 21.923 | 22.5204 | 18.8053 | 18.3102 | 12.1365 | 19.5885 | 13.739 | 13.2702 | 25.116 | 18.2322 | 28.5205 | 20.6594 | 30.5789 | 27.0626
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 24.6256 | 22.2367 | 21.8379 | 22.4162 | 18.7404 | 18.2533 | 12.0807 | 19.4895 | 13.6799 | 13.2126 | 25.1083 | 18.2544 | 28.512 | 20.6752 | 30.5698 | 27.055
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 24.9465 | 22.351 | 22.0823 | 22.5215 | 18.7939 | 18.3449 | 12.1036 | 19.5604 | 13.7075 | 13.2496 | 25.2143 | 18.3364 | 28.6098 | 20.7491 | 30.6654 | 27.1156
Heating (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 15.9999 | 26.3834 | 20.7328 | 31.5042 | 16.8709 | 24.6854 | 19.9049 | 35.6647 | 28.8099 | 27.7584 | 46.7872 | 38.0511 | 52.3867 | 49.5117 | 54.7511 | 73.943
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 26.0073 | 45.8533 | 35.4751 | 55.0199 | 28.999 | 42.8449 | 34.7268 | 62.7105 | 50.4714 | 48.7619 | 82.3646 | 66.8539 | 92.428 | 87.2119 | 96.6728 | 130.7287
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6721 | 14.9678 | 23.7583 | 12.3343 | 18.4061 | 15.0193 | 27.2676 | 21.9107 | 21.2062 | 35.8393 | 29.0687 | 40.2992 | 37.9896 | 42.1804 | 57.0758
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6075 | 14.8947 | 23.6895 | 12.2777 | 18.3385 | 14.972 | 27.2086 | 21.8493 | 21.1562 | 35.7695 | 29.0016 | 40.2329 | 37.9169 | 42.1155 | 57.0083
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6041 | 14.8908 | 23.6861 | 12.2747 | 18.3352 | 14.9696 | 27.2057 | 21.8464 | 21.1537 | 35.7663 | 28.9985 | 40.2299 | 37.9137 | 42.1126 | 57.0055
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6122 | 14.8997 | 23.6966 | 12.2825 | 18.3457 | 14.9775 | 27.2158 | 21.8578 | 21.1624 | 35.7787 | 29.011 | 40.2425 | 37.928 | 42.1255 | 57.0206
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 39.0384 | 29.59 | 47.1602 | 24.3765 | 36.4521 | 29.7692 | 54.2112 | 43.4683 | 42.1281 | 71.2965 | 57.7579 | 80.2232 | 75.5629 | 83.9859 | 113.7382
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6126 | 14.9002 | 23.697 | 12.2828 | 18.3461 | 14.9778 | 27.2162 | 21.8581 | 21.1627 | 35.7791 | 29.0113 | 40.2428 | 37.9283 | 42.1258 | 57.0208
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6104 | 14.8981 | 23.6923 | 12.2803 | 18.3413 | 14.974 | 27.2109 | 21.8517 | 21.1582 | 35.7721 | 29.004 | 40.2352 | 37.9194 | 42.1178 | 57.0104
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.7082 | 15.0117 | 23.7931 | 12.367 | 18.4407 | 15.0426 | 27.2935 | 21.937 | 21.228 | 35.8681 | 29.0961 | 40.3232 | 38.0167 | 42.2019 | 57.0933
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.47 | 3.44 | 3.49 | 3.44 | 3.58 | 3.54 | 3.96 | 3.44 | 3.7 | 3.9 | 3.44 | 3.66 | 3.21 | 3.71 | 3.19 | 3.73
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.64 | 3.19 | 3.26 | 3.23 | 3.35 | 3.33 | 3.73 | 3.19 | 3.45 | 3.68 | 3.19 | 3.45 | 3.27 | 3.45 | 3.24 | 4.32
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.44 | 3.49 | 3.48 | 3.64 | 3.59 | 4.01 | 3.55 | 3.77 | 3.95 | 3.57 | 4.01 | 3.58 | 3.77 | 3.52 | 3.77
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.44 | 3.44 | 3.59 | 3.53 | 3.98 | 3.44 | 3.97 | 3.92 | 3.44 | 3.93 | 3.49 | 3.77 | 3.45 | 3.77
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.44 | 3.44 | 3.58 | 3.52 | 3.97 | 3.45 | 3.98 | 3.91 | 3.44 | 3.92 | 3.44 | 3.77 | 3.44 | 3.77
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.44 | 3.44 | 3.58 | 3.52 | 3.97 | 3.45 | 3.98 | 3.91 | 3.44 | 3.92 | 3.44 | 3.77 | 3.44 | 3.77
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.19 | 3.21 | 3.21 | 3.21 | 3.56 | 3.5 | 3.69 | 3.44 | 3.69 | 3.64 | 3.19 | 3.61 | 3.19 | 3.43 | 3.19 | 3.45
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.44 | 3.44 | 3.78 | 3.72 | 3.95 | 3.45 | 3.95 | 3.89 | 3.44 | 3.88 | 3.44 | 3.75 | 3.44 | 3.77
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.45 | 3.44 | 3.78 | 3.72 | 3.95 | 3.45 | 3.95 | 3.89 | 3.44 | 3.88 | 3.44 | 3.75 | 3.44 | 3.77
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.44 | 3.44 | 3.78 | 3.72 | 3.95 | 3.45 | 3.95 | 3.89 | 3.44 | 3.88 | 3.44 | 3.75 | 3.44 | 3.77
Heating Efficiency (%)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 1.64 | 1.05 | 1.23 | 1.05 | 1.01 | 1.01 | 0.74 | 1.11 | 1.11 | 0.87 | 1.5 | 1.46 | 1.69 | 1.81 | 1.81 | 2.38
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 3.77 | 2.78 | 2.97 | 2.75 | 2.74 | 2.7 | 2.13 | 2.4 | 2.51 | 2.15 | 2.5 | 2.44 | 2.83 | 3.03 | 3.03 | 4.01
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 1.37 | 1.27 | 1.26 | 1.29 | 1.29 | 1.21 | 1.05 | 1.08 | 1.21 | 1.07 | 1.09 | 1.12 | 1.15 | 1.23 | 1.23 | 1.64
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 1.1 | 1 | 0.99 | 1.01 | 1.01 | 0.92 | 0.79 | 0.89 | 0.9 | 0.81 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 1.07 | 0.98 | 0.96 | 0.99 | 0.99 | 0.9 | 0.76 | 0.87 | 0.87 | 0.78 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 1.07 | 0.97 | 0.96 | 0.98 | 0.98 | 0.89 | 0.76 | 0.86 | 0.86 | 0.78 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.91 | 1.73 | 1.7 | 1.74 | 1.74 | 1.56 | 1.31 | 1.51 | 1.48 | 1.35 | 2.01 | 1.96 | 2.29 | 2.44 | 2.45 | 3.26
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 1 | 0.9 | 0.88 | 0.91 | 0.91 | 0.81 | 0.69 | 0.79 | 0.77 | 0.71 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 0.99 | 0.9 | 0.88 | 0.9 | 0.91 | 0.81 | 0.68 | 0.78 | 0.77 | 0.7 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 1 | 0.9 | 0.89 | 0.91 | 0.91 | 0.81 | 0.68 | 0.79 | 0.77 | 0.7 | 1.02 | 0.99 | 1.15 | 1.23 | 1.23 | 1.64
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.086934 | 0.12123 | 0.099363 | 0.1001 | 0.13142 | 0.099089 | 0.14878 | 0.076944 | 0.03734 | 0.075545 | 0.091063 | 0.037343 | 0.061592 | 0.075642 | 0.060516 | 0.095764
| Total Cost ($/m2) | 28.38 | 33.11 | 27.14 | 24.6 | 29.49 | 24.39 | 30.33 | 17.74 | 8.35 | 15.52 | 20.98 | 8.28 | 14.31 | 17.06 | 13.62 | 23.66
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.0114 | 0.0080426 | 0.0081387 | 0.0095083 | 0.0086075 | 0.0076295 | 0.0085638 | 0.0096572 | 0.0068693 | 0.0084137 | 0.0083012 | 0.0069032 | 0.0078741 | 0.008079 | 0.0078623 | 0.0041224
| Total Cost ($/m2) | 0.12 | 1.17 | 0.93 | 2.91 | 0.84 | 1.49 | 2.24 | 5.18 | 2.61 | 4.07 | 6.24 | 3.78 | 7.74 | 6.53 | 9.56 | 8.19
Total Utility Costs
| Cost Intensity ($/m2) | 28.49 | 34.27 | 28.07 | 27.51 | 30.32 | 25.88 | 32.57 | 22.92 | 10.95 | 19.59 | 27.22 | 12.07 | 22.05 | 23.6 | 23.18 | 31.84
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 218147.2222 | 136397.2222 | 135208.3333 | 78477.7778 | 34886.1111 | 84805.5556 | 8561.1111 | 54038.8889 | 38516.6667 | 9336.1111 | 41150 | 25213.8889 | 34011.1111 | 14733.3333 | 11655.5556 | 4383.3333
| Interior Lighting | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500
| Exterior Lighting | 25672.2222 | 25661.1111 | 25655.5556 | 25652.7778 | 25633.3333 | 25627.7778 | 25641.6667 | 25625 | 25633.3333 | 25583.3333 | 25627.7778 | 25613.8889 | 25611.1111 | 25605.5556 | 25591.6667 | 25436.1111
| Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 104519.4444 | 74827.7778 | 76161.1111 | 75658.3333 | 74486.1111 | 70197.2222 | 57986.1111 | 68325 | 69044.4444 | 60558.3333 | 80786.1111 | 78872.2222 | 92027.7778 | 97147.2222 | 99066.6667 | 152627.7778
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 682316.6667 | 570863.8889 | 571005.5556 | 513766.6667 | 468986.1111 | 514608.3333 | 426163.8889 | 481966.6667 | 467175 | 429458.3333 | 481541.6667 | 463680.5556 | 485627.7778 | 471463.8889 | 470291.6667 | 516425
Gas (MJ)
| Heating | 21330 | 302840 | 238770 | 639800 | 203310 | 407040 | 546770 | 1121050 | 793130 | 1010370 | 1572310 | 1145500 | 2055940 | 1690820 | 2542230 | 4150400
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 21330 | 302840 | 238770 | 639800 | 203310 | 407040 | 546770 | 1121050 | 793130 | 1010370 | 1572310 | 1145500 | 2055940 | 1690820 | 2542230 | 4150400
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2477670 | 2357950 | 2294390 | 2489360 | 1891660 | 2259630 | 2080960 | 2856130 | 2474960 | 2556420 | 3305860 | 2814750 | 3804200 | 3388090 | 4235280 | 6009530
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 375.6985 | 234.9066 | 232.8591 | 135.1563 | 60.0817 | 146.0542 | 14.7442 | 93.0671 | 66.3343 | 16.0789 | 70.8695 | 43.424 | 58.5748 | 25.3741 | 20.0735 | 7.5491
| Interior Lighting (elec) | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506
| Exterior Lighting (elec) | 44.2133 | 44.1942 | 44.1846 | 44.1798 | 44.1464 | 44.1368 | 44.1607 | 44.132 | 44.1464 | 44.0602 | 44.1368 | 44.1129 | 44.1081 | 44.0985 | 44.0746 | 43.8067
| Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 180.0059 | 128.8702 | 131.1665 | 130.3006 | 128.2818 | 120.8954 | 99.8651 | 117.671 | 118.91 | 104.295 | 139.1318 | 135.8357 | 158.4925 | 167.3093 | 170.615 | 262.8593
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1175.1024 | 983.1557 | 983.3997 | 884.8215 | 807.6993 | 886.271 | 733.9498 | 830.0547 | 804.5802 | 739.6236 | 829.3228 | 798.5619 | 836.36 | 811.9666 | 809.9478 | 889.3997
Gas (MJ/m2)
| Heating (gas) | 10.2042 | 144.8773 | 114.2265 | 306.0775 | 97.2626 | 194.7262 | 261.5724 | 536.3054 | 379.4299 | 483.3566 | 752.1863 | 548.0022 | 983.5528 | 808.8809 | 1216.1918 | 1985.5333
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 10.2042 | 144.8773 | 114.2265 | 306.0775 | 97.2626 | 194.7262 | 261.5724 | 536.3054 | 379.4299 | 483.3566 | 752.1863 | 548.0022 | 983.5528 | 808.8809 | 1216.1918 | 1985.5333
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1185.3066 | 1128.033 | 1097.6262 | 1190.899 | 904.9619 | 1080.9972 | 995.5222 | 1366.3602 | 1184.0101 | 1222.9802 | 1581.5091 | 1346.5642 | 1819.9127 | 1620.8475 | 2026.1395 | 2874.933
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 160.705 | 136.7914 | 120.4892 | 107.0419 | 126.3821 | 100.6122 | 97.3371 | 98.9481 | 99.0995 | 97.6588 | 101.1298 | 101.174 | 103.0186 | 104.0986 | 104.1283 | 113.1793
| Feb | 168.421 | 136.8234 | 125.0563 | 112.9863 | 122.3877 | 104.2174 | 105.8588 | 98.9481 | 102.7139 | 97.7605 | 101.1298 | 100.8387 | 103.0186 | 104.0986 | 104.1283 | 113.1793
| Mar | 169.3486 | 142.052 | 143.6818 | 121.1585 | 122.0116 | 113.2726 | 97.2674 | 116.6256 | 103.5497 | 98.7924 | 106.2539 | 107.523 | 103.0186 | 100.8167 | 104.1283 | 113.1793
| Apr | 176.471 | 160.0071 | 147.8018 | 139.7954 | 130.5556 | 136.4815 | 110.342 | 117.2837 | 119.3664 | 103.854 | 108.152 | 113.3547 | 112.8799 | 98.458 | 99.0589 | 107.3063
| May | 186.095 | 170.4653 | 168.0616 | 152.1114 | 127.3465 | 148.2509 | 112.1794 | 136.5291 | 126.5272 | 110.8364 | 139.3241 | 121.6036 | 163.802 | 117.5438 | 115.471 | 113.7637
| Jun | 193.0644 | 172.1958 | 190.6332 | 163.6526 | 129.3819 | 169.1671 | 113.5299 | 163.4256 | 137.3206 | 115.6986 | 164.9543 | 132.481 | 162.3434 | 141.9788 | 140.1628 | 131.3507
| Jul | 187.2959 | 178.5063 | 188.7338 | 177.0304 | 136.7337 | 167.7689 | 122.0865 | 168.9488 | 140.8328 | 125.6668 | 167.4306 | 139.292 | 170.0005 | 142.6544 | 156.7606 | 139.2665
| Aug | 194.7983 | 177.2577 | 188.0077 | 168.4917 | 146.2176 | 164.998 | 118.0187 | 169.0335 | 139.8724 | 121.7964 | 165.9457 | 140.8328 | 161.2739 | 138.04 | 154.4638 | 131.5518
| Sep | 187.1428 | 176.1386 | 178.099 | 158.3374 | 143.4593 | 161.0684 | 132.0851 | 147.2461 | 128.6114 | 136.6033 | 142.8343 | 131.3914 | 140.4884 | 129.5466 | 129.3551 | 108.2924
| Oct | 184.622 | 158.0831 | 151.0351 | 146.2593 | 134.9171 | 138.3915 | 111.8292 | 131.0367 | 116.6811 | 102.6012 | 121.4972 | 120.4758 | 124.7546 | 112.906 | 122.9355 | 113.1793
| Nov | 171.7628 | 143.1419 | 137.594 | 115.2875 | 129.1115 | 109.7452 | 97.9096 | 121.7072 | 102.1925 | 98.2997 | 120.4982 | 102.8285 | 103.3436 | 104.0986 | 104.1283 | 113.1793
| Dec | 162.1545 | 139.7702 | 118.6751 | 104.5712 | 128.9138 | 106.1137 | 97.2674 | 98.9481 | 99.0995 | 97.6588 | 101.1298 | 100.8125 | 103.0186 | 104.0986 | 104.1283 | 113.1793
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-13:00 | 28-JAN-14:00 | 23-JAN-15:00 | 26-JAN-13:00 | 18-JAN-16:49 | 06-JAN-17:10 | 02-JAN-16:49 | 02-JAN-17:10 | 02-JAN-16:30 | 02-JAN-16:30 | 27-JAN-17:10 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 25-FEB-13:39 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-15:00 | 13-FEB-11:00 | 08-FEB-17:10 | 15-FEB-15:00 | 01-FEB-17:30 | 14-FEB-15:00 | 21-FEB-17:40 | 01-FEB-16:00 | 11-FEB-17:30 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 01-FEB-09:09
| Mar | 13-MAR-15:30 | 25-MAR-12:30 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-14:09 | 31-MAR-15:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-15:09 | 29-MAR-15:00 | 31-MAR-14:00 | 30-MAR-16:00 | 01-MAR-17:00 | 30-MAR-16:00 | 01-MAR-17:49 | 01-MAR-17:00
| Apr | 01-APR-15:09 | 29-APR-14:30 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 06-APR-16:00 | 04-APR-14:00 | 01-APR-09:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:00 | 31-MAY-16:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 30-MAY-16:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-15:00 | 29-JUN-14:09 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-15:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-14:00 | 24-JUL-14:20 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-15:00
| Aug | 21-AUG-14:30 | 31-AUG-14:09 | 01-AUG-16:00 | 17-AUG-14:39 | 08-AUG-12:00 | 05-AUG-12:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-16:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-14:39
| Sep | 11-SEP-14:00 | 16-SEP-14:00 | 09-SEP-15:09 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:30 | 02-SEP-14:00 | 02-SEP-15:00 | 27-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 02-SEP-15:00
| Oct | 06-OCT-14:09 | 06-OCT-15:00 | 14-OCT-13:00 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-15:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 23-OCT-08:09
| Nov | 07-NOV-14:39 | 03-NOV-14:30 | 13-NOV-15:09 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-16:40 | 13-NOV-16:00 | 04-NOV-13:00 | 08-NOV-17:10 | 04-NOV-16:49 | 02-NOV-14:00 | 04-NOV-16:00 | 02-NOV-16:00 | 06-NOV-17:10 | 01-NOV-16:49 | 01-NOV-08:09
| Dec | 16-DEC-12:00 | 02-DEC-12:00 | 09-DEC-15:30 | 13-DEC-15:09 | 19-DEC-12:00 | 05-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 8170.97 | 7794.87 | 6762.66 | 6920.59 | 5447.45 | 7071.21 | 5345.4 | 7428.82 | 6446.4 | 3796.55 | 7864.13 | 6789.44 | 8253.87 | 7746.08 | 8595.13 | 11173.04
| Total Source Energy (MJ/m2) | 3908.96 | 3729.03 | 3235.23 | 3310.78 | 2606.04 | 3382.84 | 2557.22 | 3553.92 | 3083.93 | 1816.25 | 3762.17 | 3248.04 | 3948.62 | 3705.69 | 4111.87 | 5345.14
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 187509.6427 | 195879.1152 | 176678.037 | 169796.3552 | 58474.6051 | 180904.6402 | 59663.8313 | 150276.7126 | 205141.8874 | 49498.9827 | 285086.8227 | 210068.5924 | 203301.4682 | 202780.4075 | 206820.7957 | 220158.2406
| CO2 (kg) | 434409.3062 | 493591.5263 | 417807.7487 | 392518.3067 | 156921.5856 | 432296.6863 | 161455.2258 | 350073.2628 | 485996.8835 | 126943.6156 | 674271.8653 | 501029.188 | 490333.7979 | 488816.6542 | 503566.6299 | 580253.0724
| NOX (kg) | 765.1756 | 642.3666 | 696.4311 | 723.8476 | 134.8414 | 693.4107 | 139.6533 | 636.1851 | 817.7141 | 167.1766 | 1152.9861 | 828.5453 | 796.5513 | 791.3006 | 797.4673 | 652.3579
| SO2 (kg) | 2920.5915 | 2723.1044 | 2296.1882 | 1803.4922 | 1364.7442 | 2830.8671 | 1240.2344 | 1759.6681 | 2040.2673 | 332.2075 | 3245.6305 | 2025.1021 | 1146.7123 | 1259.3161 | 1110.6447 | 2629.9177
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0133 | 0.0077 | 0.0063 | 0.0066 | 0.0006 | 0.0053 | 0.0006 | 0.0072 | 0.008 | 0.0014 | 0.01 | 0.008 | 0.0086 | 0.0089 | 0.0084 | 0.0093
| Water for Electricity (m3) | 361.4624 | 928.8633 | 16961.4 | 3207.75 | 8234.32 | 14117.8 | 7482.5 | 109.4243 | 2121.34 | 4387.69 | 747.0839 | 2105.47 | 753.4238 | 29864.4 | 729.6293 | 527.6202

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2477.67 | 1185.31 | 1185.31
Net Site Energy | 2477.67 | 1185.31 | 1185.31
Total Source Energy | 8170.97 | 3908.96 | 3908.96
Net Source Energy | 8170.97 | 3908.96 | 3908.96
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 21.33 | 0 | 0 | 0 | 0
Cooling | 785.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 376.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2456.34 | 21.33 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38626.94 | 26641.11 | 11985.84 | 0.69 | 3.47
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 84001.84 | 59146.72 | 24855.12 | 0.7 | 3.64
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33519.44 | 22782.7 | 10736.74 | 0.68 | 3.45
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27208.93 | 18395.5 | 8813.43 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26599.41 | 17983.41 | 8616 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26503.24 | 17918.4 | 8584.85 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 47409.15 | 32052.53 | 15356.62 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24717.23 | 16710.9 | 8006.32 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24625.58 | 16648.94 | 7976.64 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24946.54 | 16865.94 | 8080.6 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15999.85 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26007.29 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20501.92 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.64 | 1870.5 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.77 | 7190.3 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.37 | 1560.32 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.1 | 1248.22 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.07 | 1220.26 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.07 | 1215.85 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.91 | 2087.91 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1133.91 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1129.71 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1144.43 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32150.6694 | 56.3191 | 213.7007 | 0 | 0.001 | 26448.0953 | 13846.3816
February | 29555.2801 | 51.948 | 197.8291 | 0 | 0.0009 | 24483.9198 | 12746.1839
March | 33895.4061 | 59.56 | 226.7508 | 0 | 0.001 | 28063.3475 | 14616.2895
April | 34715.9489 | 61.2013 | 233.81 | 0 | 0.0011 | 28937.1618 | 14990.109
May | 38567.6036 | 68.018 | 259.9596 | 0 | 0.0012 | 32173.5584 | 16655.8877
June | 39689.4538 | 69.9965 | 267.5213 | 0 | 0.0012 | 33109.4193 | 17140.3723
July | 41523.9704 | 73.2319 | 279.8866 | 0 | 0.0013 | 34639.7951 | 17932.6306
August | 42219.9643 | 74.4594 | 284.5779 | 0 | 0.0013 | 35220.4016 | 18233.204
September | 39055.7116 | 68.8789 | 263.2497 | 0 | 0.0012 | 32580.744 | 16866.6831
October | 37591.1327 | 66.2957 | 253.3757 | 0 | 0.0012 | 31358.7099 | 16234.1597
November | 33616.7058 | 59.2713 | 226.4683 | 0 | 0.001 | 28028.5369 | 14516.2485
December | 31827.4595 | 55.9955 | 213.4618 | 0 | 0.001 | 26418.7121 | 13731.4929
Annual Sum or Average | 434409.3062 | 765.1756 | 2920.5915 | 0 | 0.0133 | 361462.402 | 187509.6427
Minimum of Months | 29555.2801 | 51.948 | 197.8291 | 0 | 0.0009 | 24483.9198 | 12746.1839
Maximum of Months | 42219.9643 | 74.4594 | 284.5779 | 0 | 0.0013 | 35220.4016 | 18233.204
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 179730000000 | 160705.046 | 06-JAN-13:00 | 72368.391 | 8089.532 | 19801.403 | 0 | 60445.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 166382000000 | 168421.037 | 25-FEB-13:39 | 72368.391 | 8089.532 | 19801.403 | 0 | 68161.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 190706000000 | 169348.613 | 13-MAR-15:30 | 72368.391 | 8089.532 | 19801.403 | 0 | 69089.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 196644000000 | 176470.994 | 01-APR-15:09 | 72368.391 | 8089.532 | 19801.403 | 0 | 76211.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 218637000000 | 186095.001 | 24-MAY-14:00 | 72368.391 | 8089.532 | 19801.403 | 0 | 85835.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 224997000000 | 193064.445 | 27-JUN-14:00 | 72368.391 | 8089.532 | 19801.403 | 0 | 92805.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 235397000000 | 187295.935 | 13-JUL-14:00 | 72368.391 | 8089.532 | 19801.403 | 0 | 87036.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 239342000000 | 194798.334 | 21-AUG-14:30 | 72368.391 | 8089.532 | 19801.403 | 0 | 94539.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 221404000000 | 187142.765 | 11-SEP-14:00 | 72368.391 | 8089.532 | 19801.403 | 0 | 86883.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 213100000000 | 184622.048 | 06-OCT-14:09 | 72368.391 | 8089.532 | 19801.403 | 0 | 84362.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 190469000000 | 171762.755 | 07-NOV-14:39 | 72368.391 | 8089.532 | 19801.403 | 0 | 71503.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 179530000000 | 162154.467 | 16-DEC-12:00 | 72368.391 | 8089.532 | 19801.403 | 0 | 61895.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2456340000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 166382000000 | 160705.046 |  | 72368.391 | 8089.532 | 19801.403 | 0 | 60445.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 239342000000 | 194798.334 |  | 72368.391 | 8089.532 | 19801.403 | 0 | 94539.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 59316.72 | 243.16 | 0 | 59559.88
Cost per Total Building Area ($/m2) | 28.38 | 0.12 | 0 | 28.49
Cost per Net Conditioned Building Area ($/m2) | 28.38 | 0.12 | 0 | 28.49

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2357.95 | 1128.04 | 1128.04
Net Site Energy | 2357.95 | 1128.04 | 1128.04
Total Source Energy | 7794.87 | 3729.03 | 3729.03
Net Source Energy | 7794.87 | 3729.03 | 3729.03
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 302.84 | 0 | 0 | 0 | 0
Cooling | 491.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 269.38 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2055.11 | 302.84 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26093.07 | 17641.08 | 8451.98 | 0.68 | 3.44
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68265.72 | 46321.61 | 21944.11 | 0.68 | 3.19
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31651.92 | 21399.33 | 10252.59 | 0.68 | 3.44
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24913.25 | 16843.43 | 8069.82 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24280.38 | 16415.56 | 7864.82 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24169.43 | 16340.54 | 7828.88 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42939.67 | 29030.79 | 13908.88 | 0.68 | 3.21
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22337.52 | 15102.02 | 7235.5 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22236.71 | 15033.87 | 7202.84 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22350.99 | 15111.13 | 7239.86 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26383.37 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 45853.28 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19672.07 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19607.54 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19604.09 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19612.24 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39038.36 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19612.64 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19610.41 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19708.21 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1197.03 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.78 | 3036.69 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1452.04 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1142.9 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1113.87 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1108.78 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.73 | 1969.87 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1024.74 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1020.12 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1025.36 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37451.3241 | 47.3905 | 187.7199 | 0 | 0.0005 | 64026.1044 | 14688.4467
February | 33502.7584 | 42.3585 | 167.4309 | 0 | 0.0005 | 57105.8978 | 13135.2379
March | 36286.836 | 47.0776 | 198.1383 | 0 | 0.0006 | 67585.2117 | 14381.3367
April | 37280.7734 | 48.8794 | 210.7403 | 0 | 0.0006 | 71886.0874 | 14841.2904
May | 43612.4729 | 57.2988 | 248.1833 | 0 | 0.0007 | 84658.8755 | 17377.1059
June | 47560.5289 | 62.514 | 271.0439 | 0 | 0.0008 | 92457.0545 | 18953.805
July | 50389.7977 | 66.2328 | 287.1677 | 0 | 0.0008 | 97957.1164 | 20081.3242
August | 50528.8022 | 66.4154 | 287.959 | 0 | 0.0008 | 98227.0643 | 20136.7128
September | 44533.4618 | 58.5348 | 253.7877 | 0 | 0.0007 | 86570.7059 | 17747.4116
October | 40740.2705 | 53.4478 | 230.7533 | 0 | 0.0006 | 78712.9205 | 16222.7071
November | 35193.0287 | 45.8851 | 195.3402 | 0 | 0.0006 | 66631.7919 | 13977.0505
December | 36511.4718 | 46.3319 | 184.84 | 0 | 0.0005 | 63044.4757 | 14336.6866
Annual Sum or Average | 493591.5263 | 642.3666 | 2723.1044 | 0 | 0.0077 | 928863.306 | 195879.1152
Minimum of Months | 33502.7584 | 42.3585 | 167.4309 | 0 | 0.0005 | 57105.8978 | 13135.2379
Maximum of Months | 50528.8022 | 66.4154 | 287.959 | 0 | 0.0008 | 98227.0643 | 20136.7128
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 141658000000 | 136791.387 | 03-JAN-13:00 | 72368.391 | 8089.532 | 14091.406 | 0 | 42242.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 126347000000 | 136823.403 | 23-FEB-15:09 | 72368.391 | 8089.532 | 14091.406 | 0 | 42274.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 149532000000 | 142051.995 | 25-MAR-12:30 | 72368.391 | 8089.532 | 14091.406 | 0 | 47502.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 159048000000 | 160007.139 | 29-APR-14:30 | 72368.391 | 8089.532 | 14091.406 | 0 | 65457.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 187308000000 | 170465.26 | 26-MAY-14:00 | 72368.391 | 8089.532 | 14091.406 | 0 | 75915.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 204561000000 | 172195.777 | 13-JUN-14:00 | 72368.391 | 8089.532 | 14091.406 | 0 | 77646.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 216730000000 | 178506.336 | 18-JUL-12:00 | 72368.391 | 8089.532 | 14091.406 | 0 | 83957.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 217328000000 | 177257.73 | 31-AUG-14:09 | 72368.391 | 8089.532 | 14091.406 | 0 | 82708.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 191538000000 | 176138.598 | 16-SEP-14:00 | 72368.391 | 8089.532 | 14091.406 | 0 | 81589.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 174152000000 | 158083.122 | 06-OCT-15:00 | 72368.391 | 8089.532 | 14091.406 | 0 | 63533.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 147423000000 | 143141.865 | 03-NOV-14:30 | 72368.391 | 8089.532 | 14091.406 | 0 | 48592.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 139486000000 | 139770.182 | 02-DEC-12:00 | 72368.391 | 8089.532 | 14091.406 | 0 | 45220.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2055110000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 126347000000 | 136791.387 |  | 72368.391 | 8089.532 | 14091.406 | 0 | 42242.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 217328000000 | 178506.336 |  | 72368.391 | 8089.532 | 14091.406 | 0 | 83957.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 69204.95 | 2435.62 | 0 | 71640.56
Cost per Total Building Area ($/m2) | 33.11 | 1.17 | 0 | 34.27
Cost per Net Conditioned Building Area ($/m2) | 33.11 | 1.17 | 0 | 34.27

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2294.39 | 1097.63 | 1097.63
Net Site Energy | 2294.39 | 1097.63 | 1097.63
Total Source Energy | 6762.66 | 3235.23 | 3235.23
Net Source Energy | 6762.66 | 3235.23 | 3235.23
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 238.77 | 0 | 0 | 0 | 0
Cooling | 486.75 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 274.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2055.62 | 238.77 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28301.81 | 19664.93 | 8636.88 | 0.69 | 3.49
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 63755.69 | 45536.66 | 18219.03 | 0.71 | 3.26
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29027 | 20187.58 | 8839.42 | 0.7 | 3.49
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24556.63 | 16602.33 | 7954.3 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23894.73 | 16154.83 | 7739.9 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23764.81 | 16066.99 | 7697.82 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42271.02 | 28578.73 | 13692.29 | 0.68 | 3.21
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21923 | 14821.77 | 7101.23 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21837.91 | 14764.24 | 7073.66 | 0.68 | 3.45
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22082.28 | 14929.46 | 7152.82 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20732.81 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35475.1 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14967.82 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14894.74 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14890.81 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14899.7 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29590.02 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14900.16 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14898.06 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15011.74 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1397.67 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.97 | 3244.93 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.26 | 1436.99 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1126.54 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.96 | 1096.18 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.96 | 1090.22 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.7 | 1939.2 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.88 | 1005.73 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.88 | 1020.04 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1013.03 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 29802.7491 | 47.9777 | 151.4952 | 0 | 0.0004 | 1118970 | 12430.8011
February | 27108.5935 | 43.6847 | 138.1196 | 0 | 0.0004 | 1020180 | 11311.5279
March | 31441.5741 | 52.304 | 172.0369 | 0 | 0.0005 | 1270790 | 13285.0535
April | 31940.5248 | 53.6741 | 178.6743 | 0 | 0.0005 | 1319840 | 13550.4953
May | 35762.8999 | 60.4049 | 202.2812 | 0 | 0.0005 | 1494240 | 15203.2025
June | 41012.8943 | 69.3181 | 232.307 | 0 | 0.0006 | 1716040 | 17439.6594
July | 43865.3613 | 74.1396 | 248.4666 | 0 | 0.0007 | 1835410 | 18652.6311
August | 43791.7465 | 74.0152 | 248.0496 | 0 | 0.0007 | 1832330 | 18621.3283
September | 39239.3317 | 66.3207 | 222.2627 | 0 | 0.0006 | 1641840 | 16685.5197
October | 33890.4375 | 57.0837 | 190.5429 | 0 | 0.0005 | 1407520 | 14391.1602
November | 29276.7589 | 48.6588 | 159.874 | 0 | 0.0004 | 1180940 | 12365.9094
December | 30674.8771 | 48.8495 | 152.0783 | 0 | 0.0004 | 1123250 | 12740.7487
Annual Sum or Average | 417807.7487 | 696.4311 | 2296.1882 | 0 | 0.0063 | 16961400 | 176678.037
Minimum of Months | 27108.5935 | 43.6847 | 138.1196 | 0 | 0.0004 | 1020180 | 11311.5279
Maximum of Months | 43865.3613 | 74.1396 | 248.4666 | 0 | 0.0007 | 1835410 | 18652.6311
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 135613000000 | 120489.205 | 28-JAN-14:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 25660.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 123640000000 | 125056.251 | 28-FEB-15:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 30227.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 154012000000 | 143681.839 | 17-MAR-14:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 48853.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 159957000000 | 147801.759 | 01-APR-15:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 52973.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 181093000000 | 168061.645 | 27-MAY-15:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 73233.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 207974000000 | 190633.233 | 28-JUN-15:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 95804.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 222441000000 | 188733.84 | 11-JUL-15:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 93905.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 222068000000 | 188007.693 | 01-AUG-16:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 93179.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 198982000000 | 178099.042 | 09-SEP-15:09 | 72368.391 | 8089.532 | 14370.524 | 0 | 83270.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 170583000000 | 151035.144 | 14-OCT-13:00 | 72368.391 | 8089.532 | 14370.524 | 0 | 56206.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 143123000000 | 137594.049 | 13-NOV-15:09 | 72368.391 | 8089.532 | 14370.524 | 0 | 42765.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 136131000000 | 118675.064 | 09-DEC-15:30 | 72368.391 | 8089.532 | 14370.524 | 0 | 23846.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2055620000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 123640000000 | 118675.064 |  | 72368.391 | 8089.532 | 14370.524 | 0 | 23846.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 222441000000 | 190633.233 |  | 72368.391 | 8089.532 | 14370.524 | 0 | 95804.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 56737.02 | 1943.27 | 0 | 58680.29
Cost per Total Building Area ($/m2) | 27.14 | 0.93 | 0 | 28.07
Cost per Net Conditioned Building Area ($/m2) | 27.14 | 0.93 | 0 | 28.07

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2489.36 | 1190.9 | 1190.9
Net Site Energy | 2489.36 | 1190.9 | 1190.9
Total Source Energy | 6920.59 | 3310.78 | 3310.78
Net Source Energy | 6920.59 | 3310.78 | 3310.78
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 639.8 | 0 | 0 | 0 | 0
Cooling | 282.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 272.37 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1849.56 | 639.8 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.255 | 0.129 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.255 | 0.129 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.255 | 0.129 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.255 | 0.129 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.255 | 0.129 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25956.83 | 17548.98 | 8407.85 | 0.68 | 3.44
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 62956.58 | 43888.55 | 19068.04 | 0.7 | 3.23
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30032.32 | 20816.05 | 9216.27 | 0.69 | 3.48
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25179.64 | 17023.53 | 8156.11 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24525.98 | 16581.6 | 7944.38 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24410.66 | 16503.63 | 7907.02 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 43250.33 | 29240.82 | 14009.51 | 0.68 | 3.21
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22520.4 | 15225.67 | 7294.74 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22416.22 | 15155.23 | 7260.99 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22521.51 | 15226.41 | 7295.09 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31504.22 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55019.88 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23758.31 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23689.5 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23686.08 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23696.64 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 47160.21 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23697.02 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23692.32 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23793.09 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1190.78 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.75 | 3010.66 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.29 | 1473.52 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1155.12 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1125.14 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1119.85 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.74 | 1984.12 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1033.13 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1028.35 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1033.18 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 35013.5413 | 58.4394 | 130.8286 | 0 | 0.0005 | 232636.3182 | 14580.1546
February | 30670.9746 | 52.082 | 118.9682 | 0 | 0.0004 | 211557.0887 | 12854.0924
March | 30512.8435 | 55.37 | 135.7891 | 0 | 0.0005 | 241510.3928 | 13116.2751
April | 29110.9282 | 54.5691 | 138.0949 | 0 | 0.0005 | 245628.9411 | 12674.6233
May | 31905.2814 | 61.4579 | 159.4423 | 0 | 0.0006 | 283615.1382 | 14043.7024
June | 34808.7003 | 67.2129 | 174.7475 | 0 | 0.0006 | 310841.3578 | 15336.6874
July | 37289.4843 | 72.0028 | 187.1998 | 0 | 0.0007 | 332991.5688 | 16429.6855
August | 37730.9896 | 72.8583 | 189.4309 | 0 | 0.0007 | 336960.2469 | 16624.4879
September | 33561.9259 | 64.7973 | 168.4483 | 0 | 0.0006 | 299636.3202 | 14786.6046
October | 29566.5098 | 55.9166 | 142.6751 | 0 | 0.0005 | 253780.397 | 12918.5528
November | 29032.4512 | 52.3087 | 127.3629 | 0 | 0.0005 | 226520.0393 | 12445.2833
December | 33314.6768 | 56.8327 | 130.5045 | 0 | 0.0005 | 232074.6818 | 13986.2058
Annual Sum or Average | 392518.3067 | 723.8476 | 1803.4922 | 0 | 0.0066 | 3207750 | 169796.3552
Minimum of Months | 29032.4512 | 52.082 | 118.9682 | 0 | 0.0004 | 211557.0887 | 12445.2833
Maximum of Months | 37730.9896 | 72.8583 | 189.4309 | 0 | 0.0007 | 336960.2469 | 16624.4879
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 134136000000 | 107041.929 | 23-JAN-15:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 12430.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 121982000000 | 112986.331 | 18-FEB-15:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 18374.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 139253000000 | 121158.534 | 28-MAR-14:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 26546.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 141627000000 | 139795.419 | 15-APR-15:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 45183.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 163530000000 | 152111.412 | 31-MAY-16:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 57499.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 179228000000 | 163652.593 | 19-JUN-14:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 69040.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 192000000000 | 177030.402 | 03-JUL-14:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 82418.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 194288000000 | 168491.681 | 17-AUG-14:39 | 72368.391 | 8089.532 | 14153.866 | 0 | 73879.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 172767000000 | 158337.388 | 11-SEP-13:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 63725.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 146327000000 | 146259.25 | 12-OCT-15:00 | 72368.391 | 8089.532 | 14153.866 | 0 | 51647.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 130609000000 | 115287.505 | 22-NOV-15:09 | 72368.391 | 8089.532 | 14153.866 | 0 | 20675.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 133812000000 | 104571.236 | 13-DEC-15:09 | 72368.391 | 8089.532 | 14153.866 | 0 | 9959.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1849560000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 121982000000 | 104571.236 |  | 72368.391 | 8089.532 | 14153.866 | 0 | 9959.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 194288000000 | 177030.402 |  | 72368.391 | 8089.532 | 14153.866 | 0 | 82418.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51428.59 | 6083.39 | 0 | 57511.99
Cost per Total Building Area ($/m2) | 24.6 | 2.91 | 0 | 27.51
Cost per Net Conditioned Building Area ($/m2) | 24.6 | 2.91 | 0 | 27.51

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1891.66 | 904.96 | 904.96
Net Site Energy | 1891.66 | 904.96 | 904.96
Total Source Energy | 5447.45 | 2606.04 | 2606.04
Net Source Energy | 5447.45 | 2606.04 | 2606.04
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 203.31 | 0 | 0 | 0 | 0
Cooling | 125.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 268.15 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1688.35 | 203.31 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.44 | 0.272 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.44 | 0.272 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.44 | 0.272 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.44 | 0.272 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.44 | 0.272 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20503.39 | 14966.7 | 5536.69 | 0.73 | 3.58
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 51683.34 | 38969.71 | 12713.63 | 0.75 | 3.35
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24356.16 | 18322.93 | 6033.23 | 0.75 | 3.64
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20376.24 | 14958.21 | 5418.03 | 0.73 | 3.59
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19993.7 | 14637.77 | 5355.93 | 0.73 | 3.58
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19927.28 | 14582.2 | 5345.08 | 0.73 | 3.58
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 36350.16 | 26247.33 | 10102.84 | 0.72 | 3.56
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18805.34 | 13646.5 | 5158.84 | 0.73 | 3.78
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18740.44 | 13592.56 | 5147.88 | 0.73 | 3.78
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18793.87 | 13636.99 | 5156.88 | 0.73 | 3.78
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16870.91 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28998.95 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12334.28 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12277.74 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12274.74 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12282.46 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24376.45 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12282.81 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12280.3 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12367.01 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1147.38 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.74 | 2999.87 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.29 | 1464.78 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1156.05 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1126.93 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1121.89 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.74 | 1980.47 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1037.25 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1032.39 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.91 | 1036.4 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13836.3996 | 11.9505 | 109.4142 | 0 | 0.0001 | 660123.0103 | 5122.6197
February | 12355.2291 | 10.6655 | 98.7282 | 0 | 0 | 595655.6095 | 4577.3815
March | 13535.6949 | 11.6627 | 112.0692 | 0 | 0.0001 | 676160.4487 | 5026.6453
April | 12545.1163 | 10.7957 | 106.2765 | 0 | 0 | 641220.033 | 4666.1313
May | 12663.8801 | 10.8697 | 112.3366 | 0 | 0.0001 | 677802.455 | 4725.7249
June | 12347.3115 | 10.5836 | 112.1021 | 0 | 0.0001 | 676396.0464 | 4615.4442
July | 13222.6173 | 11.317 | 123.0568 | 0 | 0.0001 | 742504.4651 | 4951.8115
August | 14341.9802 | 12.2749 | 133.5129 | 0 | 0.0001 | 805595.2463 | 5371.1261
September | 13172.0541 | 11.2746 | 122.4302 | 0 | 0.0001 | 738723.3299 | 4932.3998
October | 12865.4406 | 11.0267 | 116.9767 | 0 | 0.0001 | 705808.7709 | 4809.6418
November | 12514.4766 | 10.76 | 107.6924 | 0 | 0.0001 | 649768.7135 | 4659.8465
December | 13521.3852 | 11.6604 | 110.1483 | 0 | 0.0001 | 664564.663 | 5015.8324
Annual Sum or Average | 156921.5856 | 134.8414 | 1364.7442 | 0 | 0.0006 | 8234320 | 58474.6051
Minimum of Months | 12347.3115 | 10.5836 | 98.7282 | 0 | 0 | 595655.6095 | 4577.3815
Maximum of Months | 14341.9802 | 12.2749 | 133.5129 | 0 | 0.0001 | 805595.2463 | 5371.1261
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 135350000000 | 126382.142 | 26-JAN-13:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 31820.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 122132000000 | 122387.665 | 13-FEB-11:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 27826.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 138638000000 | 122011.578 | 31-MAR-14:09 | 72368.391 | 8089.532 | 14103.421 | 0 | 27450.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 131474000000 | 130555.643 | 11-APR-15:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 35994.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 138975000000 | 127346.482 | 30-MAY-12:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 32785.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 138687000000 | 129381.911 | 28-JUN-12:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 34820.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 152241000000 | 136733.682 | 24-JUL-14:20 | 72368.391 | 8089.532 | 14103.421 | 0 | 42172.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 165177000000 | 146217.648 | 08-AUG-12:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 51656.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 151466000000 | 143459.264 | 25-SEP-14:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 48897.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 144717000000 | 134917.098 | 05-OCT-14:09 | 72368.391 | 8089.532 | 14103.421 | 0 | 40355.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 133227000000 | 129111.531 | 20-NOV-12:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 34550.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 136261000000 | 128913.768 | 19-DEC-12:00 | 72368.391 | 8089.532 | 14103.421 | 0 | 34352.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1688350000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 122132000000 | 122011.578 |  | 72368.391 | 8089.532 | 14103.421 | 0 | 27450.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 165177000000 | 146217.648 |  | 72368.391 | 8089.532 | 14103.421 | 0 | 51656.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 61634.74 | 1750 | 0 | 63384.73
Cost per Total Building Area ($/m2) | 29.49 | 0.84 | 0 | 30.32
Cost per Net Conditioned Building Area ($/m2) | 29.49 | 0.84 | 0 | 30.32

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2259.63 | 1081 | 1081
Net Site Energy | 2259.63 | 1081 | 1081
Total Source Energy | 7071.21 | 3382.84 | 3382.84
Net Source Energy | 7071.21 | 3382.84 | 3382.84
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 407.04 | 0 | 0 | 0 | 0
Cooling | 305.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 252.71 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1852.59 | 407.04 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.251 | 0.11 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21604.59 | 15428.87 | 6175.72 | 0.71 | 3.54
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52110.3 | 38898.63 | 13211.67 | 0.75 | 3.33
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24282.89 | 17805.04 | 6477.85 | 0.73 | 3.59
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20035.11 | 14253.42 | 5781.68 | 0.71 | 3.53
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19603.73 | 13896.84 | 5706.89 | 0.71 | 3.52
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19513.17 | 13822.18 | 5690.99 | 0.71 | 3.52
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35687.86 | 24905.26 | 10782.59 | 0.7 | 3.5
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18310.24 | 12833.58 | 5476.67 | 0.7 | 3.72
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18253.32 | 12787 | 5466.32 | 0.7 | 3.72
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18344.88 | 12861.94 | 5482.94 | 0.7 | 3.72
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24685.41 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42844.86 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18406.09 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18338.55 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18335.16 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18345.7 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36452.13 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18346.08 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18341.35 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 18440.71 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1145.05 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.7 | 2954.03 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.21 | 1373.76 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.92 | 1051.65 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1019.7 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1013.03 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.56 | 1782.69 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.81 | 941.85 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.81 | 937.65 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.81 | 944.41 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 35762.6024 | 53.9707 | 202.2965 | 0 | 0.0004 | 1008740 | 14613.0264
February | 29260.8534 | 45.944 | 182.2996 | 0 | 0.0003 | 909106.3151 | 12141.9007
March | 33221.6496 | 52.1765 | 207.1023 | 0 | 0.0004 | 1032800 | 13786.8454
April | 31945.9096 | 51.9489 | 215.8423 | 0 | 0.0004 | 1076450 | 13442.0094
May | 35448.6194 | 57.9751 | 242.6132 | 0 | 0.0005 | 1209970 | 14950.1923
June | 41051.2469 | 67.3178 | 282.6475 | 0 | 0.0005 | 1409640 | 17331.7417
July | 43705.6277 | 71.6741 | 300.9563 | 0 | 0.0006 | 1500950 | 18452.777
August | 44559.12 | 73.0737 | 306.8334 | 0 | 0.0006 | 1530260 | 18813.1266
September | 38627.0878 | 63.3446 | 265.9761 | 0 | 0.0005 | 1326500 | 16308.4834
October | 33591.9558 | 54.7039 | 227.6998 | 0 | 0.0004 | 1135590 | 14142.7618
November | 30481.053 | 48.3861 | 194.8471 | 0 | 0.0004 | 971699.9187 | 12702.9151
December | 34640.9609 | 52.8952 | 201.753 | 0 | 0.0004 | 1006060 | 14218.8605
Annual Sum or Average | 432296.6863 | 693.4107 | 2830.8671 | 0 | 0.0053 | 14117800 | 180904.6402
Minimum of Months | 29260.8534 | 45.944 | 182.2996 | 0 | 0.0003 | 909106.3151 | 12141.9007
Maximum of Months | 44559.12 | 73.0737 | 306.8334 | 0 | 0.0006 | 1530260 | 18813.1266
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 132371000000 | 100612.247 | 18-JAN-16:49 | 72368.391 | 8089.532 | 13163.823 | 0 | 1117.501 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119297000000 | 104217.394 | 08-FEB-17:10 | 72368.391 | 8089.532 | 13163.823 | 0 | 4722.648 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 135528000000 | 113272.589 | 31-MAR-15:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 19650.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 141256000000 | 136481.517 | 21-APR-14:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 42859.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 158778000000 | 148250.891 | 31-MAY-15:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 54629.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 184979000000 | 169167.06 | 27-JUN-15:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 75545.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 196961000000 | 167768.897 | 24-JUL-15:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 74147.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 200807000000 | 164998.04 | 05-AUG-12:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 71376.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 174068000000 | 161068.407 | 01-SEP-14:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 67446.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 149016000000 | 138391.488 | 03-OCT-14:00 | 72368.391 | 8089.532 | 13163.823 | 0 | 44769.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 127510000000 | 109745.206 | 10-NOV-16:40 | 72368.391 | 8089.532 | 13163.823 | 0 | 10250.46 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 132019000000 | 106113.684 | 05-DEC-16:30 | 72368.391 | 8089.532 | 13163.823 | 0 | 6618.938 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1852590000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119297000000 | 100612.247 |  | 72368.391 | 8089.532 | 13163.823 | 0 | 1117.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 200807000000 | 169167.06 |  | 72368.391 | 8089.532 | 13163.823 | 0 | 75545.314 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 50992.2 | 3105.52 | 0 | 54097.72
Cost per Total Building Area ($/m2) | 24.39 | 1.49 | 0 | 25.88
Cost per Net Conditioned Building Area ($/m2) | 24.39 | 1.49 | 0 | 25.88

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2080.96 | 995.52 | 995.52
Net Site Energy | 2080.96 | 995.52 | 995.52
Total Source Energy | 5345.4 | 2557.22 | 2557.22
Net Source Energy | 5345.4 | 2557.22 | 2557.22
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 546.77 | 0 | 0 | 0 | 0
Cooling | 30.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 208.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1534.19 | 546.77 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.392 | 0.253 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12953.29 | 10060.9 | 2892.4 | 0.78 | 3.96
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35338.16 | 28223.01 | 7115.15 | 0.8 | 3.73
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17435.14 | 13903.37 | 3531.77 | 0.8 | 4.01
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13674.49 | 10700.9 | 2973.58 | 0.78 | 3.98
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13294.02 | 10379.78 | 2914.24 | 0.78 | 3.97
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13213.72 | 10312.08 | 2901.64 | 0.78 | 3.97
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23290.85 | 17993.85 | 5296.99 | 0.77 | 3.69
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12136.48 | 9407.16 | 2729.32 | 0.78 | 3.95
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12080.69 | 9360.46 | 2720.22 | 0.77 | 3.95
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 12103.59 | 9379.67 | 2723.92 | 0.77 | 3.95
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 19904.94 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34726.81 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15019.26 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14972 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14969.58 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14977.5 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29769.23 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14977.78 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14974.03 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15042.63 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.74 | 853.45 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.13 | 2334.65 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1195.88 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.79 | 916.18 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.76 | 886.24 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.76 | 879.93 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.31 | 1489.13 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.69 | 795.95 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 791.63 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.68 | 793.41 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16431.7696 | 14.3389 | 103.6894 | 0 | 0.0001 | 625480.2329 | 6003.4152
February | 12903.4835 | 11.1899 | 93.9554 | 0 | 0 | 566824.101 | 4752.5715
March | 14662.8766 | 12.7219 | 105.6587 | 0 | 0.0001 | 637424.7022 | 5397.2069
April | 13234.8922 | 11.455 | 100.3577 | 0 | 0.0001 | 605465.7047 | 4886.8058
May | 12915.6415 | 11.1412 | 104.644 | 0 | 0.0001 | 631352.5397 | 4789.3898
June | 12294.9956 | 10.5879 | 102.8358 | 0 | 0 | 620455.5462 | 4569.0665
July | 12254.7912 | 10.5387 | 105.1077 | 0 | 0 | 634172.8088 | 4562.0833
August | 12790.9929 | 11.0036 | 109.0295 | 0 | 0.0001 | 657832.684 | 4759.6288
September | 12320.9314 | 10.5942 | 105.9226 | 0 | 0 | 639090.2402 | 4587.4607
October | 12816.3946 | 11.0451 | 105.7308 | 0 | 0.0001 | 637916.8181 | 4758.3561
November | 12997.2733 | 11.2416 | 99.9418 | 0 | 0 | 602962.5504 | 4803.2968
December | 15831.1834 | 13.7954 | 103.3611 | 0 | 0.0001 | 623517.1702 | 5794.5499
Annual Sum or Average | 161455.2258 | 139.6533 | 1240.2344 | 0 | 0.0006 | 7482500 | 59663.8313
Minimum of Months | 12254.7912 | 10.5387 | 93.9554 | 0 | 0 | 566824.101 | 4562.0833
Maximum of Months | 16431.7696 | 14.3389 | 109.0295 | 0 | 0.0001 | 657832.684 | 6003.4152
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 128247000000 | 97337.061 | 06-JAN-17:10 | 72368.391 | 8089.532 | 10936.459 | 0 | 69.68 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 116220000000 | 105858.841 | 15-FEB-15:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 14464.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 130696000000 | 97267.382 | 01-MAR-17:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 124143000000 | 110342.038 | 29-APR-13:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 18947.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 129451000000 | 112179.37 | 17-MAY-13:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 20784.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 127217000000 | 113529.922 | 15-JUN-12:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 22135.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 130029000000 | 122086.465 | 03-JUL-12:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 30692.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 134880000000 | 118018.721 | 15-AUG-11:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 26624.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 131038000000 | 132085.062 | 28-SEP-14:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 40690.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 130797000000 | 111829.161 | 13-OCT-14:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 20434.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 123630000000 | 97909.635 | 13-NOV-16:00 | 72368.391 | 8089.532 | 10936.459 | 0 | 642.254 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 127844000000 | 97267.382 | 01-DEC-16:49 | 72368.391 | 8089.532 | 10936.459 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1534190000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 116220000000 | 97267.382 |  | 72368.391 | 8089.532 | 10936.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 134880000000 | 132085.062 |  | 72368.391 | 8089.532 | 10936.459 | 0 | 40690.681 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 63404.35 | 4682.41 | 0 | 68086.75
Cost per Total Building Area ($/m2) | 30.33 | 2.24 | 0 | 32.57
Cost per Net Conditioned Building Area ($/m2) | 30.33 | 2.24 | 0 | 32.57

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2856.13 | 1366.36 | 1366.36
Net Site Energy | 2856.13 | 1366.36 | 1366.36
Total Source Energy | 7428.82 | 3553.92 | 3553.92
Net Source Energy | 7428.82 | 3553.92 | 3553.92
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1121.05 | 0 | 0 | 0 | 0
Cooling | 194.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 245.97 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1735.08 | 1121.05 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.355 | 0.274 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.355 | 0.274 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.355 | 0.274 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.355 | 0.274 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.355 | 0.274 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27644.09 | 18689.71 | 8954.39 | 0.68 | 3.44
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 58917.12 | 40025.09 | 18892.03 | 0.68 | 3.19
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22845.85 | 16440.42 | 6405.43 | 0.72 | 3.55
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22158.41 | 14980.93 | 7177.48 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21519.71 | 14549.11 | 6970.59 | 0.68 | 3.45
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21401.24 | 14469.02 | 6932.22 | 0.68 | 3.45
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37605.58 | 25424.5 | 12181.08 | 0.68 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19588.48 | 13243.44 | 6345.04 | 0.68 | 3.45
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19489.53 | 13176.54 | 6312.98 | 0.68 | 3.45
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19560.39 | 13224.45 | 6335.94 | 0.68 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35664.66 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 62710.5 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27267.63 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27208.56 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27205.67 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27215.83 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 54211.22 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27216.15 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27210.88 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27293.5 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1268.18 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.4 | 2629.27 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.08 | 1234.26 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1016.52 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.87 | 1005.17 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.86 | 999.64 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.51 | 1725.17 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.79 | 914.97 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.78 | 910.35 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.79 | 913.65 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37379.3431 | 58.2645 | 134.5258 | 0 | 0.0006 | 8362.0374 | 15162.202
February | 31838.598 | 50.8348 | 121.2489 | 0 | 0.0005 | 7537.3479 | 13025.0608
March | 29699.6172 | 51.6786 | 136.6195 | 0 | 0.0006 | 8494.8283 | 12539.4418
April | 24571.5114 | 45.5775 | 128.612 | 0 | 0.0005 | 7998.0196 | 10632.3487
May | 24714.3458 | 48.37 | 143.3154 | 0 | 0.0006 | 8913.2344 | 10925.2617
June | 28080.9201 | 56.071 | 168.9785 | 0 | 0.0007 | 10509.638 | 12515.1846
July | 30265.3921 | 60.5006 | 182.4976 | 0 | 0.0007 | 11350.4817 | 13494.9588
August | 31189.3967 | 62.3245 | 187.9412 | 0 | 0.0008 | 11689.0431 | 13904.8407
September | 25502.2246 | 50.7095 | 152.288 | 0 | 0.0006 | 9471.5076 | 11346.4783
October | 25415.0694 | 48.3712 | 139.8129 | 0 | 0.0006 | 8694.9829 | 11109.7327
November | 26971.3157 | 48.0354 | 130.1656 | 0 | 0.0005 | 8093.9603 | 11488.4859
December | 34445.5287 | 55.4474 | 133.6628 | 0 | 0.0006 | 8309.2568 | 14132.7165
Annual Sum or Average | 350073.2628 | 636.1851 | 1759.6681 | 0 | 0.0072 | 109424.3381 | 150276.7126
Minimum of Months | 24571.5114 | 45.5775 | 121.2489 | 0 | 0.0005 | 7537.3479 | 10632.3487
Maximum of Months | 37379.3431 | 62.3245 | 187.9412 | 0 | 0.0008 | 11689.0431 | 15162.202
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 132592000000 | 98948.107 | 02-JAN-16:49 | 72368.391 | 8089.532 | 12617.184 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119515000000 | 98948.107 | 01-FEB-17:30 | 72368.391 | 8089.532 | 12617.184 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 134697000000 | 116625.63 | 09-MAR-15:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 23550.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 126820000000 | 117283.679 | 04-APR-15:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 24208.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 141332000000 | 136529.123 | 31-MAY-15:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 43454.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 166645000000 | 163425.606 | 30-JUN-15:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 70350.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 179978000000 | 168948.82 | 25-JUL-12:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 75873.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 185346000000 | 169033.492 | 17-AUG-14:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 75958.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 150184000000 | 147246.098 | 09-SEP-14:30 | 72368.391 | 8089.532 | 12617.184 | 0 | 54170.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 137871000000 | 131036.744 | 20-OCT-15:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 37961.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 128341000000 | 121707.243 | 04-NOV-13:00 | 72368.391 | 8089.532 | 12617.184 | 0 | 28632.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 131755000000 | 98948.107 | 01-DEC-16:40 | 72368.391 | 8089.532 | 12617.184 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1735080000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119515000000 | 98948.107 |  | 72368.391 | 8089.532 | 12617.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 185346000000 | 169033.492 |  | 72368.391 | 8089.532 | 12617.184 | 0 | 75958.385 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 37084.61 | 10826.24 | 0 | 47910.84
Cost per Total Building Area ($/m2) | 17.74 | 5.18 | 0 | 22.92
Cost per Net Conditioned Building Area ($/m2) | 17.74 | 5.18 | 0 | 22.92

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2474.96 | 1184.01 | 1184.01
Net Site Energy | 2474.96 | 1184.01 | 1184.01
Total Source Energy | 6446.4 | 3083.93 | 3083.93
Net Source Energy | 6446.4 | 3083.93 | 3083.93
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 793.13 | 0 | 0 | 0 | 0
Cooling | 138.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 248.56 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1681.83 | 793.13 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.362 | 0.225 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.362 | 0.225 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.362 | 0.225 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.362 | 0.225 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.362 | 0.225 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19625.27 | 15183.78 | 4441.48 | 0.77 | 3.7
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41566.61 | 33197.39 | 8369.22 | 0.8 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20022.7 | 15991.24 | 4031.47 | 0.8 | 3.77
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15434.49 | 12110.62 | 3323.87 | 0.78 | 3.97
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14980.56 | 11724.93 | 3255.63 | 0.78 | 3.98
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14893.98 | 11647.66 | 3246.32 | 0.78 | 3.98
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26574.17 | 20447.76 | 6126.4 | 0.77 | 3.69
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13739.03 | 10622.2 | 3116.84 | 0.77 | 3.95
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13679.89 | 10569.97 | 3109.92 | 0.77 | 3.95
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13707.47 | 10594.34 | 3113.14 | 0.77 | 3.95
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28809.92 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 50471.45 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21910.66 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21849.35 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21846.44 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21857.78 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 43468.3 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21858.1 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21851.7 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21937.05 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1258.86 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.51 | 2746.14 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.21 | 1377.94 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1021.71 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.87 | 1004.07 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.86 | 996.45 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.48 | 1683.58 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.77 | 895.88 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.77 | 890.79 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.77 | 893.17 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44143.3182 | 69.6683 | 160.3937 | 0 | 0.0006 | 166735.5106 | 18181.4264
February | 37970.9684 | 61.1949 | 144.8297 | 0 | 0.0006 | 150566.2793 | 15763.5828
March | 40936.3779 | 67.2708 | 163.159 | 0 | 0.0006 | 169631.4313 | 17121.863
April | 36456.8966 | 61.9832 | 156.5282 | 0 | 0.0006 | 162752.7145 | 15451.6868
May | 39140.455 | 68.0783 | 176.3452 | 0 | 0.0007 | 183368.0686 | 16739.4005
June | 40731.551 | 71.3979 | 186.5024 | 0 | 0.0007 | 193933.3211 | 17474.0343
July | 43209.9115 | 75.8117 | 198.2267 | 0 | 0.0008 | 206125.218 | 18544.0836
August | 43374.8799 | 76.0882 | 198.9132 | 0 | 0.0008 | 206838.9812 | 18613.6078
September | 38952.5473 | 68.2086 | 177.973 | 0 | 0.0007 | 185063.5818 | 16703.8792
October | 37598.2124 | 64.2311 | 163.0926 | 0 | 0.0006 | 169580.1706 | 15965.5735
November | 39016.2916 | 63.853 | 154.0851 | 0 | 0.0006 | 160195.686 | 16293.0232
December | 44465.4738 | 69.9281 | 160.2185 | 0 | 0.0006 | 166551.4761 | 18289.7263
Annual Sum or Average | 485996.8835 | 817.7141 | 2040.2673 | 0 | 0.008 | 2121340 | 205141.8874
Minimum of Months | 36456.8966 | 61.1949 | 144.8297 | 0 | 0.0006 | 150566.2793 | 15451.6868
Maximum of Months | 44465.4738 | 76.0882 | 198.9132 | 0 | 0.0008 | 206838.9812 | 18613.6078
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 132190000000 | 99099.498 | 02-JAN-17:10 | 72368.391 | 8089.532 | 12768.575 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119371000000 | 102713.94 | 14-FEB-15:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 9487.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 134486000000 | 103549.711 | 02-MAR-15:09 | 72368.391 | 8089.532 | 12768.575 | 0 | 10323.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 129032000000 | 119366.385 | 22-APR-13:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 26139.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 145376000000 | 126527.182 | 31-MAY-15:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 33300.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 153753000000 | 137320.64 | 29-JUN-14:09 | 72368.391 | 8089.532 | 12768.575 | 0 | 44094.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 163419000000 | 140832.785 | 31-JUL-14:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 47606.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 163984000000 | 139872.384 | 01-AUG-14:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 46645.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 146721000000 | 128611.416 | 02-SEP-14:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 35384.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 134445000000 | 116681.127 | 13-OCT-14:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 23454.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 127005000000 | 102192.507 | 08-NOV-17:10 | 72368.391 | 8089.532 | 12768.575 | 0 | 3093.01 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 132044000000 | 99099.498 | 01-DEC-16:00 | 72368.391 | 8089.532 | 12768.575 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1681830000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119371000000 | 99099.498 |  | 72368.391 | 8089.532 | 12768.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 163984000000 | 140832.785 |  | 72368.391 | 8089.532 | 12768.575 | 0 | 47606.287 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17444.28 | 5448.28 | 0 | 22892.56
Cost per Total Building Area ($/m2) | 8.35 | 2.61 | 0 | 10.95
Cost per Net Conditioned Building Area ($/m2) | 8.35 | 2.61 | 0 | 10.95

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2556.42 | 1222.98 | 1222.98
Net Site Energy | 2556.42 | 1222.98 | 1222.98
Total Source Energy | 3796.55 | 1816.25 | 1816.25
Net Source Energy | 3796.55 | 1816.25 | 1816.25
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1010.37 | 0 | 0 | 0 | 0
Cooling | 33.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 218.01 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1546.05 | 1010.37 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 4.092 | 0.392 | 0.253 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 4.092 | 0.392 | 0.253 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 4.092 | 0.392 | 0.253 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16094.38 | 12226.58 | 3867.8 | 0.76 | 3.9
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37366.49 | 29215.15 | 8151.33 | 0.78 | 3.68
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18668.32 | 14583.16 | 4085.16 | 0.78 | 3.95
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14839.65 | 11330.98 | 3508.66 | 0.76 | 3.92
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14448.59 | 11001.86 | 3446.73 | 0.76 | 3.91
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14367.94 | 10934.06 | 3433.88 | 0.76 | 3.91
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25586.36 | 19234.63 | 6351.73 | 0.75 | 3.64
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13270.24 | 10014.68 | 3255.55 | 0.75 | 3.89
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13212.61 | 9966.61 | 3246.01 | 0.75 | 3.89
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 13249.56 | 9997.46 | 3252.11 | 0.75 | 3.89
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27758.37 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 48761.94 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21206.17 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21156.15 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21153.65 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21162.41 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42128.08 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21162.69 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21158.16 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21228.04 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.87 | 1008.18 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.15 | 2355.84 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.07 | 1223.64 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.81 | 940.56 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.78 | 909.96 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.78 | 903.66 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.35 | 1536.19 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.71 | 818.61 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 814.18 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.7 | 817.02 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 15794.397 | 18.6994 | 27.9202 | 0 | 0.0001 | 368411.735 | 5933.6938
February | 12090.9224 | 14.9013 | 25.1182 | 0 | 0.0001 | 331583.3868 | 4605.1753
March | 13043.4179 | 16.2656 | 28.313 | 0 | 0.0001 | 373796.8305 | 4988.358
April | 10278.9485 | 13.4804 | 26.54 | 0 | 0.0001 | 350522.6017 | 4002.026
May | 8473.5245 | 12.0322 | 27.7497 | 0 | 0.0001 | 366654.3862 | 3397.5851
June | 7436.3942 | 11.0462 | 27.461 | 0 | 0.0001 | 362903.3247 | 3033.8616
July | 7087.0281 | 10.9431 | 28.8255 | 0 | 0.0001 | 380985.1995 | 2935.8595
August | 7238.2564 | 11.2714 | 30.046 | 0 | 0.0001 | 397126.3103 | 3008.6619
September | 7730.6596 | 11.3946 | 27.9811 | 0 | 0.0001 | 369766.3722 | 3144.4112
October | 9341.4822 | 12.7849 | 27.5291 | 0 | 0.0001 | 363675.0624 | 3694.2239
November | 12684.4146 | 15.7113 | 26.8529 | 0 | 0.0001 | 354498.9816 | 4839.6398
December | 15744.1702 | 18.6461 | 27.8709 | 0 | 0.0001 | 367762.5811 | 5915.4866
Annual Sum or Average | 126943.6156 | 167.1766 | 332.2075 | 0 | 0.0014 | 4387690 | 49498.9827
Minimum of Months | 7087.0281 | 10.9431 | 25.1182 | 0 | 0.0001 | 331583.3868 | 2935.8595
Maximum of Months | 15794.397 | 18.6994 | 30.046 | 0 | 0.0001 | 397126.3103 | 5933.6938
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 129814000000 | 97658.758 | 02-JAN-16:30 | 72368.391 | 8089.532 | 11327.836 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 116837000000 | 97760.459 | 21-FEB-17:40 | 72368.391 | 8089.532 | 11327.836 | 0 | 101.701 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 131711000000 | 98792.371 | 29-MAR-15:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 7006.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 123510000000 | 103853.986 | 29-APR-14:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 12068.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 129195000000 | 110836.414 | 05-MAY-15:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 19050.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 127873000000 | 115698.569 | 28-JUN-14:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 23912.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 134244000000 | 125666.813 | 24-JUL-14:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 33881.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 139932000000 | 121796.447 | 07-AUG-14:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 30010.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 130291000000 | 136603.344 | 02-SEP-15:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 44817.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 128145000000 | 102601.171 | 17-OCT-14:00 | 72368.391 | 8089.532 | 11327.836 | 0 | 10815.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 124912000000 | 98299.708 | 04-NOV-16:49 | 72368.391 | 8089.532 | 11327.836 | 0 | 640.949 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 129585000000 | 97658.758 | 01-DEC-16:19 | 72368.391 | 8089.532 | 11327.836 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1546050000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 116837000000 | 97658.758 |  | 72368.391 | 8089.532 | 11327.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 139932000000 | 136603.344 |  | 72368.391 | 8089.532 | 11327.836 | 0 | 44817.586 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 32443.62 | 8500.91 | 0 | 40944.53
Cost per Total Building Area ($/m2) | 15.52 | 4.07 | 0 | 19.59
Cost per Net Conditioned Building Area ($/m2) | 15.52 | 4.07 | 0 | 19.59

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3305.86 | 1581.51 | 1581.51
Net Site Energy | 3305.86 | 1581.51 | 1581.51
Total Source Energy | 7864.13 | 3762.17 | 3762.17
Net Source Energy | 7864.13 | 3762.17 | 3762.17
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1572.31 | 0 | 0 | 0 | 0
Cooling | 148.14 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 290.83 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1733.55 | 1572.31 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37259.71 | 25190.66 | 12069.04 | 0.68 | 3.44
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61842 | 41886.69 | 19955.31 | 0.68 | 3.19
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22389.42 | 16256.23 | 6133.19 | 0.73 | 3.57
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25105.46 | 16973.38 | 8132.08 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25101.87 | 16970.95 | 8130.92 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25115.61 | 16980.24 | 8135.37 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 49942.45 | 33765.25 | 16177.2 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25115.99 | 16980.5 | 8135.49 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25108.31 | 16975.31 | 8133 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25214.35 | 17047 | 8167.35 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46787.21 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 82364.62 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35839.35 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35769.52 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35766.27 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35778.71 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 71296.48 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35779.06 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35772.11 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35868.15 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.5 | 1709.3 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.5 | 2737.26 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1236.6 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1151.72 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1151.56 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1152.19 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.01 | 2199.48 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1152.2 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1151.85 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.02 | 1156.72 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 66315.3285 | 102.9573 | 256.6255 | 0 | 0.0008 | 59055.0155 | 27040.3964
February | 56783.7156 | 89.9982 | 230.7657 | 0 | 0.0007 | 53107.4972 | 23329.6805
March | 59047.3658 | 96.7175 | 258.7378 | 0 | 0.0008 | 59550.3512 | 24559.113
April | 49065.2995 | 84.8853 | 242.0826 | 0 | 0.0007 | 55724.3749 | 20839.3304
May | 50081.6631 | 89.8836 | 266.5198 | 0 | 0.0008 | 61354.1748 | 21580.7796
June | 55384.0046 | 100.7202 | 302.6519 | 0 | 0.0009 | 69673.7375 | 23991.8528
July | 60592.0129 | 110.3129 | 331.8396 | 0 | 0.001 | 76393.221 | 26259.5259
August | 59765.771 | 108.7835 | 327.1639 | 0 | 0.001 | 75316.7727 | 25899.0425
September | 50354.3447 | 91.2843 | 273.4335 | 0 | 0.0008 | 62946.9546 | 21785.4041
October | 49718.0409 | 87.681 | 255.2927 | 0 | 0.0008 | 58767.5623 | 21275.8905
November | 53610.3195 | 89.5415 | 245.2821 | 0 | 0.0008 | 56456.2454 | 22463.0974
December | 63553.9993 | 100.2208 | 255.2355 | 0 | 0.0008 | 58737.9948 | 26062.7097
Annual Sum or Average | 674271.8653 | 1152.9861 | 3245.6305 | 0 | 0.01 | 747083.9019 | 285086.8227
Minimum of Months | 49065.2995 | 84.8853 | 230.7657 | 0 | 0.0007 | 53107.4972 | 20839.3304
Maximum of Months | 66315.3285 | 110.3129 | 331.8396 | 0 | 0.001 | 76393.221 | 27040.3964
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 137033000000 | 101129.812 | 02-JAN-16:30 | 72368.391 | 8089.532 | 14798.889 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 123232000000 | 101129.812 | 01-FEB-16:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 138182000000 | 106253.861 | 31-MAR-14:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 10997.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 129304000000 | 108152.001 | 07-APR-14:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 12895.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 142368000000 | 139324.114 | 30-MAY-15:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 44067.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 161673000000 | 164954.305 | 08-JUN-12:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 69697.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 177265000000 | 167430.645 | 13-JUL-14:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 72173.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 174767000000 | 165945.674 | 04-AUG-15:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 70688.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 146064000000 | 142834.301 | 27-SEP-14:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 47577.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 136366000000 | 121497.155 | 31-OCT-16:49 | 72368.391 | 8089.532 | 14798.889 | 0 | 20367.343 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 131002000000 | 120498.229 | 02-NOV-14:00 | 72368.391 | 8089.532 | 14798.889 | 0 | 25241.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 136297000000 | 101129.812 | 01-DEC-16:19 | 72368.391 | 8089.532 | 14798.889 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1733550000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 123232000000 | 101129.812 |  | 72368.391 | 8089.532 | 14798.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 177265000000 | 167430.645 |  | 72368.391 | 8089.532 | 14798.889 | 0 | 72173.833 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43850.58 | 13052.05 | 0 | 56902.64
Cost per Total Building Area ($/m2) | 20.98 | 6.24 | 0 | 27.22
Cost per Net Conditioned Building Area ($/m2) | 20.98 | 6.24 | 0 | 27.22

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2814.75 | 1346.56 | 1346.56
Net Site Energy | 2814.75 | 1346.56 | 1346.56
Total Source Energy | 6789.44 | 3248.04 | 3248.04
Net Source Energy | 6789.44 | 3248.04 | 3248.04
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1145.5 | 0 | 0 | 0 | 0
Cooling | 90.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 283.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1669.25 | 1145.5 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.354 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.354 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.354 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27144.69 | 20604.51 | 6540.18 | 0.76 | 3.66
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40341.5 | 32218.95 | 8122.55 | 0.8 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18539.93 | 14807.01 | 3732.92 | 0.8 | 4.01
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17468.8 | 13519.65 | 3949.15 | 0.77 | 3.93
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17639.7 | 13592.31 | 4047.4 | 0.77 | 3.92
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17691.32 | 13618.6 | 4072.72 | 0.77 | 3.92
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 36620.94 | 27685.63 | 8935.31 | 0.76 | 3.61
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18232.16 | 13851.81 | 4380.35 | 0.76 | 3.88
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18254.38 | 13859.04 | 4395.35 | 0.76 | 3.88
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18336.4 | 13924.06 | 4412.35 | 0.76 | 3.88
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38051.14 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 66853.93 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29068.69 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29001.56 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28998.45 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29011 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57757.89 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29011.34 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29004.05 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29096.1 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.46 | 1666.89 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.44 | 2665.2 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1275.89 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1121.34 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1121.15 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1121.91 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.96 | 2138.74 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1121.93 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.98 | 1121.49 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1127.04 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47980.9089 | 73.9668 | 164.8217 | 0 | 0.0007 | 171324.6416 | 19589.5743
February | 41686.1174 | 65.2263 | 148.4128 | 0 | 0.0006 | 154276.465 | 17114.0501
March | 44153.0756 | 70.9651 | 167.3647 | 0 | 0.0007 | 173992.3687 | 18311.1364
April | 38194.7801 | 63.8001 | 157.8318 | 0 | 0.0006 | 164100.3954 | 16076.6599
May | 38437.1915 | 65.7393 | 167.1377 | 0 | 0.0007 | 173786.7199 | 16329.1895
June | 38580.4227 | 67.1872 | 174.2712 | 0 | 0.0007 | 181211.9892 | 16508.029
July | 41865.5872 | 73.4405 | 191.9912 | 0 | 0.0007 | 199641.1553 | 17965.9102
August | 42471.0751 | 74.4376 | 194.4161 | 0 | 0.0008 | 202162.2424 | 18219.3691
September | 38257.7555 | 66.2598 | 170.8354 | 0 | 0.0007 | 177637.0581 | 16334.1131
October | 39267.0943 | 66.1941 | 165.5255 | 0 | 0.0007 | 172103.9813 | 16587.1389
November | 41784.4363 | 67.0892 | 158.0132 | 0 | 0.0006 | 164270.0127 | 17322.0551
December | 48350.7435 | 74.2392 | 164.4808 | 0 | 0.0007 | 170967.7096 | 19711.3667
Annual Sum or Average | 501029.188 | 828.5453 | 2025.1021 | 0 | 0.008 | 2105470 | 210068.5924
Minimum of Months | 38194.7801 | 63.8001 | 148.4128 | 0 | 0.0006 | 154276.465 | 16076.6599
Maximum of Months | 48350.7435 | 74.4376 | 194.4161 | 0 | 0.0008 | 202162.2424 | 19711.3667
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 135828000000 | 101173.992 | 27-JAN-17:10 | 72368.391 | 8089.532 | 14481.562 | 0 | 361.506 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 122312000000 | 100838.672 | 11-FEB-17:30 | 72368.391 | 8089.532 | 14481.562 | 0 | 26.186 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 137943000000 | 107523.007 | 30-MAR-16:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 12583.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 130101000000 | 113354.672 | 25-APR-14:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 18415.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 137780000000 | 121603.623 | 23-MAY-15:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 26664.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 143667000000 | 132480.953 | 27-JUN-15:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 37541.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 158278000000 | 139292.035 | 17-JUL-15:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 44352.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 160277000000 | 140832.834 | 30-AUG-13:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 45893.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 140833000000 | 131391.446 | 02-SEP-14:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 36451.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 136446000000 | 120475.833 | 05-OCT-14:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 25536.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 130235000000 | 102828.515 | 04-NOV-16:00 | 72368.391 | 8089.532 | 14481.562 | 0 | 2016.029 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 135545000000 | 100812.485 | 01-DEC-16:40 | 72368.391 | 8089.532 | 14481.562 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1669250000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 122312000000 | 100812.485 |  | 72368.391 | 8089.532 | 14481.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 160277000000 | 140832.834 |  | 72368.391 | 8089.532 | 14481.562 | 0 | 45893.349 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17315.23 | 7907.62 | 0 | 25222.86
Cost per Total Building Area ($/m2) | 8.28 | 3.78 | 0 | 12.07
Cost per Net Conditioned Building Area ($/m2) | 8.28 | 3.78 | 0 | 12.07

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3804.2 | 1819.92 | 1819.92
Net Site Energy | 3804.2 | 1819.92 | 1819.92
Total Source Energy | 8253.87 | 3948.62 | 3948.62
Net Source Energy | 8253.87 | 3948.62 | 3948.62
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2055.94 | 0 | 0 | 0 | 0
Cooling | 122.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 331.3 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1748.26 | 2055.94 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42019.25 | 28408.51 | 13610.74 | 0.68 | 3.21
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 60039.68 | 43110.36 | 16929.33 | 0.72 | 3.27
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23356.75 | 17072.01 | 6284.75 | 0.73 | 3.58
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26400.62 | 18365.84 | 8034.78 | 0.7 | 3.49
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28506.05 | 19272.46 | 9233.59 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28520.12 | 19281.97 | 9238.15 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 56748.03 | 38366.39 | 18381.64 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28520.48 | 19282.22 | 9238.26 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28512.01 | 19276.49 | 9235.52 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28609.83 | 19342.63 | 9267.2 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 52386.71 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 92428.01 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40299.17 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40232.9 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40229.88 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40242.53 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 80223.2 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40242.85 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40235.24 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 40323.16 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.69 | 1927.65 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.83 | 3096.74 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1311.26 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1307.88 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1307.72 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1308.37 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.29 | 2499.2 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1308.39 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1308 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1312.49 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 58407.9423 | 81.537 | 93.1344 | 0 | 0.0007 | 61129.0912 | 22941.2026
February | 48124.0776 | 69.2449 | 83.4572 | 0 | 0.0007 | 54791.6889 | 19099.2503
March | 43846.2554 | 68.2339 | 92.7891 | 0 | 0.0007 | 60951.0283 | 17893.2114
April | 33965.6112 | 57.495 | 86.9795 | 0 | 0.0006 | 57159.023 | 14304.2972
May | 33533.6289 | 60.0114 | 96.4482 | 0 | 0.0007 | 63395.4172 | 14432.8056
June | 35349.4643 | 64.3517 | 105.2223 | 0 | 0.0008 | 69166.7934 | 15318.5917
July | 37503.6768 | 68.3925 | 112.0228 | 0 | 0.0008 | 73637.4789 | 16263.5099
August | 38326.0379 | 69.918 | 114.5632 | 0 | 0.0008 | 75307.5089 | 16622.5951
September | 31418.3771 | 56.5854 | 91.5349 | 0 | 0.0007 | 60167.2839 | 13556.7666
October | 34871.5133 | 59.3454 | 90.3317 | 0 | 0.0007 | 59363.2797 | 14716.1137
November | 41328.5298 | 64.4525 | 87.9061 | 0 | 0.0007 | 57744.2577 | 16878.8217
December | 53658.6833 | 76.9837 | 92.3231 | 0 | 0.0007 | 60610.9506 | 21274.3023
Annual Sum or Average | 490333.7979 | 796.5513 | 1146.7123 | 0 | 0.0086 | 753423.8017 | 203301.4682
Minimum of Months | 31418.3771 | 56.5854 | 83.4572 | 0 | 0.0006 | 54791.6889 | 13556.7666
Maximum of Months | 58407.9423 | 81.537 | 114.5632 | 0 | 0.0008 | 75307.5089 | 22941.2026
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 141845000000 | 103018.616 | 02-JAN-16:40 | 72368.391 | 8089.532 | 16687.693 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 127140000000 | 103018.616 | 01-FEB-17:19 | 72368.391 | 8089.532 | 16687.693 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 141432000000 | 103018.616 | 01-MAR-17:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 132633000000 | 112879.916 | 01-APR-16:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 15734.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 147104000000 | 163801.98 | 27-MAY-14:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 66656.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 160496000000 | 162343.383 | 29-JUN-14:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 65197.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 170870000000 | 170000.509 | 15-JUL-14:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 72854.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 174745000000 | 161273.864 | 25-AUG-16:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 64128.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 139614000000 | 140488.44 | 14-SEP-14:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 43342.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 137748000000 | 124754.567 | 07-OCT-14:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 27608.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 133991000000 | 103343.572 | 02-NOV-16:00 | 72368.391 | 8089.532 | 16687.693 | 0 | 324.955 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 140643000000 | 103018.616 | 01-DEC-16:30 | 72368.391 | 8089.532 | 16687.693 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1748260000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 127140000000 | 103018.616 |  | 72368.391 | 8089.532 | 16687.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 174745000000 | 170000.509 |  | 72368.391 | 8089.532 | 16687.693 | 0 | 72854.893 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29910.73 | 16188.58 | 0 | 46099.31
Cost per Total Building Area ($/m2) | 14.31 | 7.74 | 0 | 22.05
Cost per Net Conditioned Building Area ($/m2) | 14.31 | 7.74 | 0 | 22.05

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3388.09 | 1620.85 | 1620.85
Net Site Energy | 3388.09 | 1620.85 | 1620.85
Total Source Energy | 7746.08 | 3705.69 | 3705.69
Net Source Energy | 7746.08 | 3705.69 | 3705.69
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1690.82 | 0 | 0 | 0 | 0
Cooling | 53.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 349.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1697.27 | 1690.82 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.385 | 0.305 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30562.44 | 24183.36 | 6379.07 | 0.79 | 3.71
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 50104.12 | 40015.92 | 10088.2 | 0.8 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20394.91 | 16288.5 | 4106.41 | 0.8 | 3.77
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20334.59 | 16240.32 | 4094.26 | 0.8 | 3.77
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20331.91 | 16238.18 | 4093.72 | 0.8 | 3.77
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20343.78 | 16247.67 | 4096.11 | 0.8 | 3.77
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41396.95 | 32711.41 | 8685.54 | 0.79 | 3.43
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20659.39 | 16383.8 | 4275.59 | 0.79 | 3.75
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20675.15 | 16387.88 | 4287.27 | 0.79 | 3.75
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20749.09 | 16449.43 | 4299.66 | 0.79 | 3.75
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 49511.68 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 87211.93 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37989.56 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37916.88 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37913.65 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37927.96 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 75562.85 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37928.29 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37919.42 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38016.69 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.81 | 1978.62 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.03 | 3310.18 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1403.55 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1399.4 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1399.22 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1400.03 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.44 | 2671.95 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1400.05 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1399.55 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1405.1 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 53305.5267 | 77.5958 | 105.8809 | 0 | 0.0008 | 2509450 | 21272.6828
February | 45228.0639 | 67.3154 | 95.1812 | 0 | 0.0007 | 2256190 | 18192.0541
March | 43360.447 | 68.6536 | 106.1431 | 0 | 0.0008 | 2516900 | 17838.8932
April | 37494.7707 | 61.4334 | 99.2598 | 0 | 0.0007 | 2354050 | 15625.506
May | 35660.7266 | 60.8139 | 103.0315 | 0 | 0.0007 | 2443900 | 15091.7766
June | 35326.3808 | 61.825 | 107.7845 | 0 | 0.0007 | 2556880 | 15103.1387
July | 36868.9077 | 65.2844 | 115.2384 | 0 | 0.0008 | 2733820 | 15836.0555
August | 36912.9499 | 65.1709 | 114.6838 | 0 | 0.0008 | 2720630 | 15836.4687
September | 34465.1362 | 59.7811 | 103.216 | 0 | 0.0007 | 2448430 | 14683.056
October | 37421.6813 | 62.3612 | 102.8547 | 0 | 0.0007 | 2439480 | 15696.3038
November | 41750.7904 | 65.6927 | 100.7118 | 0 | 0.0007 | 2388030 | 17136.8118
December | 51021.2731 | 75.373 | 105.3303 | 0 | 0.0008 | 2496650 | 20467.6602
Annual Sum or Average | 488816.6542 | 791.3006 | 1259.3161 | 0 | 0.0089 | 29864400 | 202780.4075
Minimum of Months | 34465.1362 | 59.7811 | 95.1812 | 0 | 0.0007 | 2256190 | 14683.056
Maximum of Months | 53305.5267 | 77.5958 | 115.2384 | 0 | 0.0008 | 2733820 | 21272.6828
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 142618000000 | 104098.567 | 02-JAN-16:49 | 72368.391 | 8089.532 | 17767.644 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 128225000000 | 104098.567 | 01-FEB-17:30 | 72368.391 | 8089.532 | 17767.644 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 143041000000 | 100816.702 | 30-MAR-16:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 2591.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 133786000000 | 98457.974 | 06-APR-16:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 232.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 138893000000 | 117543.814 | 16-MAY-16:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 19318.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 145314000000 | 141978.753 | 30-JUN-15:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 43753.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 155369000000 | 142654.378 | 21-JUL-16:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 44428.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 154620000000 | 138039.957 | 09-AUG-16:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 39814.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 139150000000 | 129546.614 | 01-SEP-16:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 31321.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 138642000000 | 112905.993 | 06-OCT-15:00 | 72368.391 | 8089.532 | 17767.644 | 0 | 14680.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 135718000000 | 104098.567 | 06-NOV-17:10 | 72368.391 | 8089.532 | 17767.644 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 141891000000 | 104098.567 | 01-DEC-16:40 | 72368.391 | 8089.532 | 17767.644 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1697270000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 128225000000 | 98457.974 |  | 72368.391 | 8089.532 | 17767.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 155369000000 | 142654.378 |  | 72368.391 | 8089.532 | 17767.644 | 0 | 44428.811 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 35662.32 | 13660.19 | 0 | 49322.51
Cost per Total Building Area ($/m2) | 17.06 | 6.53 | 0 | 23.6
Cost per Net Conditioned Building Area ($/m2) | 17.06 | 6.53 | 0 | 23.6

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4235.28 | 2026.14 | 2026.14
Net Site Energy | 4235.28 | 2026.14 | 2026.14
Total Source Energy | 8595.13 | 4111.87 | 4111.87
Net Source Energy | 8595.13 | 4111.87 | 4111.87
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2542.23 | 0 | 0 | 0 | 0
Cooling | 41.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 356.64 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1693.05 | 2542.23 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.487 | 0.409 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.487 | 0.409 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.487 | 0.409 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 44911.87 | 30364.16 | 14547.71 | 0.68 | 3.19
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68316.2 | 47889.07 | 20427.13 | 0.7 | 3.24
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27247.52 | 19253.27 | 7994.24 | 0.71 | 3.52
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30358.21 | 20575.91 | 9782.3 | 0.68 | 3.45
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30563.96 | 20663.78 | 9900.18 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30578.57 | 20673.66 | 9904.91 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 60854.96 | 41143.02 | 19711.94 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30578.92 | 20673.89 | 9905.02 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30569.79 | 20667.72 | 9902.07 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30665.4 | 20732.36 | 9933.04 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 54751.05 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 96672.75 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42180.42 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42115.54 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42112.63 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42125.48 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 83985.93 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42125.79 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42117.76 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42201.89 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.81 | 1977.93 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.03 | 3314.44 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1405.67 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1402.28 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1402.13 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1402.8 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.45 | 2680.07 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1402.82 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1402.4 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1406.79 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 59449.9248 | 82.8953 | 94.4824 | 0 | 0.0007 | 62013.19 | 23341.2649
February | 51243.6057 | 72.5743 | 85.0924 | 0 | 0.0007 | 55857.8554 | 20226.504
March | 49686.1552 | 74.1062 | 94.6767 | 0 | 0.0007 | 62174.1982 | 19969.0325
April | 38457.6269 | 61.8814 | 88.0064 | 0 | 0.0007 | 57820.0134 | 15888.5296
May | 34241.3935 | 58.8996 | 90.7394 | 0 | 0.0007 | 59633.9097 | 14510.0833
June | 31713.9293 | 57.0832 | 92.2835 | 0 | 0.0007 | 60659.1913 | 13680.9921
July | 34154.7425 | 62.044 | 101.2337 | 0 | 0.0007 | 66544.4569 | 14788.1713
August | 34327.7357 | 61.9663 | 100.4703 | 0 | 0.0007 | 66041.1891 | 14825.611
September | 32178.5057 | 56.4832 | 88.9587 | 0 | 0.0007 | 58468.3503 | 13744.1201
October | 37024.7636 | 61.5441 | 91.1366 | 0 | 0.0007 | 59886.0382 | 15484.6962
November | 44573.3893 | 67.8989 | 89.5526 | 0 | 0.0007 | 58817.4043 | 18049.7659
December | 56514.8577 | 80.0909 | 94.0121 | 0 | 0.0007 | 61713.4561 | 22312.0247
Annual Sum or Average | 503566.6299 | 797.4673 | 1110.6447 | 0 | 0.0084 | 729629.253 | 206820.7957
Minimum of Months | 31713.9293 | 56.4832 | 85.0924 | 0 | 0.0007 | 55857.8554 | 13680.9921
Maximum of Months | 59449.9248 | 82.8953 | 101.2337 | 0 | 0.0007 | 66544.4569 | 23341.2649
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 143897000000 | 104128.263 | 02-JAN-16:30 | 72368.391 | 8089.532 | 17797.34 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 129614000000 | 104128.263 | 01-FEB-17:10 | 72368.391 | 8089.532 | 17797.34 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 144271000000 | 104128.263 | 01-MAR-17:49 | 72368.391 | 8089.532 | 17797.34 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 134167000000 | 99058.851 | 04-APR-14:00 | 72368.391 | 8089.532 | 17797.34 | 0 | 803.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 138376000000 | 115470.955 | 31-MAY-15:00 | 72368.391 | 8089.532 | 17797.34 | 0 | 17215.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 140755000000 | 140162.779 | 14-JUN-14:00 | 72368.391 | 8089.532 | 17797.34 | 0 | 41907.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 154411000000 | 156760.642 | 08-JUL-15:00 | 72368.391 | 8089.532 | 17797.34 | 0 | 58505.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 153244000000 | 154463.803 | 12-AUG-14:00 | 72368.391 | 8089.532 | 17797.34 | 0 | 56208.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 135671000000 | 129355.061 | 07-SEP-14:00 | 72368.391 | 8089.532 | 17797.34 | 0 | 31099.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 138961000000 | 122935.494 | 07-OCT-14:00 | 72368.391 | 8089.532 | 17797.34 | 0 | 24680.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 136481000000 | 104128.263 | 01-NOV-16:49 | 72368.391 | 8089.532 | 17797.34 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 143201000000 | 104128.263 | 01-DEC-16:19 | 72368.391 | 8089.532 | 17797.34 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1693050000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 129614000000 | 99058.851 |  | 72368.391 | 8089.532 | 17797.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 154411000000 | 156760.642 |  | 72368.391 | 8089.532 | 17797.34 | 0 | 58505.379 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 28460.19 | 19987.73 | 0 | 48447.93
Cost per Total Building Area ($/m2) | 13.62 | 9.56 | 0 | 23.18
Cost per Net Conditioned Building Area ($/m2) | 13.62 | 9.56 | 0 | 23.18

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6009.53 | 2874.94 | 2874.94
Net Site Energy | 6009.53 | 2874.94 | 2874.94
Total Source Energy | 11173.04 | 5345.14 | 5345.14
Net Source Energy | 11173.04 | 5345.14 | 5345.14
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4150.4 | 0 | 0 | 0 | 0
Cooling | 15.78 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 91.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 549.46 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1859.13 | 4150.4 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.616 | 0.541 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.616 | 0.541 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 2.956 | 0.616 | 0.541 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 2.956 | 0.616 | 0.541 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 2.956 | 0.616 | 0.541 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39423.89 | 31486.09 | 7937.79 | 0.8 | 3.73
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 66314.72 | 52962.6 | 13352.12 | 0.8 | 4.32
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27102.77 | 21645.77 | 5457 | 0.8 | 3.77
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27053.45 | 21606.38 | 5447.07 | 0.8 | 3.77
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27051.39 | 21604.74 | 5446.66 | 0.8 | 3.77
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27062.39 | 21613.52 | 5448.87 | 0.8 | 3.77
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 53902.14 | 43049.23 | 10852.91 | 0.8 | 3.45
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27062.6 | 21613.69 | 5448.91 | 0.8 | 3.77
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27054.99 | 21607.61 | 5447.38 | 0.8 | 3.77
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27115.62 | 21656.04 | 5459.59 | 0.8 | 3.77
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 73943.03 | 0.78
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 130728.69 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57075.76 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57008.33 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57005.52 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57020.55 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 113738.21 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57020.84 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57010.44 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57093.33 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.38 | 2604.58 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.01 | 7641.31 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.64 | 1865.18 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.63 | 1861.78 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.63 | 1861.64 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.63 | 1862.4 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.26 | 3561.1 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.63 | 1862.41 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.63 | 1861.89 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.64 | 1866.06 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 74610.484 | 78.8752 | 233.4157 | 0 | 0.0009 | 46804.5158 | 27538.0656
February | 64638.8234 | 68.6485 | 208.8086 | 0 | 0.0008 | 41872.4805 | 23906.079
March | 59052.6456 | 64.5547 | 229.2357 | 0 | 0.0008 | 45981.0435 | 22123.07
April | 43082.2264 | 49.1567 | 210.3459 | 0 | 0.0007 | 42203.5147 | 16457.0893
May | 33120.8229 | 40.2364 | 212.8757 | 0 | 0.0007 | 42721.9208 | 13028.2595
June | 30549.3278 | 37.8715 | 212.2274 | 0 | 0.0007 | 42594.3737 | 12133.5493
July | 31030.537 | 38.6165 | 218.6774 | 0 | 0.0007 | 43889.3555 | 12347.5291
August | 32240.6523 | 39.811 | 220.6892 | 0 | 0.0007 | 44292.1705 | 12781.123
September | 34302.7015 | 41.1483 | 209.5117 | 0 | 0.0007 | 42045.0491 | 13412.5397
October | 46513.3653 | 52.7573 | 220.5225 | 0 | 0.0008 | 44243.9451 | 17719.3909
November | 61318.2261 | 66.229 | 221.2433 | 0 | 0.0008 | 44373.4347 | 22848.3528
December | 69793.2601 | 74.4527 | 232.3647 | 0 | 0.0009 | 46598.4012 | 25863.1923
Annual Sum or Average | 580253.0724 | 652.3579 | 2629.9177 | 0 | 0.0093 | 527620.205 | 220158.2406
Minimum of Months | 30549.3278 | 37.8715 | 208.8086 | 0 | 0.0007 | 41872.4805 | 12133.5493
Maximum of Months | 74610.484 | 78.8752 | 233.4157 | 0 | 0.0009 | 46804.5158 | 27538.0656
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 164921000000 | 113179.271 | 02-JAN-09:09 | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 147542000000 | 113179.271 | 01-FEB-09:09 | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 162019000000 | 113179.271 | 01-MAR-17:00 | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 148709000000 | 107306.271 | 01-APR-09:09 | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 150535000000 | 113763.7 | 30-MAY-16:00 | 72368.391 | 8089.532 | 26848.348 | 0 | 6457.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 150086000000 | 131350.735 | 20-JUN-15:00 | 72368.391 | 8089.532 | 26848.348 | 0 | 24044.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 154649000000 | 139266.485 | 29-JUL-15:00 | 72368.391 | 8089.532 | 26848.348 | 0 | 31960.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 156068000000 | 131551.839 | 15-AUG-14:39 | 72368.391 | 8089.532 | 26848.348 | 0 | 24245.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 148150000000 | 108292.35 | 02-SEP-15:00 | 72368.391 | 8089.532 | 26848.348 | 0 | 986.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 155898000000 | 113179.271 | 23-OCT-08:09 | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 156355000000 | 113179.271 | 01-NOV-08:09 | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 164195000000 | 113179.271 | 01-DEC-09:09 | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1859130000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 147542000000 | 107306.271 |  | 72368.391 | 8089.532 | 26848.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 164921000000 | 139266.485 |  | 72368.391 | 8089.532 | 26848.348 | 0 | 31960.214 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 49454.78 | 17109.81 | 0 | 66564.59
Cost per Total Building Area ($/m2) | 23.66 | 8.19 | 0 | 31.84
Cost per Net Conditioned Building Area ($/m2) | 23.66 | 8.19 | 0 | 31.84

## Picture
DOE Commercial Building Benchmark - Strip Mall

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0