## BuildingSummary
Building Summary Large Office pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Reference Building Large Office Pre-1980
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 46320 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 12 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.38
| East | 0.38
| North | 0.38
| West | 0.38
| Total | 0.38
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11589.72
| Net Dimensions - Total Area (m2) | 6953.64
| Wall to Skin Ratio | 0.765
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3563
| Net Dimensions - Total Area (m2) | 3563
| Roof to Skin Ratio | 0.235
Window Dimensions (m2)
| South | 1390.85
| East | 927.23
| North | 1390.85
| West | 927.23
| Total Area (m2) | 4636.16
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 3563
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 8523.53
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 92640.76
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.36496 | See Reference Buildings Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | 2 water cooled chillers | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | boiler
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 1504.13

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 7.5347 | 10.76 |  |  | 10.001 |  | 958.9195 |  | 0
Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 3.6267
Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 2397.06 |  |  |  | 967.5482 |  |  | 23972.9872
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Underground walls
| Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
| R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER 1 | 1945.6871 | 1905.6581 | 1872.4722 | 1876.4717 | 1613.9673 | 1695.1187 | 1447.6952 | 1875.404 | 1445.1941 | 1544.4306 | 1669.2914 | 1253.0214 | 1653.2841 | 1233.71 | 1432.225 | 1273.4987
| COOLSYS1 CHILLER 2 | 1945.6871 | 1905.6581 | 1872.4722 | 1876.4717 | 1613.9673 | 1695.1187 | 1447.6952 | 1875.404 | 1445.1941 | 1544.4306 | 1669.2914 | 1253.0214 | 1653.2841 | 1233.71 | 1432.225 | 1273.4987
Heating (kW)
| HEATSYS1 BOILER | 3200.1507 | 3579.1921 | 3484.4359 | 3731.1429 | 3160.4302 | 3550.4317 | 3283.8731 | 3929.9826 | 3430.435 | 3668.9932 | 3902.7404 | 3388.2219 | 4089.5019 | 3805.6804 | 4065.4519 | 4775.9897
HVAC Efficiency
Air Conditioning (COP)
| COOLSYS1 CHILLER 1 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11
| COOLSYS1 CHILLER 2 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11
| Heating Efficiency (%) | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 19.53 | 19.89 | 21.37 | 20.63 | 19.38 | 21.84 | 19.33 | 20.35 | 22.52 | 20.36 | 17.86 | 19.43 | 18.07 | 18.99 | 17.71 | 17.84
| VAV_2_FAN | 201.34 | 205.59 | 224.24 | 213.69 | 199.6 | 228.73 | 201.49 | 210.46 | 233.07 | 212.85 | 187.23 | 203.69 | 189.27 | 200.2 | 187.3 | 191.47
| VAV_3_FAN | 20.58 | 21.42 | 23.78 | 22.08 | 19.4 | 23.4 | 18.72 | 20.83 | 22.65 | 20.2 | 17.85 | 18.62 | 18.01 | 17.75 | 16.81 | 16.8
| VAV_5_FAN | 9.52 | 9.4 | 8.12 | 9.48 | 9.13 | 8.08 | 7.04 | 9.01 | 9.68 | 7.85 | 8.93 | 9.57 | 8.91 | 8.95 | 7.95 | 6.78
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.07924 | 0.10194 | 0.072059 | 0.094641 | 0.051424 | 0.092974 | 0.14708 | 0.064038 | 0.036955 | 0.071107 | 0.090613 | 0.036957 | 0.059144 | 0.075629 | 0.059271 | 0.096754
| Total Cost ($/m2) | 16.98 | 20.56 | 14 | 18.02 | 8.87 | 16.25 | 21.93 | 11.76 | 5.69 | 10.25 | 13.77 | 5.28 | 8.84 | 10.43 | 8.11 | 12.77
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01136 | 0.0080626 | 0.0082469 | 0.0096433 | 0.0085594 | 0.0076822 | 0.0085423 | 0.0096904 | 0.0068833 | 0.0084151 | 0.0082874 | 0.0068839 | 0.0078898 | 0.008012 | 0.0078688 | 0.0041129
| Total Cost ($/m2) | 0.13 | 0.43 | 0.33 | 0.97 | 0.32 | 0.44 | 0.66 | 1.63 | 0.68 | 1.48 | 1.47 | 0.78 | 1.96 | 1.47 | 2.43 | 2.27
Total Utility Costs
| Cost Intensity ($/m2) | 17.11 | 20.99 | 14.33 | 18.99 | 9.19 | 16.69 | 22.59 | 13.39 | 6.37 | 11.73 | 15.24 | 6.06 | 10.8 | 11.9 | 10.54 | 15.03
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 3586430.5556 | 3053255.5556 | 2675200 | 2561538.8889 | 1895033.3333 | 1892494.4444 | 966886.1111 | 2260022.2222 | 1103294.4444 | 780336.1111 | 1124527.7778 | 737386.1111 | 1020700 | 550111.1111 | 524097.2222 | 325991.6667
| Interior Lighting | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444
| Exterior Lighting | 269230.5556 | 269127.7778 | 269077.7778 | 269036.1111 | 268830.5556 | 268769.4444 | 268913.8889 | 268750 | 268852.7778 | 268319.4444 | 268791.6667 | 268636.1111 | 268616.6667 | 268555.5556 | 268400 | 266758.3333
| Interior Equipment | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333
| Exterior Equipment | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111
| Fans | 242766.6667 | 228144.4444 | 281252.7778 | 229244.4444 | 199100 | 279555.5556 | 185019.4444 | 227783.3333 | 276661.1111 | 210808.3333 | 197775 | 218430.5556 | 205133.3333 | 210077.7778 | 201144.4444 | 215288.8889
| Pumps | 349536.1111 | 330841.6667 | 314708.3333 | 321158.3333 | 232575 | 250550 | 154841.6667 | 326047.2222 | 161327.7778 | 122402.7778 | 143261.1111 | 112161.1111 | 131947.2222 | 91530.5556 | 83163.8889 | 62800
| Heat Rejection | 273372.2222 | 255555.5556 | 253580.5556 | 237161.1111 | 191616.6667 | 199094.4444 | 126936.1111 | 220188.8889 | 117744.4444 | 91727.7778 | 102102.7778 | 80138.8889 | 95455.5556 | 62669.4444 | 55208.3333 | 37769.4444
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 9925097.2222 | 9340688.8889 | 8997583.3333 | 8821900 | 7990919.4444 | 8094227.7778 | 6906358.3333 | 8506555.5556 | 7131641.6667 | 6677358.3333 | 7040216.6667 | 6620513.8889 | 6925611.1111 | 6386705.5556 | 6335777.7778 | 6112372.2222
Gas (MJ)
| Heating | 417130 | 2323930 | 1734840 | 4449210 | 1525780 | 2484270 | 3355680 | 7573800 | 4378350 | 7891170 | 7960160 | 4975620 | 11220140 | 8234880 | 14010530 | 25185950
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 129190 | 163090 | 143480 | 195790 | 189530 | 167010 | 217530 | 221520 | 216650 | 234970 | 244120 | 242940 | 263660 | 267210 | 295850 | 334820
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 546320 | 2487020 | 1878310 | 4645000 | 1715310 | 2651280 | 3573210 | 7795320 | 4595000 | 8126130 | 8204290 | 5218560 | 11483800 | 8502080 | 14306380 | 25520780
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 36276670 | 36113500 | 34269610 | 36403850 | 30482620 | 31790500 | 28436100 | 38418920 | 30268910 | 32164620 | 33549070 | 29052420 | 36416010 | 31494220 | 37115180 | 47525320
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 278.7358 | 237.2977 | 207.9154 | 199.0817 | 147.2812 | 147.0839 | 75.146 | 175.648 | 85.7476 | 60.6474 | 87.3978 | 57.3093 | 79.3284 | 42.7544 | 40.7326 | 25.3359
| Interior Lighting (elec) | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522
| Exterior Lighting (elec) | 20.9245 | 20.9165 | 20.9126 | 20.9094 | 20.8934 | 20.8886 | 20.8999 | 20.8871 | 20.8951 | 20.8537 | 20.8904 | 20.8783 | 20.8768 | 20.872 | 20.8599 | 20.7323
| Interior Equipment (elec) | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998
| Exterior Equipment (elec) | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124
| Fans (elec) | 18.8677 | 17.7313 | 21.8588 | 17.8168 | 15.474 | 21.7269 | 14.3796 | 17.7032 | 21.502 | 16.3839 | 15.371 | 16.9763 | 15.9429 | 16.3272 | 15.6329 | 16.7322
| Pumps (elec) | 27.1658 | 25.7129 | 24.459 | 24.9603 | 18.0756 | 19.4726 | 12.0342 | 25.3402 | 12.5383 | 9.5131 | 11.1342 | 8.7171 | 10.2549 | 7.1137 | 6.4635 | 4.8808
| Heat Rejection (elec) | 21.2464 | 19.8617 | 19.7082 | 18.4321 | 14.8924 | 15.4735 | 9.8654 | 17.113 | 9.151 | 7.129 | 7.9354 | 6.2284 | 7.4188 | 4.8706 | 4.2908 | 2.9354
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 771.3743 | 725.9543 | 699.2883 | 685.6343 | 621.0508 | 629.0799 | 536.7592 | 661.1258 | 554.2681 | 518.9614 | 547.1626 | 514.5435 | 538.2555 | 496.372 | 492.4139 | 475.0509
Gas (MJ/m2)
| Heating (gas) | 9.0053 | 50.1708 | 37.4531 | 96.053 | 32.9397 | 53.6323 | 72.445 | 163.509 | 94.5232 | 170.3606 | 171.8501 | 107.4175 | 242.229 | 177.7809 | 302.4701 | 543.7337
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 2.7891 | 3.5209 | 3.0976 | 4.2269 | 4.0917 | 3.6055 | 4.6962 | 4.7823 | 4.6772 | 5.0727 | 5.2703 | 5.2448 | 5.6921 | 5.7687 | 6.387 | 7.2284
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11.7944 | 53.6917 | 40.5504 | 100.2798 | 37.0314 | 57.2379 | 77.1412 | 168.2914 | 99.2004 | 175.4331 | 177.1205 | 112.6623 | 247.9211 | 183.5494 | 308.8571 | 550.9622
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 783.1687 | 779.646 | 739.8387 | 785.9143 | 658.0823 | 686.3178 | 613.9004 | 829.4172 | 653.4685 | 694.3946 | 724.2831 | 627.206 | 786.1768 | 679.9215 | 801.2711 | 1026.0132
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 2108.5026 | 2093.7524 | 1886.9808 | 1931.6612 | 1820.9821 | 1772.749 | 1642.2499 | 1834.58 | 1622.3343 | 1348.1928 | 1347.1568 | 1562.2106 | 1304.6889 | 1346.7153 | 1340.5254 | 1365.6017
| Feb | 2112.0344 | 2042.169 | 1903.8707 | 1940.9758 | 1824.8398 | 1771.1662 | 1805.9258 | 1761.502 | 1680.2813 | 1673.9161 | 1302.2458 | 1490.1932 | 1285.4735 | 1524.7518 | 1283.3324 | 1348.5154
| Mar | 2104.0368 | 2090.0104 | 1945.0387 | 2007.8454 | 1817.7147 | 1836.1657 | 1703.6358 | 2028.8426 | 1699.2332 | 1737.1676 | 1774.2187 | 1626.7205 | 1688.6073 | 1629.7202 | 1315.737 | 1345.7821
| Apr | 2102.9396 | 2077.7452 | 1943.4075 | 2029.8209 | 1867.1096 | 1861.2343 | 1760.5676 | 2011.8215 | 1735.929 | 1717.0733 | 1866.2877 | 1703.9928 | 1781.8194 | 1588.1049 | 1629.3824 | 1281.2726
| May | 2103.3684 | 2081.9779 | 1985.6411 | 2072.143 | 1905.3428 | 1916.6856 | 1817.2423 | 2068.8683 | 1765.0864 | 1836.2886 | 1927.3146 | 1705.7892 | 1923.9075 | 1673.1492 | 1741.7267 | 1636.8935
| Jun | 2111.2775 | 2062.3722 | 2033.9645 | 2071.4295 | 1909.2588 | 1931.2056 | 1817.2172 | 2060.8004 | 2162.013 | 1833.2776 | 1944.1338 | 1867.7656 | 1934.0608 | 1742.2705 | 1837.0608 | 1755.8663
| Jul | 2081.0087 | 2086.9907 | 2046.317 | 2060.2802 | 1923.2446 | 1965.9692 | 1840.8303 | 2053.6888 | 2135.0454 | 1875.2836 | 1946.262 | 1771.7732 | 1945.7341 | 1738.2398 | 1840.9591 | 1738.9608
| Aug | 2089.8795 | 2068.8159 | 2057.3632 | 2071.1095 | 1922.8018 | 1953.1999 | 1829.1001 | 2093.7237 | 1862.3336 | 1865.892 | 1974.4195 | 1783.7622 | 1941.1211 | 1726.8585 | 1840.6593 | 1721.7896
| Sep | 2076.606 | 2072.2165 | 2062.6587 | 2072.1033 | 1915.7379 | 1943.1162 | 1827.8132 | 2064.452 | 1818.6569 | 1839.0916 | 1956.2779 | 1714.1325 | 1946.2912 | 1729.9942 | 1800.5896 | 1611.6946
| Oct | 2099.6165 | 2088.6142 | 2020.5004 | 2049.4701 | 1916.964 | 1891.75 | 1816.0282 | 2073.3877 | 1816.8187 | 1782.6555 | 1948.687 | 1670.6686 | 1825.7287 | 1671.5707 | 1669.2071 | 1342.9703
| Nov | 2100.271 | 2091.6099 | 1936.657 | 1966.6995 | 1931.9904 | 1852.4207 | 1815.7522 | 2004.5172 | 1688.4359 | 1763.1416 | 1946.1226 | 1568.9529 | 1744.7596 | 1429.7016 | 1348.8875 | 1344.8503
| Dec | 2102.3185 | 2093.9291 | 1933.2952 | 1955.592 | 1862.1907 | 1796.9016 | 1635.4834 | 1682.798 | 1553.029 | 1348.1584 | 1347.2143 | 1435.2416 | 1347.0197 | 1345.8675 | 1302.951 | 1347.3723
Time of Peak Electrical Demand
| Jan | 05-JAN-08:09 | 20-JAN-08:09 | 26-JAN-16:10 | 24-JAN-16:00 | 25-JAN-16:40 | 18-JAN-16:49 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:19 | 02-JAN-16:49 | 12-JAN-16:00 | 27-JAN-16:10 | 02-JAN-16:00 | 05-JAN-08:09 | 13-JAN-16:00 | 02-JAN-08:09
| Feb | 03-FEB-08:09 | 15-FEB-16:00 | 28-FEB-16:00 | 22-FEB-08:09 | 13-FEB-16:10 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:19 | 21-FEB-16:10 | 01-FEB-16:00 | 07-FEB-15:09 | 27-FEB-16:00 | 02-FEB-16:40 | 01-FEB-08:09 | 03-FEB-08:09
| Mar | 07-MAR-08:09 | 08-MAR-08:09 | 21-MAR-15:00 | 29-MAR-15:39 | 31-MAR-15:50 | 31-MAR-15:00 | 30-MAR-15:50 | 09-MAR-16:19 | 02-MAR-16:10 | 29-MAR-15:39 | 31-MAR-15:39 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 30-MAR-07:30 | 14-MAR-07:10
| Apr | 17-APR-07:10 | 17-APR-07:00 | 03-APR-15:09 | 13-APR-07:00 | 11-APR-15:09 | 10-APR-15:09 | 13-APR-15:30 | 04-APR-15:39 | 20-APR-15:00 | 19-APR-15:50 | 10-APR-07:00 | 25-APR-15:50 | 27-APR-15:09 | 06-APR-15:00 | 04-APR-15:00 | 10-APR-07:10
| May | 26-MAY-07:10 | 05-MAY-07:10 | 22-MAY-07:00 | 23-MAY-07:10 | 31-MAY-07:10 | 19-MAY-07:00 | 26-MAY-15:09 | 15-MAY-07:10 | 26-MAY-15:50 | 31-MAY-15:00 | 25-MAY-15:30 | 24-MAY-15:09 | 31-MAY-07:40 | 26-MAY-15:09 | 31-MAY-15:00 | 30-MAY-15:09
| Jun | 27-JUN-15:50 | 19-JUN-07:10 | 13-JUN-07:30 | 06-JUN-07:10 | 29-JUN-07:10 | 13-JUN-07:30 | 26-JUN-15:30 | 27-JUN-07:10 | 29-JUN-15:30 | 29-JUN-15:09 | 15-JUN-07:10 | 27-JUN-15:09 | 21-JUN-07:10 | 23-JUN-07:00 | 15-JUN-07:10 | 22-JUN-15:20
| Jul | 13-JUL-15:39 | 18-JUL-15:00 | 13-JUL-07:10 | 24-JUL-07:10 | 20-JUL-07:10 | 28-JUL-07:10 | 03-JUL-07:40 | 25-JUL-15:30 | 07-JUL-15:00 | 31-JUL-07:00 | 17-JUL-07:00 | 25-JUL-07:10 | 17-JUL-07:10 | 21-JUL-15:50 | 05-JUL-07:00 | 24-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 28-AUG-07:30 | 09-AUG-07:10 | 18-AUG-07:00 | 30-AUG-15:09 | 09-AUG-15:50 | 09-AUG-15:09 | 01-AUG-15:09 | 21-AUG-15:00 | 04-AUG-15:50 | 11-AUG-15:50 | 31-AUG-07:10 | 15-AUG-15:20 | 14-AUG-07:40 | 18-AUG-15:39
| Sep | 29-SEP-07:10 | 15-SEP-15:20 | 18-SEP-07:10 | 18-SEP-07:10 | 11-SEP-07:30 | 01-SEP-15:20 | 22-SEP-15:00 | 27-SEP-07:10 | 28-SEP-15:00 | 07-SEP-15:30 | 08-SEP-07:10 | 12-SEP-15:50 | 22-SEP-07:10 | 13-SEP-15:00 | 06-SEP-15:00 | 01-SEP-15:00
| Oct | 31-OCT-07:10 | 23-OCT-07:10 | 04-OCT-07:00 | 20-OCT-07:00 | 23-OCT-07:00 | 06-OCT-15:00 | 31-OCT-15:20 | 03-OCT-07:10 | 03-OCT-15:50 | 17-OCT-15:20 | 31-OCT-07:00 | 04-OCT-15:00 | 06-OCT-15:30 | 05-OCT-15:00 | 27-OCT-15:09 | 30-OCT-07:10
| Nov | 15-NOV-08:09 | 20-NOV-08:09 | 06-NOV-16:00 | 22-NOV-16:10 | 09-NOV-16:00 | 10-NOV-16:40 | 16-NOV-16:00 | 03-NOV-15:00 | 08-NOV-16:10 | 03-NOV-15:09 | 02-NOV-07:00 | 10-NOV-16:10 | 02-NOV-15:39 | 21-NOV-13:00 | 09-NOV-16:40 | 06-NOV-08:09
| Dec | 18-DEC-08:09 | 20-DEC-08:09 | 13-DEC-16:10 | 26-DEC-08:00 | 29-DEC-16:00 | 05-DEC-16:30 | 07-DEC-15:30 | 08-DEC-09:00 | 08-DEC-15:09 | 13-DEC-16:19 | 18-DEC-16:30 | 21-DEC-16:10 | 01-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 29-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 119114.15 | 124847.2 | 104504.8 | 111909.09 | 90907.95 | 107126.18 | 80852.6 | 118022.48 | 90203.79 | 50748.79 | 98831.69 | 84779.4 | 98232.3 | 89204.95 | 94016.41 | 106468.9
| Total Source Energy (MJ/m2) | 2571.53 | 2695.3 | 2256.13 | 2415.98 | 1962.59 | 2312.72 | 1745.51 | 2547.96 | 1947.39 | 1095.6 | 2133.65 | 1830.28 | 2120.71 | 1925.83 | 2029.7 | 2298.53
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 29390.47 | 24493.57 | 35113.44 | 20382.02 | 14159.03 | 28761.12 | 7345.55 | 17838.36 | 15053.66 | 6228.36 | 9642.78 | 9624.33 | 8618.98 | 6634.07 | 4394.69 | 2957.86
| Water Systems | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13
| Total Building | 30894.6 | 25997.7 | 36617.57 | 21886.15 | 15663.17 | 30265.25 | 8849.68 | 19342.49 | 16557.8 | 7732.5 | 11146.91 | 11128.47 | 10123.11 | 8138.21 | 5898.82 | 4461.99
Emissions
| Carbon Equivalent (kg) | 2731810 | 3160540 | 2750020 | 2801230 | 964797.0299 | 2777790 | 871551.9554 | 2436110 | 2996120 | 632875.6623 | 3901430 | 2798570 | 2577670 | 2487260 | 2426680 | 2180150
| CO2 (kg) | 6331300 | 7947730 | 6485420 | 6409570 | 2582630 | 6604120 | 2341030 | 5553960 | 7027580 | 1578660 | 9087760 | 6573560 | 6063450 | 5871400 | 5745050 | 5638120
| NOX (kg) | 11141.5523 | 10393.8883 | 10884.8643 | 12129.2749 | 2214.8058 | 10729.1667 | 2013.0937 | 10661.3102 | 12127.4725 | 2240.6184 | 16157.5877 | 11303.3632 | 10516.0656 | 10038.1539 | 9800.212 | 6604.8463
| SO2 (kg) | 42483.5308 | 44555.7528 | 36181.5852 | 30966.1169 | 23253.0765 | 44525.4346 | 20097.6356 | 31054.4176 | 31143.6902 | 5163.242 | 47447.635 | 28911.8644 | 16348.6308 | 17055.548 | 14957.2838 | 31121.2585
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1936 | 0.1254 | 0.0983 | 0.1135 | 0.0106 | 0.0837 | 0.0094 | 0.1259 | 0.1217 | 0.0209 | 0.1438 | 0.1131 | 0.1204 | 0.1191 | 0.1106 | 0.108
| Water for Electricity (m3) | 5257.9 | 15198.4 | 267268 | 55080.4 | 140303 | 222057 | 121260 | 1931.31 | 32383.4 | 68221.2 | 10922.5 | 30062.4 | 10744.7 | 404560 | 9829.58 | 6244.89

## Picture
DOE Commercial Building Benchmark - Large Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 54.5 | 2841.79
|  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | 10.2
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 11.3 | 60.8 | 3170.29
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 15 | 83.75 | 4366.96
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.75
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
|  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
|  |  | WinterDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
|  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 29.42 | 1534.04
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600