## BuildingSummary
Building Summary Quick Service Restaurant new construction
|  | Value | Data Source
Program
| Building Name | Benchmark Quick Service Post-1980 Construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Service
Form |  |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991 for all Form parameters
| Total Floor Area (m2) | 232.2
| Building Shape | Rectangle
| Aspect Ratio | 1
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.28
| East | 0.14
| North | 0
| West | 0.14
| Total | 0.14
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 2 zones
| Floor to Ceiling Height (m) | 3.048
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass Wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 185.9
| Net Dimensions - Total Area (m2) | 159.9
| Wall to Skin Ratio | 0.44
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 258.86
| Net Dimensions - Total Area (m2) | 258.86
| Roof to Skin Ratio | 0.56
| Window Dimensions (m2) |  | Time Saver Standards; FF Restaurant studies (EPRI, MEOS, LBL) cited in Huang et al. 1991
| South | 13.01
| East | 6.51
| North | 0
| West | 6.51
| Total Area (m2) | 26.03
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4-in slab-on-grade
| Dimensions - Total Area (m2) | 232.2
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 2.41 | See Reference Buildings Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 414.19

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Dining | Yes | 1 | 116.1289 | 354.1871 | 3.0499 | 92.9401 | 26.02 | 1.3935 | 83.3333 | 15.4586 | 129.1668 |  |  | 10 |  | 833.3333 |  | 2.4091
Kitchen | Yes | 1 | 116.1289 | 354.1871 | 3.0499 | 92.9401 | 0 | 18.5806 | 6.25 | 16.6478 | 301.3892 | 1292.1384 | 151.416 | 8 |  | 50 | 1557.4251 | 2.4091
Total Conditioned Zones |  |  | 232.2578 | 708.3742 |  | 185.8802 | 26.02 |  | 89.5833
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall | Mass Wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade | 4-in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:1_COOLC DXCOIL | 41.4341 | 42.5471 | 44.915 | 43.3602 | 36.3503 | 44.7773 | 28.0181 | 41.5042 | 35.0528 | 31.9566 | 37.5389 | 31.6974 | 36.4912 | 26.6165 | 33.8038 | 27.07
| PSZ-AC_2:2_COOLC DXCOIL | 18.0435 | 18.499 | 19.3914 | 18.629 | 17.9406 | 18.842 | 14.2138 | 17.9406 | 16.8912 | 16.0455 | 20.6953 | 19.7351 | 23.3389 | 19.4802 | 25.0852 | 22.0134
Heating (kW)
| PSZ-AC_1:1_HEATC | 51.5064 | 62.8412 | 57.5418 | 66.2722 | 50.6439 | 59.6716 | 52.647 | 70.4353 | 59.0671 | 61.6453 | 75.1503 | 63.3283 | 78.9276 | 72.2871 | 77.7894 | 100.2156
| PSZ-AC_2:2_HEATC | 28.1314 | 38.0748 | 33.6733 | 41.3617 | 29.091 | 35.3703 | 32.1552 | 44.3415 | 35.6415 | 38.3469 | 59.7537 | 49.255 | 72.8251 | 70.8848 | 80.1194 | 130.6096
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:1_COOLC DXCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC_2:2_COOLC DXCOIL | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Heating Efficiency (%)
| PSZ-AC_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_2:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| DINING EXHAUST FAN | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
| KITCHEN EXHAUST FAN | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
| PSZ-AC_1:1_FAN | 1.67 | 1.71 | 1.81 | 1.75 | 1.58 | 1.81 | 1.51 | 1.67 | 1.8 | 1.6 | 1.51 | 1.61 | 1.47 | 1.5 | 1.36 | 1.64
| PSZ-AC_2:2_FAN | 0.73 | 0.74 | 0.78 | 0.75 | 0.72 | 0.76 | 0.72 | 0.72 | 0.73 | 0.72 | 0.83 | 0.85 | 0.94 | 1 | 1.01 | 1.33
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.075652 | 0.10548 | 0.097389 | 0.10643 | 0.12468 | 0.093957 | 0.14533 | 0.06531 | 0.03779 | 0.072357 | 0.053599 | 0.037811 | 0.051261 | 0.06768 | 0.050365 | 0.087495
| Total Cost ($/m2) | 83.52 | 110.97 | 105.5 | 105.19 | 115.2 | 97.61 | 131.57 | 63.02 | 36.33 | 65.89 | 50.5 | 35.48 | 48.2 | 62.72 | 46.28 | 81.61
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.01147 | 0.0081945 | 0.0085964 | 0.010623 | 0.008406 | 0.0081359 | 0.008428 | 0.0099854 | 0.0071492 | 0.0083193 | 0.0087225 | 0.0071271 | 0.0079403 | 0.0085326 | 0.0079242 | 0.0041582
| Total Cost ($/m2) | 30.75 | 25.72 | 25.31 | 38.7 | 24.31 | 26.17 | 28.21 | 44.71 | 27.65 | 34.46 | 45.24 | 31.9 | 47.58 | 45.3 | 54.21 | 39.27
Total Utility Costs
| Cost Intensity ($/m2) | 114.27 | 136.69 | 130.81 | 143.89 | 139.51 | 123.78 | 159.78 | 107.73 | 63.98 | 100.35 | 95.73 | 67.38 | 95.78 | 108.02 | 100.49 | 120.88
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 43372.2222 | 31605.5556 | 37969.4444 | 17155.5556 | 4047.2222 | 28302.7778 | 1116.6667 | 12791.6667 | 11030.5556 | 1683.3333 | 8130.5556 | 6611.1111 | 7130.5556 | 3691.6667 | 2391.6667 | 1011.1111
| Interior Lighting | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667 | 47966.6667
| Exterior Lighting | 12955.5556 | 12933.3333 | 12927.7778 | 12950 | 12947.2222 | 12936.1111 | 12922.2222 | 12936.1111 | 12933.3333 | 12913.8889 | 12916.6667 | 12919.4444 | 12927.7778 | 12911.1111 | 12908.3333 | 12830.5556
| Interior Equipment | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111 | 113711.1111
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 19363.8889 | 20002.7778 | 20977.7778 | 20511.1111 | 18600 | 20961.1111 | 18066.6667 | 20002.7778 | 21063.8889 | 19088.8889 | 19780.5556 | 20611.1111 | 20488.8889 | 21158.3333 | 20877.7778 | 25908.3333
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 19136.1111 | 18227.7778 | 18127.7778 | 17347.2222 | 17405.5556 | 17497.2222 | 16572.2222 | 16777.7778 | 16675 | 16219.4444 | 16397.2222 | 16230.5556 | 16238.8889 | 15869.4444 | 15638.8889 | 15291.6667
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 256505.5556 | 244447.2222 | 251683.3333 | 229641.6667 | 214677.7778 | 241375 | 210355.5556 | 224186.1111 | 223380.5556 | 211583.3333 | 218905.5556 | 218050 | 218463.8889 | 215311.1111 | 213494.4444 | 216719.4444
Gas (MJ)
| Heating | 4020 | 100910 | 61300 | 209140 | 36460 | 117950 | 134480 | 396080 | 255680 | 314390 | 554430 | 389680 | 736410 | 576620 | 924840 | 1518720
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910 | 563910
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 54950 | 64300 | 58920 | 73300 | 71560 | 65400 | 79260 | 80380 | 79040 | 84070 | 86600 | 86270 | 91970 | 92940 | 100820 | 111540
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 622880 | 729120 | 684140 | 846360 | 671930 | 747260 | 777660 | 1040370 | 898630 | 962370 | 1204940 | 1039860 | 1392290 | 1233470 | 1589570 | 2194170
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1546300 | 1609130 | 1590200 | 1673070 | 1444780 | 1616210 | 1534940 | 1847440 | 1702800 | 1724070 | 1992990 | 1824840 | 2178760 | 2008590 | 2358140 | 2974350
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 672.0324 | 489.7134 | 588.3188 | 265.8173 | 62.7098 | 438.5383 | 17.3022 | 198.2009 | 170.9133 | 26.0825 | 125.9792 | 102.4361 | 110.4846 | 57.2007 | 37.0578 | 15.6667
| Interior Lighting (elec) | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211 | 743.2211
| Exterior Lighting (elec) | 200.7403 | 200.396 | 200.3099 | 200.6542 | 200.6112 | 200.439 | 200.2238 | 200.439 | 200.396 | 200.0947 | 200.1377 | 200.1808 | 200.3099 | 200.0516 | 200.0086 | 198.8035
| Interior Equipment (elec) | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007 | 1761.9007
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 300.0344 | 309.9337 | 325.0409 | 317.8101 | 288.1983 | 324.7826 | 279.9346 | 309.9337 | 326.3751 | 295.7734 | 306.4905 | 319.3596 | 317.4658 | 327.8385 | 323.4914 | 401.4375
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 296.5051 | 282.4309 | 280.8815 | 268.7871 | 269.691 | 271.1113 | 256.7789 | 259.9638 | 258.3714 | 251.3127 | 254.0673 | 251.4849 | 251.614 | 245.8896 | 242.3173 | 236.9372
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 3974.434 | 3787.5958 | 3899.7159 | 3558.1906 | 3326.3321 | 3739.9931 | 3259.3613 | 3473.6593 | 3461.1776 | 3278.3851 | 3391.8395 | 3378.5831 | 3384.9961 | 3336.1453 | 3307.9969 | 3357.9668
Gas (MJ/m2)
| Heating (gas) | 17.3022 | 434.3204 | 263.8375 | 900.1463 | 156.9252 | 507.6612 | 578.8069 | 1704.743 | 1100.4562 | 1353.1463 | 2386.2873 | 1677.1972 | 3169.536 | 2481.7939 | 3980.5458 | 6536.6274
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896 | 2427.0896
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 236.5068 | 276.7496 | 253.5939 | 315.4859 | 307.9969 | 281.484 | 341.138 | 345.9585 | 340.1911 | 361.8404 | 372.7296 | 371.3093 | 395.8423 | 400.0172 | 433.933 | 480.0723
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2680.8987 | 3138.1596 | 2944.564 | 3642.7649 | 2892.0117 | 3216.2348 | 3347.0776 | 4477.7912 | 3867.7369 | 4142.0763 | 5186.1066 | 4475.5961 | 5992.4679 | 5308.9007 | 6841.5684 | 9443.7893
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 6655.3327 | 6925.7554 | 6844.2799 | 7200.9555 | 6218.3868 | 6956.2279 | 6606.4388 | 7951.4505 | 7328.9145 | 7420.4614 | 8577.9031 | 7854.1792 | 9377.4641 | 8645.0461 | 10149.5223 | 12801.713
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 40.206 | 37.85 | 35.4649 | 32.8194 | 35.8718 | 32.5292 | 32.2391 | 32.3066 | 32.4415 | 32.2672 | 32.2585 | 32.474 | 32.3031 | 32.4537 | 32.3132 | 35.395
| Feb | 41.6762 | 36.9731 | 36.8828 | 33.2007 | 36.4972 | 32.6423 | 32.299 | 32.3422 | 32.4596 | 32.2607 | 32.2837 | 32.3873 | 32.3194 | 32.4469 | 32.3484 | 32.9043
| Mar | 41.6102 | 39.2406 | 41.4761 | 34.9174 | 35.6153 | 34.5457 | 32.2503 | 34.4196 | 32.8159 | 32.341 | 33.1018 | 34.4522 | 32.4147 | 32.5052 | 32.3389 | 32.9178
| Apr | 42.9572 | 43.0569 | 42.6566 | 37.1343 | 36.9135 | 41.9317 | 32.7781 | 35.1078 | 36.6813 | 32.2755 | 33.011 | 34.0681 | 34.0466 | 32.5273 | 32.3737 | 32.9515
| May | 45.1656 | 45.5386 | 50.3242 | 41.5152 | 36.9829 | 45.8142 | 33.3564 | 38.9562 | 39.6203 | 33.091 | 37.5587 | 37.1228 | 42.4012 | 34.3274 | 32.9843 | 32.9868
| Jun | 47.2024 | 45.9196 | 54.7631 | 44.2498 | 35.3436 | 53.3656 | 35.5876 | 46.7758 | 42.8972 | 36.0049 | 45.6711 | 41.9324 | 43.0426 | 41.1347 | 37.0546 | 36.2388
| Jul | 46.9505 | 48.4824 | 53.7418 | 47.8132 | 38.0326 | 52.1495 | 40.6738 | 48.8893 | 44.5835 | 36.4734 | 46.5276 | 41.9724 | 44.2142 | 41.6059 | 41.6477 | 37.0514
| Aug | 46.796 | 48.3968 | 54.2191 | 45.8373 | 40.8223 | 49.8015 | 36.1343 | 47.6052 | 42.4582 | 35.8433 | 44.5669 | 42.7512 | 44.257 | 40.0739 | 40.0361 | 35.2863
| Sep | 46.6299 | 47.8562 | 49.1333 | 42.6284 | 43.6764 | 48.4558 | 39.1074 | 40.967 | 39.4786 | 42.2875 | 39.7283 | 39.3878 | 36.8042 | 37.7565 | 34.8332 | 33.0334
| Oct | 46.1144 | 43.02 | 42.8179 | 38.1286 | 38.8944 | 41.5721 | 33.9162 | 38.1952 | 36.9968 | 32.9849 | 34.7644 | 36.3731 | 34.6727 | 33.5248 | 33.778 | 32.9798
| Nov | 42.7233 | 40.4209 | 41.0981 | 33.6895 | 36.0188 | 33.2442 | 32.3531 | 35.512 | 32.5579 | 32.3954 | 34.4787 | 32.3833 | 32.4534 | 32.5317 | 32.4085 | 32.9232
| Dec | 39.5961 | 39.4794 | 34.5846 | 32.6917 | 36.4736 | 32.8796 | 32.2372 | 32.3427 | 32.4328 | 32.2944 | 32.3281 | 32.3431 | 32.2952 | 32.4465 | 32.3232 | 35.4136
Time of Peak Electrical Demand
| Jan | 06-JAN-12:15 | 03-JAN-12:15 | 28-JAN-17:00 | 23-JAN-17:00 | 26-JAN-12:00 | 03-JAN-06:45 | 06-JAN-06:30 | 06-JAN-06:45 | 20-JAN-06:30 | 10-JAN-06:45 | 17-JAN-06:00 | 24-JAN-06:15 | 31-JAN-06:45 | 10-JAN-06:00 | 17-JAN-06:00 | 01-JAN-11:15
| Feb | 23-FEB-11:15 | 23-FEB-13:00 | 28-FEB-18:30 | 20-FEB-18:30 | 12-FEB-13:00 | 17-FEB-06:30 | 21-FEB-06:45 | 14-FEB-06:00 | 21-FEB-06:45 | 17-FEB-06:45 | 28-FEB-06:30 | 10-FEB-06:45 | 21-FEB-06:00 | 14-FEB-06:00 | 21-FEB-06:00 | 21-FEB-06:00
| Mar | 13-MAR-18:30 | 26-MAR-12:00 | 17-MAR-18:45 | 28-MAR-18:00 | 31-MAR-10:15 | 31-MAR-12:00 | 31-MAR-05:45 | 09-MAR-19:15 | 25-MAR-18:30 | 29-MAR-18:30 | 31-MAR-18:15 | 26-MAR-18:15 | 19-MAR-18:30 | 30-MAR-18:00 | 31-MAR-05:45 | 10-MAR-06:00
| Apr | 17-APR-12:00 | 29-APR-12:00 | 01-APR-16:00 | 15-APR-16:15 | 11-APR-18:30 | 21-APR-18:15 | 29-APR-10:15 | 05-APR-18:30 | 22-APR-18:45 | 21-APR-05:15 | 29-APR-10:15 | 26-APR-18:45 | 02-APR-18:45 | 06-APR-18:00 | 21-APR-05:15 | 14-APR-05:30
| May | 24-MAY-10:15 | 18-MAY-12:00 | 28-MAY-16:00 | 31-MAY-17:30 | 28-MAY-10:15 | 31-MAY-16:15 | 09-MAY-11:15 | 15-MAY-12:00 | 31-MAY-16:30 | 15-MAY-16:00 | 30-MAY-16:15 | 23-MAY-16:00 | 27-MAY-16:15 | 16-MAY-16:00 | 31-MAY-10:15 | 30-MAY-10:15
| Jun | 26-JUN-10:15 | 13-JUN-16:15 | 28-JUN-16:15 | 23-JUN-12:00 | 28-JUN-10:15 | 27-JUN-16:15 | 16-JUN-10:15 | 30-JUN-16:00 | 20-JUN-16:15 | 18-JUN-12:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-11:15 | 30-JUN-16:15 | 14-JUN-16:30 | 20-JUN-17:00
| Jul | 13-JUL-10:15 | 30-JUL-10:00 | 19-JUL-16:00 | 03-JUL-11:00 | 29-JUL-10:15 | 24-JUL-16:15 | 02-JUL-12:00 | 25-JUL-10:15 | 31-JUL-16:15 | 24-JUL-12:00 | 14-JUL-11:15 | 17-JUL-12:00 | 15-JUL-12:00 | 21-JUL-16:00 | 08-JUL-12:00 | 29-JUL-17:00
| Aug | 21-AUG-12:00 | 31-AUG-10:15 | 01-AUG-16:00 | 17-AUG-12:00 | 08-AUG-10:15 | 05-AUG-12:00 | 15-AUG-11:15 | 17-AUG-18:00 | 01-AUG-12:00 | 07-AUG-16:30 | 04-AUG-16:15 | 30-AUG-12:00 | 25-AUG-18:00 | 09-AUG-16:00 | 12-AUG-12:00 | 15-AUG-16:00
| Sep | 10-SEP-10:15 | 16-SEP-10:15 | 12-SEP-16:00 | 11-SEP-12:00 | 24-SEP-10:00 | 01-SEP-11:15 | 28-SEP-16:15 | 09-SEP-12:00 | 02-SEP-18:30 | 02-SEP-16:15 | 06-SEP-11:15 | 02-SEP-12:00 | 13-SEP-18:30 | 01-SEP-16:00 | 08-SEP-18:45 | 19-SEP-05:00
| Oct | 07-OCT-10:15 | 29-OCT-11:00 | 02-OCT-18:15 | 12-OCT-16:15 | 19-OCT-10:00 | 03-OCT-17:30 | 16-OCT-17:30 | 20-OCT-17:30 | 01-OCT-17:00 | 17-OCT-17:30 | 31-OCT-16:45 | 05-OCT-12:00 | 08-OCT-17:45 | 05-OCT-17:00 | 07-OCT-17:45 | 06-OCT-05:45
| Nov | 01-NOV-10:15 | 26-NOV-11:00 | 12-NOV-13:00 | 19-NOV-17:30 | 20-NOV-11:15 | 10-NOV-17:15 | 03-NOV-05:00 | 05-NOV-12:00 | 10-NOV-06:30 | 03-NOV-05:00 | 02-NOV-18:15 | 10-NOV-06:30 | 03-NOV-05:00 | 21-NOV-06:00 | 03-NOV-05:00 | 14-NOV-06:00
| Dec | 16-DEC-11:15 | 02-DEC-11:15 | 11-DEC-17:30 | 26-DEC-06:00 | 19-DEC-12:00 | 05-DEC-13:00 | 15-DEC-06:30 | 08-DEC-06:00 | 08-DEC-06:00 | 05-DEC-06:45 | 12-DEC-06:00 | 26-DEC-06:45 | 26-DEC-06:00 | 29-DEC-06:45 | 26-DEC-06:00 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 3743.17 | 3992.4 | 3612.94 | 3705.28 | 3125.7 | 3924.24 | 3192.99 | 4022.16 | 3649.54 | 2377.78 | 4110.24 | 3740.09 | 4223.49 | 4041.25 | 4377.4 | 5182.86
| Total Source Energy (MJ/m2) | 16110.54 | 17183.24 | 15550.03 | 15947.48 | 13452.96 | 16889.87 | 13742.57 | 17311.29 | 15707.56 | 10233.94 | 17690.39 | 16097.28 | 18177.83 | 17393.48 | 18840.27 | 22306.93
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19
| Total Building | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19 | 414.19
Emissions
| Carbon Equivalent (kg) | 81578.8072 | 94686.2768 | 88313.7325 | 86000.4225 | 37205.383 | 94884.9077 | 38606.723 | 79258.3329 | 107455.1556 | 32764.5562 | 138437.0349 | 107824.3917 | 99885.7808 | 100925.1289 | 101741.4914 | 100548.6244
| CO2 (kg) | 195343.3943 | 242590.0361 | 214318.253 | 204642.8736 | 101990.0592 | 231752.2746 | 106149.6237 | 189871.28 | 259441.0005 | 86746.6167 | 332055.9582 | 261725.2178 | 244933.3497 | 247268.6238 | 251288.3451 | 267076.6469
| NOX (kg) | 316.7381 | 303.4191 | 334.3489 | 350.05 | 89.1042 | 351.5565 | 92.9508 | 320.4648 | 415.5592 | 104.3383 | 547.322 | 413.3371 | 380.4449 | 383.1941 | 382.617 | 295.1639
| SO2 (kg) | 1098.1125 | 1166.2113 | 1012.2505 | 806.2718 | 624.8694 | 1327.9572 | 612.3185 | 818.645 | 975.6972 | 163.7941 | 1475.5641 | 952.4579 | 515.9855 | 575.2338 | 504.3044 | 1103.7716
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0051 | 0.0034 | 0.0028 | 0.003 | 0.0004 | 0.0026 | 0.0004 | 0.0034 | 0.0039 | 0.0007 | 0.0046 | 0.0038 | 0.0039 | 0.0041 | 0.0038 | 0.004
| Water for Electricity (m3) | 135.8858 | 397.7452 | 7476.09 | 1433.8 | 3769.28 | 6621.89 | 3693.38 | 50.8985 | 1014.32 | 2161.69 | 339.6172 | 990.1196 | 338.9354 | 13638.6 | 331.2221 | 221.4169

## Picture
DOE Commercial Building Benchmark - Quick Service Restaurant

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 24 | 1251.43
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 6
BLDG_LIGHT_SCH | Fraction | Through 12/31 | SummerDesign | [24 empty] | 24 | 35.4 | 1845.86 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 17.7
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.3 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | 7.55 | 44.5 | 2320.36
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.2 | 0.45 | 0.6 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | 6.75
GAS_EQUIP_SCH | Fraction | Through 12/31 | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 0 | 0
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.09 | 0.14 | 0.1 | 0.1 | 0.22 | 0.27 | 0.24 | 0.21 | 0.14 | 0.13 | 0.15 | 0.17 | 0.17 | 0.17 | 0.15 | 0.14 | 0.12 | 0.02 | 2.86
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5 | 101.5 | 5292.5
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 14.5
Kitchen_Exhaust_SCH | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456
|  |  | Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442.4
CLGSETP_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 0 | 0
|  |  | Other | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 600
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 0 | 0
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482.4
HVACOperationSchd | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
MinOA_Sched | Fraction | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 140 | 7300
Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 7.75 | 52.65 | 2745.32
|  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 7.45
|  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 6.45
Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600