## BuildingSummary
Building Summary Secondary School pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Secondary School New
| Available Fuel Types | gas, electricity
| Principal Building Activity | Education
Form
| Total Floor Area (m2) | 19592 | Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
| Building Shape | "E" Shape
Aspect Ratio
| Number of Floors | 2
Window Fraction (Window to Wall Ratio)
| South | 0.35
| East | 0.35
| North | 0.35
| West | 0.28
| Total | 0.34
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures
| Floor to Ceiling Height (m) | 4
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-Framed | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 6384
| Net Dimensions - Total Area (m2) | 4088.16
| Wall to Skin Ratio | 0.35
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11902
| Net Dimensions - Total Area (m2) | 11768.6976
| Roof to Skin Ratio | 0.65
| Window Dimensions (m2) |  | Pless, et al. 2007
| South | 753.18
| East | 291.61
| North | 753.18
| West | 291.2
| Total Area (m2) | 2089.17
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 11902
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 6792
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 39184
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.60327 | See Benchmark Technical Report
HVAC
| System Type | MZ CAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Heating Type | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | 2003 CBECS
| Cooling Type | Packaged DX | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | Storage Tank
| Fuel | Natural Gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 2677.93

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 0.17901
LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 0.29153
BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.56362
OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 0.39893
GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.2801 | 1 | 1976 | 11.3864 | 5 |  | 717.2337 | 10 |  | 19760 |  | 0
AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608.0006 | 266.3502 | 3 | 416 | 11.8138 | 5 |  |  | 10 |  | 4160 |  | 0.24855
AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512.0005 | 106.4001 | 1 | 988 | 12.0812 | 5 |  |  | 8 |  | 7904 |  | 0.26438
KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6 | 36 | 16.7657 | 222.2745 | 1119.4456 | 503.4582 | 8 |  | 288 | 1887.788 | 0.17006
CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200.0002 | 70.0001 | 1.39 | 448.9209 | 14.3812 | 19.2674 |  |  | 10 |  | 4489.2086 |  | 0.32703
MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 0
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 1.1994
LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 1.3119
BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 1.584
OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 1.4193
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236.0002 | 83.0101 | 4.35 | 193.1034 | 16.3387 | 10 |  |  | 8 |  | 1544.8276 |  | 1.307
MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 1.0203
Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 6080.0643
Data Source | [7 empty] | 1 |  | 2 | 4, 5 | 4, 5 | 4, 5 | 3 | 3 | 3 | 4 | 4
Sources
[1] Pless, S.; Torcellini, P.; Long, N. (2007). Technical Support Document: Development of the Advanced Energy Design Guide for K-12 Schools--30% Energy Savings. 178 pp.; NREL Report No. TP-550-42114. http://www.nrel.gov/docs/fy07osti/42114.pdf
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_1:5_COOLC DXCOIL | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 364.2728 | 490.6879 | 441.0682 | 427.7414 | 490.6879 | 435.2112 | 490.6879 | 327.0982 | 490.6879 | 327.0982
| PSZ-AC_2:6_COOLC DXCOIL | 174.2189 | 176.9992 | 190.2766 | 183.1719 | 140.2462 | 158.4212 | 97.6055 | 160.4518 | 118.2095 | 105.1863 | 110.0565 | 91.9823 | 103.624 | 91.1874 | 112.0361 | 95.317
| PSZ-AC_3:7_COOLC DXCOIL | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 162.4734 | 196.2751 | 163.3066 | 159.8081 | 196.2751 | 164.0848 | 196.2751 | 130.8393 | 196.2751 | 130.8393
| PSZ-AC_4:8_COOLC DXCOIL | 19.731 | 19.5594 | 18.8947 | 20.1487 | 16.2923 | 16.3175 | 19.7931 | 17.7835 | 14.0962 | 11.7249 | 14.2489 | 12.1014 | 14.1945 | 10.0314 | 12.1834 | 9.2957
| PSZ-AC_5:9_COOLC DXCOIL | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 87.2141 | 111.4777 | 93.2856 | 90.0771 | 111.4777 | 103.9805 | 111.4777 | 88.1485 | 111.4777 | 74.3123
| CAV_OTHER_COOLC DXCOIL | 491.1104 | 508.017 | 485.8586 | 476.0339 | 347.6097 | 413.0139 | 358.9839 | 457.3647 | 327.9151 | 296.0109 | 384.7656 | 242.3244 | 349.0939 | 248.2074 | 323.5716 | 293.3872
| CAV_POD_1_COOLC DXCOIL | 338.7333 | 357.3859 | 378.2092 | 367.2306 | 262.2861 | 318.8255 | 302.5408 | 343.6933 | 220.8161 | 236.4251 | 256.6164 | 174.7545 | 242.1562 | 151.3398 | 223.7543 | 188.8818
| CAV_POD_2_COOLC DXCOIL | 338.2952 | 356.8435 | 377.8519 | 366.4499 | 261.7163 | 318.404 | 302.4228 | 342.6023 | 220.407 | 235.3995 | 256.6326 | 174.5817 | 242.0795 | 151.6962 | 223.5858 | 188.7835
| CAV_POD_3_COOLC DXCOIL | 356.1988 | 374.8337 | 392.7273 | 384.9943 | 274.4835 | 333.0116 | 303.7543 | 360.5729 | 235.0928 | 247.7481 | 273.7098 | 186.6394 | 259.2238 | 163.7184 | 229.6993 | 189.2769
Heating (kW)
| PSZ-AC_1:5_HEATC | 765.0269 | 1009.9404 | 852.0818 | 1089.4655 | 795.6607 | 921.1228 | 879.4681 | 1212.7703 | 963.6127 | 1048.8159 | 1416.7661 | 1150.2765 | 1531.1076 | 1395.2101 | 1567.2052 | 1940.738
| PSZ-AC_2:6_HEATC | 220.2243 | 268.9727 | 248.0673 | 287.0092 | 206.18 | 241.295 | 212.1653 | 292.0789 | 221.6716 | 240.0718 | 284.0937 | 223.8799 | 299.882 | 281.1615 | 313.9301 | 413.5753
| PSZ-AC_3:7_HEATC | 306.0108 | 403.9762 | 340.8327 | 435.7862 | 318.2643 | 368.4491 | 367.0748 | 485.1081 | 385.4451 | 419.5263 | 566.7064 | 460.1106 | 612.443 | 558.084 | 626.8821 | 776.2952
| PSZ-AC_4:8_HEATC | 30.7625 | 40.2574 | 32.8108 | 44.7357 | 26.4184 | 30.6312 | 45.3451 | 43.9532 | 32.7688 | 30.3707 | 41.1409 | 30.4136 | 44.2915 | 36.0719 | 38.9123 | 55.1536
| PSZ-AC_5:9_HEATC | 173.8039 | 229.445 | 193.5816 | 247.512 | 180.7635 | 209.2668 | 199.8034 | 275.5253 | 218.92 | 238.277 | 321.8704 | 261.3275 | 347.8472 | 316.9731 | 356.0481 | 440.9098
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_1:5_COOLC DXCOIL | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.37 | 3.09 | 3.17 | 3.2 | 3.09 | 3.18 | 3.09 | 3.52 | 3.09 | 3.52
| PSZ-AC_2:6_COOLC DXCOIL | 3.31 | 3.31 | 3.31 | 3.31 | 3.4 | 3.39 | 3.83 | 3.31 | 3.54 | 3.65 | 3.33 | 3.42 | 3.33 | 3.59 | 3.33 | 3.89
| PSZ-AC_3:7_COOLC DXCOIL | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.31 | 3.64 | 3.31 | 3.52 | 3.55 | 3.31 | 3.51 | 3.31 | 3.89 | 3.31 | 3.89
| PSZ-AC_4:8_COOLC DXCOIL | 3.31 | 3.31 | 3.32 | 3.31 | 3.32 | 3.32 | 3.46 | 3.32 | 3.42 | 3.44 | 3.32 | 3.36 | 3.32 | 3.47 | 3.32 | 3.63
| PSZ-AC_5:9_COOLC DXCOIL | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.33 | 3.63 | 3.33 | 3.53 | 3.58 | 3.33 | 3.4 | 3.33 | 3.61 | 3.33 | 3.93
| CAV_OTHER_COOLC DXCOIL | 3.12 | 3.13 | 3.25 | 3.21 | 3.38 | 3.38 | 3.52 | 3.15 | 3.52 | 3.52 | 3.09 | 3.53 | 3.1 | 3.53 | 3.18 | 3.52
| CAV_POD_1_COOLC DXCOIL | 3.09 | 3.09 | 3.13 | 3.09 | 3.27 | 3.27 | 3.52 | 3.09 | 3.7 | 3.46 | 3.1 | 3.58 | 3.1 | 3.89 | 3.17 | 3.7
| CAV_POD_2_COOLC DXCOIL | 3.09 | 3.09 | 3.13 | 3.09 | 3.27 | 3.27 | 3.52 | 3.09 | 3.7 | 3.46 | 3.1 | 3.58 | 3.1 | 3.89 | 3.17 | 3.7
| CAV_POD_3_COOLC DXCOIL | 3.09 | 3.09 | 3.13 | 3.09 | 3.27 | 3.27 | 3.52 | 3.09 | 3.53 | 3.45 | 3.09 | 3.59 | 3.1 | 3.72 | 3.17 | 3.7
Heating Efficiency (%)
| PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_4:8_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC_1:5 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:6 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_3:7 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_4:8 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC_5:9 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_OTHER | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_POD_1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_POD_2 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| CAV_POD_3 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
| KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
| PSZ-AC_1:5_FAN | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76
| PSZ-AC_2:6_FAN | 7.02 | 7.13 | 7.66 | 7.38 | 6.16 | 6.88 | 5.72 | 6.46 | 5.81 | 5.56 | 4.43 | 4.05 | 4.17 | 4.58 | 4.51 | 5.76
| PSZ-AC_3:7_FAN | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 8.57 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
| PSZ-AC_4:8_FAN | 0.79 | 0.79 | 0.76 | 0.81 | 0.66 | 0.66 | 1.02 | 0.72 | 0.67 | 0.57 | 0.57 | 0.52 | 0.57 | 0.51 | 0.49 | 0.56
| PSZ-AC_5:9_FAN | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
| CAV_OTHER_FAN | 20.63 | 21.7 | 23.53 | 22.14 | 19.04 | 22.57 | 21.69 | 20.03 | 19.81 | 17.88 | 15.49 | 14.64 | 14.15 | 14.99 | 14.57 | 17.72
| CAV_POD_1_FAN | 13.64 | 14.39 | 16.06 | 14.79 | 12.9 | 15.72 | 18.25 | 13.84 | 13.34 | 13.62 | 10.33 | 9.66 | 9.75 | 9.14 | 9.01 | 11.41
| CAV_POD_2_FAN | 13.62 | 14.37 | 16.03 | 14.76 | 12.86 | 15.68 | 18.24 | 13.8 | 13.31 | 13.55 | 10.33 | 9.64 | 9.75 | 9.16 | 9 | 11.4
| CAV_POD_3_FAN | 14.34 | 15.09 | 16.78 | 15.5 | 13.53 | 16.46 | 18.33 | 14.52 | 14.2 | 14.2 | 11.02 | 10.41 | 10.44 | 9.89 | 9.25 | 11.43
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.087366 | 0.11694 | 0.085219 | 0.1018 | 0.065221 | 0.10153 | 0.15751 | 0.080257 | 0.036995 | 0.072834 | 0.083741 | 0.037003 | 0.064409 | 0.077739 | 0.0626 | 0.09596
| Total Cost ($/m2) | 19.17 | 22.45 | 17.14 | 16.67 | 9.09 | 18.04 | 19.89 | 12.15 | 5.37 | 9.08 | 11.51 | 4.81 | 8.58 | 9.7 | 7.74 | 11.87
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011429 | 0.008076 | 0.0082792 | 0.0097049 | 0.0085602 | 0.0077356 | 0.0085596 | 0.0096985 | 0.006924 | 0.0084027 | 0.0083643 | 0.0069443 | 0.0078776 | 0.0081515 | 0.0078731 | 0.0041321
| Total Cost ($/m2) | 0.43 | 1.18 | 0.89 | 2.62 | 0.84 | 1.25 | 1.82 | 4.31 | 2.03 | 3.64 | 4.56 | 2.79 | 5.74 | 4.74 | 6.94 | 6.27
Total Utility Costs
| Cost Intensity ($/m2) | 19.6 | 23.63 | 18.03 | 19.29 | 9.93 | 19.29 | 21.7 | 16.46 | 7.4 | 12.72 | 16.07 | 7.61 | 14.32 | 14.44 | 14.68 | 18.14
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1839269.4444 | 1332186.1111 | 1421022.2222 | 796444.4444 | 406725 | 993313.8889 | 132377.7778 | 578675 | 441577.7778 | 116866.6667 | 378063.8889 | 243791.6667 | 295572.2222 | 135663.8889 | 108502.7778 | 43705.5556
| Interior Lighting | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667 | 1150916.6667
| Exterior Lighting | 48986.1111 | 48966.6667 | 48958.3333 | 48950 | 48913.8889 | 48902.7778 | 48927.7778 | 48897.2222 | 48916.6667 | 48819.4444 | 48905.5556 | 48877.7778 | 48875 | 48863.8889 | 48833.3333 | 48536.1111
| Interior Equipment | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 582552.7778 | 552819.4444 | 643438.8889 | 537336.1111 | 451197.2222 | 613658.3333 | 468519.4444 | 511808.3333 | 531066.6667 | 453725 | 439875 | 432344.4444 | 440119.4444 | 436030.5556 | 437641.6667 | 497150
| Pumps | 1033.3333 | 1702.7778 | 1372.2222 | 2438.8889 | 1358.3333 | 1872.2222 | 1697.2222 | 3450 | 2388.8889 | 3372.2222 | 3591.6667 | 2911.1111 | 5116.6667 | 4188.8889 | 6530.5556 | 14822.2222
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 43730.5556 | 41761.1111 | 41911.1111 | 39897.2222 | 39941.6667 | 40580.5556 | 38205.5556 | 38622.2222 | 38669.4444 | 37363.8889 | 37758.3333 | 37547.2222 | 37344.4444 | 36677.7778 | 35997.2222 | 34938.8889
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4299213.8889 | 3761080.5556 | 3940347.2222 | 3208713.8889 | 2731780.5556 | 3481969.4444 | 2473372.2222 | 2965097.2222 | 2846263.8889 | 2443791.6667 | 2691841.6667 | 2549116.6667 | 2610672.2222 | 2445063.8889 | 2421150 | 2422794.4444
Gas (MJ)
| Heating | 191610 | 2255960 | 1539400 | 4624690 | 1272930 | 2547830 | 3470210 | 7996220 | 5041880 | 7757660 | 9931990 | 7130710 | 13490430 | 10607560 | 16442680 | 28846620
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 183770 | 250250 | 219870 | 309330 | 289290 | 263260 | 339330 | 356370 | 347300 | 372940 | 396380 | 392600 | 432010 | 435270 | 485250 | 548270
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 728770 | 2859600 | 2112660 | 5287410 | 1915610 | 3164480 | 4162930 | 8705980 | 5742570 | 8483990 | 10681760 | 7876700 | 14275830 | 11396230 | 17281320 | 29748290
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 16205930 | 16399490 | 16297910 | 16838780 | 11750010 | 15699570 | 13067070 | 19380340 | 15989110 | 17281640 | 20372390 | 17053520 | 23674240 | 20198460 | 25997460 | 38470360
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 337.9629 | 244.7872 | 261.1107 | 146.3454 | 74.7351 | 182.5199 | 24.3242 | 106.3306 | 81.1392 | 21.4741 | 69.4687 | 44.7963 | 54.3109 | 24.928 | 19.9372 | 8.0308
| Interior Lighting (elec) | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792 | 211.4792
| Exterior Lighting (elec) | 9.0011 | 8.9976 | 8.996 | 8.9945 | 8.9879 | 8.9858 | 8.9904 | 8.9848 | 8.9884 | 8.9705 | 8.9863 | 8.9812 | 8.9807 | 8.9787 | 8.9731 | 8.9184
| Interior Equipment (elec) | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 107.0432 | 101.5797 | 118.2309 | 98.7347 | 82.9068 | 112.7588 | 86.0897 | 94.044 | 97.5827 | 83.3713 | 80.8264 | 79.4426 | 80.8713 | 80.1199 | 80.416 | 91.3506
| Pumps (elec) | 0.18987 | 0.31288 | 0.25214 | 0.44814 | 0.24959 | 0.34402 | 0.31186 | 0.63393 | 0.43895 | 0.61964 | 0.65996 | 0.53491 | 0.94018 | 0.7697 | 1.2 | 2.7236
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 8.0354 | 7.6735 | 7.7011 | 7.3311 | 7.3392 | 7.4566 | 7.0202 | 7.0968 | 7.1055 | 6.8656 | 6.938 | 6.8992 | 6.862 | 6.7395 | 6.6144 | 6.42
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 789.974 | 691.0928 | 724.0328 | 589.5963 | 501.9605 | 639.8066 | 454.4784 | 544.8321 | 522.9966 | 449.043 | 494.6218 | 468.3963 | 479.707 | 449.2767 | 444.8826 | 445.1848
Gas (MJ/m2)
| Heating (gas) | 9.78 | 115.147 | 78.5729 | 236.0499 | 64.9719 | 130.0444 | 177.1238 | 408.137 | 257.3438 | 395.9606 | 506.9411 | 363.9603 | 688.5683 | 541.423 | 839.2548 | 1472.3673
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 9.3798 | 12.7731 | 11.2224 | 15.7886 | 14.7657 | 13.4371 | 17.3198 | 18.1896 | 17.7266 | 19.0353 | 20.2317 | 20.0388 | 22.0503 | 22.2167 | 24.7678 | 27.9844
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 37.1973 | 145.9575 | 107.8328 | 269.876 | 97.7751 | 161.519 | 212.4811 | 444.364 | 293.1079 | 433.0334 | 545.2103 | 402.0365 | 728.6561 | 581.6777 | 882.06 | 1518.3896
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 827.1708 | 837.0503 | 831.8656 | 859.4722 | 599.7351 | 801.3255 | 666.9595 | 989.1966 | 816.104 | 882.0764 | 1039.8321 | 870.4328 | 1208.3626 | 1030.9545 | 1326.9426 | 1963.5749
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1152.5527 | 1060.2351 | 862.6575 | 747.1346 | 891.1236 | 694.2663 | 615.5892 | 577.5951 | 618.0729 | 528.465 | 533.8179 | 590.0838 | 522.7487 | 528.8425 | 525.1426 | 545.302
| Feb | 1197.1828 | 1070.1887 | 954.891 | 691.6653 | 883.5046 | 748.0802 | 770.9057 | 590.9585 | 705.543 | 595.0245 | 532.8542 | 572.5301 | 519.8953 | 583.9491 | 523.1014 | 536.9316
| Mar | 1219.175 | 1063.2309 | 1152.1931 | 921.0544 | 837.286 | 856.8815 | 682.9497 | 881.0662 | 721.4136 | 681.2732 | 700.9124 | 706.1306 | 587.3774 | 644.3107 | 520.5292 | 536.5254
| Apr | 1264.3757 | 1170.0169 | 1159.3812 | 1074.5504 | 931.947 | 1122.6464 | 775.1026 | 915.6818 | 874.0276 | 636.7007 | 733.2889 | 774.9614 | 701.1635 | 610.3421 | 586.1723 | 530.2083
| May | 1322.5447 | 1352.1515 | 1336.2235 | 1217.8558 | 972.4386 | 1241.8705 | 850.1364 | 1136.268 | 977.2064 | 828.9185 | 1057.3011 | 863.3512 | 1024.6686 | 738.006 | 764.4226 | 634.1741
| Jun | 1347.0066 | 1368.3771 | 1581.7929 | 1318.4684 | 937.0569 | 1435.8416 | 873.7535 | 1342.5462 | 1077.5864 | 885.8526 | 1200.7742 | 966.6907 | 1148.4072 | 913.8384 | 1015.8229 | 793.4956
| Jul | 1114.5996 | 1181.9009 | 1344.7729 | 1186.0916 | 722.7295 | 1216.281 | 746.6914 | 1168.9623 | 892.5202 | 746.4197 | 1009.8562 | 781.565 | 947.9332 | 699.6049 | 824.5453 | 559.427
| Aug | 1149.3173 | 1182.3706 | 1345.8651 | 1122.5012 | 838.0301 | 1191.1805 | 700.2192 | 1156.4711 | 883.2284 | 701.3334 | 981.3177 | 799.8855 | 927.6466 | 654.552 | 765.6746 | 559.0246
| Sep | 1325.3134 | 1356.048 | 1469.5888 | 1292.07 | 1069.9462 | 1259.7158 | 1069.2822 | 1212.174 | 957.3608 | 926.4258 | 1066.659 | 913.6586 | 1015.7244 | 797.9412 | 908.3237 | 571.366
| Oct | 1305.4414 | 1243.8131 | 1209.099 | 1160.2291 | 983.6472 | 1121.6742 | 853.8937 | 1047.5434 | 888.3331 | 721.4811 | 855.6068 | 836.9542 | 749.4685 | 701.8289 | 618.2886 | 535.8612
| Nov | 1241.7427 | 1121.164 | 1076.3521 | 832.6415 | 934.6531 | 803.4942 | 670.5309 | 927.7977 | 680.7801 | 540.4033 | 844.9054 | 652.4185 | 641.532 | 543.7915 | 532.0221 | 540.526
| Dec | 1123.1664 | 1064.1907 | 855.7302 | 705.6729 | 917.4123 | 757.9682 | 631.0763 | 535.6328 | 603.9927 | 528.4013 | 520.5567 | 568.1054 | 519.4812 | 528.7488 | 522.0814 | 544.624
Time of Peak Electrical Demand
| Jan | 06-JAN-12:00 | 03-JAN-12:00 | 26-JAN-15:39 | 23-JAN-15:30 | 26-JAN-12:00 | 18-JAN-14:00 | 27-JAN-14:00 | 05-JAN-13:00 | 25-JAN-14:00 | 09-JAN-11:39 | 17-JAN-12:00 | 27-JAN-11:50 | 04-JAN-11:20 | 05-JAN-08:09 | 09-JAN-11:09 | 02-JAN-11:09
| Feb | 23-FEB-11:00 | 23-FEB-14:39 | 28-FEB-15:50 | 27-FEB-14:00 | 13-FEB-11:00 | 08-FEB-14:30 | 15-FEB-15:00 | 15-FEB-14:30 | 14-FEB-15:00 | 21-FEB-13:30 | 28-FEB-11:20 | 07-FEB-14:00 | 01-FEB-11:09 | 02-FEB-14:00 | 01-FEB-10:09 | 03-FEB-08:39
| Mar | 13-MAR-15:09 | 29-MAR-11:00 | 17-MAR-15:09 | 28-MAR-15:20 | 31-MAR-11:00 | 31-MAR-15:09 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-15:30 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-13:00 | 30-MAR-15:00 | 07-MAR-11:09 | 14-MAR-07:19
| Apr | 17-APR-12:00 | 17-APR-15:50 | 26-APR-14:30 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 18-APR-13:00 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 25-APR-14:00
| May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-11:20 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:09
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-13:00 | 29-JUN-13:00 | 28-JUN-12:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-13:00 | 30-JUN-12:00 | 14-JUN-15:09 | 21-JUN-15:00
| Jul | 10-JUL-13:30 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-14:00 | 24-JUL-13:50 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 18-JUL-13:00 | 13-JUL-14:00 | 21-JUL-14:00 | 06-JUL-14:00 | 21-JUL-15:00
| Aug | 21-AUG-13:00 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-11:00 | 04-AUG-14:00 | 15-AUG-11:00 | 17-AUG-13:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-13:00
| Sep | 07-SEP-13:00 | 15-SEP-13:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-15:09 | 08-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-15:09 | 13-SEP-15:09 | 06-SEP-11:30 | 05-SEP-13:00 | 14-SEP-14:00 | 12-SEP-13:00 | 07-SEP-14:00 | 07-SEP-14:00
| Oct | 06-OCT-13:00 | 30-OCT-10:50 | 13-OCT-15:09 | 12-OCT-15:00 | 19-OCT-11:00 | 03-OCT-14:00 | 31-OCT-12:00 | 03-OCT-14:09 | 11-OCT-15:00 | 17-OCT-12:00 | 31-OCT-11:00 | 05-OCT-15:09 | 06-OCT-14:00 | 06-OCT-15:00 | 06-OCT-14:00 | 03-OCT-13:00
| Nov | 01-NOV-11:00 | 03-NOV-14:30 | 13-NOV-14:00 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-12:00 | 14-NOV-12:00 | 03-NOV-13:00 | 08-NOV-15:09 | 03-NOV-12:00 | 02-NOV-14:39 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-12:00 | 09-NOV-12:00 | 27-NOV-10:09
| Dec | 19-DEC-12:00 | 19-DEC-15:09 | 13-DEC-12:00 | 01-DEC-14:20 | 19-DEC-12:00 | 05-DEC-13:00 | 07-DEC-14:00 | 08-DEC-11:39 | 05-DEC-13:00 | 26-DEC-11:39 | 26-DEC-11:09 | 21-DEC-14:09 | 18-DEC-11:09 | 18-DEC-08:09 | 11-DEC-10:09 | 29-DEC-11:09
Source Energy
| Total Source Energy (GJ) | 52133.57 | 52299.57 | 47174.99 | 44632.66 | 32529.33 | 48293.64 | 32104.22 | 47678.42 | 40268.92 | 24590.02 | 46027.44 | 39050.04 | 47891.56 | 43041.24 | 48828.58 | 63640.35
| Total Source Energy (MJ/m2) | 2660.96 | 2669.44 | 2407.87 | 2278.11 | 1660.34 | 2464.97 | 1638.64 | 2433.57 | 2055.38 | 1255.11 | 2349.3 | 1993.16 | 2444.44 | 2196.88 | 2492.27 | 3248.28
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
| Total Building | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
Emissions
| Carbon Equivalent (kg) | 1192200 | 1306120 | 1227590 | 1083750 | 353795.2162 | 1231450 | 364121.4959 | 957140.4625 | 1266250 | 330980.704 | 1627770 | 1183350 | 1151050 | 1099020 | 1140370 | 1218190
| CO2 (kg) | 2768140 | 3297010 | 2907400 | 2518750 | 952151.1225 | 2946410 | 988610.2737 | 2247940 | 3008370 | 864830.8352 | 3867810 | 2836730 | 2803900 | 2671950 | 2810940 | 3257670
| NOX (kg) | 4849.4169 | 4273.0502 | 4827.8743 | 4581.8584 | 820.0261 | 4711.2001 | 857.3265 | 3999.4435 | 5024.9956 | 1080.6471 | 6534.7543 | 4629.6946 | 4434.6134 | 4228.0572 | 4303.8635 | 3546.6167
| SO2 (kg) | 18402.5447 | 17941.1233 | 15845.4959 | 11264.0032 | 7949.6644 | 19154.4704 | 7198.329 | 10826.1288 | 12430.5982 | 1891.1289 | 18143.7134 | 11133.5931 | 6165.4281 | 6531.6702 | 5718.9344 | 12340.9724
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0839 | 0.0507 | 0.0432 | 0.0417 | 0.0038 | 0.0362 | 0.0037 | 0.0445 | 0.049 | 0.0083 | 0.0558 | 0.0442 | 0.0465 | 0.0465 | 0.0436 | 0.045
| Water for Electricity (m3) | 2277.54 | 6119.72 | 117046 | 20033.9 | 47963.9 | 95524.4 | 43426.9 | 673.1888 | 12924.3 | 24967.7 | 4176.23 | 11575 | 4050.3 | 154881 | 3756.27 | 2475.32

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16205.93 | 827.17 | 827.17
Net Site Energy | 16205.93 | 827.17 | 827.17
Total Source Energy | 52133.57 | 2660.96 | 2660.96
Net Source Energy | 52133.57 | 2660.96 | 2660.96
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 191.61 | 0 | 0 | 0 | 0
Cooling | 6621.37 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2097.19 | 0 | 0 | 0 | 0 | 0
Pumps | 3.72 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 183.77 | 0 | 0 | 0 | 2677.93
Refrigeration | 157.43 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 15477.17 | 728.77 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 780027.39 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 174218.89 | 117786.47 | 56432.42 | 0.68 | 3.31
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19731.03 | 13339.82 | 6391.21 | 0.68 | 3.31
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 491110.37 | 337192.42 | 153917.95 | 0.69 | 3.12
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 338733.31 | 229011.91 | 109721.4 | 0.68 | 3.09
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 338295.17 | 228715.69 | 109579.48 | 0.68 | 3.09
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 356198.79 | 240820.02 | 115378.76 | 0.68 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6895.98 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11965.66 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9326.93 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13007.38 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9173.81 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12945.26 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9179.4 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12969.6 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9817.15 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13577.44 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9809.9 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13586.53 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9954.95 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13651.39 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7870.46 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16512.16 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7086.69 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16453.86 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7179.78 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16614.24 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 48814.22 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4274.18 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10182.25 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30684.41 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 64000.22 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12342.81 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11888.83 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15891.12 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31452.85 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16933.97 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31232.08 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16994.71 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34743.12 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18076.18 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31849.07 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18040.76 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31901.39 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18904.09 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35819.8 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18516.48 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33516.37 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 765026.92 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 220224.26 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 306010.77 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 30762.47 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 173803.92 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 0 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 6717.31 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 6814.55 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 3121.45 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.02 | 13161.56 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.79 | 921.63 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 20.63 | 34719.36 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.64 | 23111.49 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.62 | 23081.59 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.34 | 24303.14 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4295.16 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 199519.1924 | 345.6837 | 1296.1169 | 0 | 0.0059 | 160407.5698 | 85544.6049
February | 185644.5716 | 324.2685 | 1226.6352 | 0 | 0.0056 | 151810.5366 | 79858.7086
March | 220413.0545 | 384.5051 | 1452.4771 | 0 | 0.0066 | 179760.7539 | 94765.5571
April | 224489.9785 | 393.6197 | 1495.1037 | 0 | 0.0068 | 185037.8113 | 96719.0554
May | 270041.7516 | 474.0907 | 1803.2073 | 0 | 0.0082 | 223169.9461 | 116404.7398
June | 285273.1775 | 501.1498 | 1907.4221 | 0 | 0.0087 | 236068.0916 | 123002.3412
July | 224306.7177 | 394.2239 | 1501.1682 | 0 | 0.0068 | 185789.0638 | 96732.8434
August | 234155.733 | 411.492 | 1566.7533 | 0 | 0.0071 | 193906.0455 | 100976.0654
September | 261589.7019 | 459.4685 | 1748.4711 | 0 | 0.008 | 216395.8051 | 112783.0562
October | 249547.3285 | 437.9285 | 1664.9247 | 0 | 0.0076 | 206055.5632 | 107552.1563
November | 222656.5068 | 390.319 | 1482.2172 | 0 | 0.0068 | 183442.8778 | 95920.5233
December | 190503.1117 | 332.6674 | 1258.048 | 0 | 0.0057 | 155698.1736 | 81939.9258
Annual Sum or Average | 2768140 | 4849.4169 | 18402.5447 | 0 | 0.0839 | 2277540 | 1192200
Minimum of Months | 185644.5716 | 324.2685 | 1226.6352 | 0 | 0.0056 | 151810.5366 | 79858.7086
Maximum of Months | 285273.1775 | 501.1498 | 1907.4221 | 0 | 0.0087 | 236068.0916 | 123002.3412
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1090060000000 | 1152552.658 | 06-JAN-12:00 | 270589.05 | 151653.867 | 127192.648 | 0 | 597685.187 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5317.238 | 0 | 0
February | 1031640000000 | 1197182.758 | 23-FEB-11:00 | 270589.05 | 151653.867 | 131867.749 | 0 | 637620.38 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5337.044 | 0 | 0
March | 1221570000000 | 1219175.023 | 13-MAR-15:09 | 270589.05 | 133019.064 | 129699.564 | 0 | 680379.869 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5372.809 | 0 | 0
April | 1257430000000 | 1264375.702 | 17-APR-12:00 | 270589.05 | 145652.643 | 137632.477 | 0 | 704958.922 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5427.942 | 0 | 0
May | 1516560000000 | 1322544.693 | 24-MAY-14:00 | 270589.05 | 137835.548 | 150948.298 | 0 | 757536.261 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5520.868 | 0 | 0
June | 1604210000000 | 1347006.578 | 28-JUN-14:00 | 270589.05 | 137835.548 | 156706.025 | 0 | 776220.005 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5541.282 | 0 | 0
July | 1262540000000 | 1114599.626 | 10-JUL-13:30 | 150327.25 | 84617.158 | 132817.456 | 0 | 741492.867 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5230.227 | 0 | 0
August | 1317700000000 | 1149317.337 | 21-AUG-13:00 | 150327.25 | 84617.158 | 146612.696 | 0 | 762379.481 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5266.084 | 0 | 0
September | 1470530000000 | 1325313.445 | 07-SEP-13:00 | 270589.05 | 145652.643 | 153781.001 | 0 | 749705.821 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5470.263 | 0 | 0
October | 1400260000000 | 1305441.397 | 06-OCT-13:00 | 270589.05 | 145652.643 | 152513.784 | 0 | 731144.18 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5427.072 | 0 | 0
November | 1246600000000 | 1241742.733 | 01-NOV-11:00 | 270589.05 | 151653.867 | 135198.53 | 0 | 678830.425 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5356.194 | 0 | 0
December | 1058060000000 | 1123166.42 | 19-DEC-12:00 | 270589.05 | 151653.867 | 131350.431 | 0 | 564144.293 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5314.111 | 0 | 0
Annual Sum or Average | 15477200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1031640000000 | 1114599.626 |  | 150327.25 | 84617.158 | 127192.648 | 0 | 564144.293 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5230.227 | 0 | 0
Maximum of Months | 1604210000000 | 1347006.578 |  | 270589.05 | 151653.867 | 156706.025 | 0 | 776220.005 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5541.282 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 375604.92 | 8329.44 | 0 | 383934.36
Cost per Total Building Area ($/m2) | 19.17 | 0.43 | 0 | 19.6
Cost per Net Conditioned Building Area ($/m2) | 19.17 | 0.43 | 0 | 19.6

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16399.49 | 837.05 | 837.05
Net Site Energy | 16399.49 | 837.05 | 837.05
Total Source Energy | 52299.57 | 2669.44 | 2669.44
Net Source Energy | 52299.57 | 2669.44 | 2669.44
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2255.96 | 0 | 0 | 0 | 0
Cooling | 4795.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1990.15 | 0 | 0 | 0 | 0 | 0
Pumps | 6.13 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 250.25 | 0 | 0 | 0 | 2677.93
Refrigeration | 150.34 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 13539.89 | 2859.6 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1019220.11 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 176999.23 | 119666.21 | 57333.02 | 0.68 | 3.31
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19559.41 | 13223.79 | 6335.62 | 0.68 | 3.31
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 508017.01 | 351029.49 | 156987.52 | 0.69 | 3.13
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 357385.87 | 241622.59 | 115763.28 | 0.68 | 3.09
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 356843.55 | 241255.94 | 115587.61 | 0.68 | 3.09
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 374833.66 | 253418.75 | 121414.91 | 0.68 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6888.9 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12486.26 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9739.65 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13726.56 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9582.6 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13662.51 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9588.24 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13687.08 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9893.62 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13901.43 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9886.23 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13910.68 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10033.3 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13977.99 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7821.56 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17190.04 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7033.11 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17124.56 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7125.64 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17284.75 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50941.01 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4940.93 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11244.81 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31079.08 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 66639.33 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12135.8 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12302.73 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18522.1 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35195.89 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19533.08 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34967.03 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19595.08 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38480.65 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17762.28 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32198.49 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17732.99 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32251.81 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18584.44 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36184.51 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20450.41 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36675.12 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1009940.45 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 268972.72 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 403976.18 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 40257.43 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 229445.01 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 25338.06 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 61692.18 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 61798.36 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 58633.21 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.13 | 13371.6 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.79 | 913.61 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 21.7 | 36531.14 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.39 | 24384.14 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.37 | 24347.13 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.09 | 25574.58 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5612.26 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 237661.0044 | 297.8964 | 1151.5103 | 0 | 0.0033 | 392734.5801 | 92845.1872
February | 212248.2025 | 265.2319 | 1017.0257 | 0 | 0.0029 | 346863.0814 | 82812.8592
March | 240128.7647 | 309.7703 | 1286.446 | 0 | 0.0036 | 438800.3861 | 94941.0752
April | 249174.6366 | 325.2705 | 1388.5606 | 0 | 0.0039 | 473648.7423 | 99011.3836
May | 325882.5149 | 426.9448 | 1837.6008 | 0 | 0.0052 | 626826.6593 | 129690.3889
June | 371787.151 | 487.6516 | 2104.3805 | 0 | 0.0059 | 717830.7106 | 148031.8934
July | 300571.5164 | 394.3252 | 1702.4497 | 0 | 0.0048 | 580727.4013 | 119687.1574
August | 301684.2822 | 395.6709 | 1707.1535 | 0 | 0.0048 | 582331.4463 | 120115.5437
September | 316597.9696 | 415.1312 | 1790.1521 | 0 | 0.005 | 610642.8894 | 126040.5955
October | 284517.0791 | 371.7462 | 1590.2723 | 0 | 0.0045 | 542455.6686 | 113098.7819
November | 237540.5906 | 307.4884 | 1287.3815 | 0 | 0.0036 | 439124.3135 | 94053.995
December | 219216.4507 | 275.9228 | 1078.1904 | 0 | 0.0031 | 367733.8963 | 85787.2863
Annual Sum or Average | 3297010 | 4273.0502 | 17941.1233 | 0 | 0.0507 | 6119720 | 1306120
Minimum of Months | 212248.2025 | 265.2319 | 1017.0257 | 0 | 0.0029 | 346863.0814 | 82812.8592
Maximum of Months | 371787.151 | 487.6516 | 2104.3805 | 0 | 0.0059 | 717830.7106 | 148031.8934
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 868926000000 | 1060235.122 | 03-JAN-12:00 | 270589.05 | 151653.867 | 119510.254 | 0 | 513069.753 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5297.529 | 0 | 0
February | 767435000000 | 1070188.746 | 23-FEB-14:39 | 270589.05 | 145652.643 | 133604.769 | 0 | 514874.869 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5352.748 | 0 | 0
March | 970847000000 | 1063230.94 | 29-MAR-11:00 | 270589.05 | 151653.867 | 121217.121 | 0 | 514342.319 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5313.915 | 0 | 0
April | 1047950000000 | 1170016.893 | 17-APR-15:50 | 270589.05 | 133019.064 | 138805.674 | 0 | 622127.026 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5361.412 | 0 | 0
May | 1386860000000 | 1352151.457 | 26-MAY-14:00 | 270589.05 | 137835.548 | 154441.508 | 0 | 783631.668 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5539.016 | 0 | 0
June | 1588200000000 | 1368377.095 | 13-JUN-14:00 | 270589.05 | 137835.548 | 155885.094 | 0 | 798380.441 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5572.295 | 0 | 0
July | 1284860000000 | 1181900.949 | 18-JUL-12:00 | 150327.25 | 84617.158 | 147907.159 | 0 | 793647.029 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5287.685 | 0 | 0
August | 1288410000000 | 1182370.582 | 31-AUG-13:00 | 150327.25 | 84617.158 | 138774.274 | 0 | 803224.22 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5313.012 | 0 | 0
September | 1351050000000 | 1356048.022 | 15-SEP-13:00 | 270589.05 | 145652.643 | 155979.193 | 0 | 778220.772 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5491.696 | 0 | 0
October | 1200180000000 | 1243813.135 | 30-OCT-10:50 | 270589.05 | 151653.867 | 128083.144 | 0 | 685743.995 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 7628.411 | 0 | 0
November | 971563000000 | 1121164.045 | 03-NOV-14:30 | 270589.05 | 137835.548 | 129286.915 | 0 | 578029.418 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5308.446 | 0 | 0
December | 813612000000 | 1064190.655 | 19-DEC-15:09 | 270589.05 | 137835.548 | 125080.479 | 0 | 525266.775 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5304.135 | 0 | 0
Annual Sum or Average | 13539900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 767435000000 | 1060235.122 |  | 150327.25 | 84617.158 | 119510.254 | 0 | 513069.753 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5287.685 | 0 | 0
Maximum of Months | 1588200000000 | 1368377.095 |  | 270589.05 | 151653.867 | 155979.193 | 0 | 803224.22 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 7628.411 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 439821.59 | 23094.21 | 0 | 462915.8
Cost per Total Building Area ($/m2) | 22.45 | 1.18 | 0 | 23.63
Cost per Net Conditioned Building Area ($/m2) | 22.45 | 1.18 | 0 | 23.63

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16297.91 | 831.87 | 831.87
Net Site Energy | 16297.91 | 831.87 | 831.87
Total Source Energy | 47174.99 | 2407.87 | 2407.87
Net Source Energy | 47174.99 | 2407.87 | 2407.87
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1539.4 | 0 | 0 | 0 | 0
Cooling | 5115.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2316.38 | 0 | 0 | 0 | 0 | 0
Pumps | 4.94 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 219.87 | 0 | 0 | 0 | 2677.93
Refrigeration | 150.88 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 14185.25 | 2112.66 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 921703.4 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 190276.65 | 128642.85 | 61633.8 | 0.68 | 3.31
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18894.74 | 12774.42 | 6120.32 | 0.68 | 3.32
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 485858.59 | 352622.32 | 133236.27 | 0.73 | 3.25
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 378209.23 | 260725.35 | 117483.88 | 0.69 | 3.13
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 377851.93 | 260392.12 | 117459.82 | 0.69 | 3.13
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 392727.26 | 271373.6 | 121353.66 | 0.69 | 3.13
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6530.74 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14039.28 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10246.41 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14947.05 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10092.61 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14883.8 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10098.34 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14908.33 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10107.23 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14768.02 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10099 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14776.91 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10241.54 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14844.23 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6782.52 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17990.2 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6003.95 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17912.3 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6103.15 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18082.37 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54477.92 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5379.42 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12983.9 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27933.85 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 69670.01 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10644.6 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12338.92 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20962.78 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40813 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21938.55 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40559.75 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22001.86 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 44082.67 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17456.68 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35222.4 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17417.32 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35264.89 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18267.45 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39172.51 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22038.93 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41400.84 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 852081.84 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 248067.29 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 340832.73 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 32810.8 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 193581.64 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 0 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 23596.6 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 23753.6 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 20198.33 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.66 | 14374.66 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.76 | 882.56 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 23.53 | 39613.28 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.06 | 27203.66 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.03 | 27153.76 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.78 | 28242.68 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5075.29 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 183105.841 | 290.8693 | 902.5453 | 0 | 0.0025 | 6666150 | 75979.2915
February | 166955.1372 | 266.889 | 835.0588 | 0 | 0.0023 | 6167790 | 69447.0441
March | 216619.4705 | 357.9299 | 1167.7349 | 0 | 0.0032 | 8625600 | 91283.5164
April | 220254.9105 | 368.0588 | 1217.1509 | 0 | 0.0033 | 8990830 | 93232.3128
May | 271467.3693 | 456.4672 | 1520.6241 | 0 | 0.0041 | 11232700 | 115196.291
June | 341244.8255 | 574.9906 | 1920.1196 | 0 | 0.0052 | 14183700 | 144926.862
July | 294153.3952 | 495.9176 | 1657.1348 | 0 | 0.0045 | 12241100 | 124954.9188
August | 296721.4181 | 500.1665 | 1671.0192 | 0 | 0.0045 | 12343700 | 126037.6568
September | 299114.5694 | 503.816 | 1681.715 | 0 | 0.0046 | 12422700 | 127015.308
October | 239950.1914 | 401.9201 | 1332.8564 | 0 | 0.0036 | 9845570 | 101665.1796
November | 195219.5286 | 322.1259 | 1049.1626 | 0 | 0.0029 | 7749730 | 82220.6866
December | 182595.1728 | 288.7235 | 890.3742 | 0 | 0.0025 | 6576180 | 75632.4408
Annual Sum or Average | 2907400 | 4827.8743 | 15845.4959 | 0 | 0.0432 | 117046000 | 1227590
Minimum of Months | 166955.1372 | 266.889 | 835.0588 | 0 | 0.0023 | 6167790 | 69447.0441
Maximum of Months | 341244.8255 | 574.9906 | 1920.1196 | 0 | 0.0052 | 14183700 | 144926.862
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 807899000000 | 862657.507 | 26-JAN-15:39 | 270589.05 | 137835.548 | 131811.738 | 0 | 317233.795 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5072.708 | 0 | 0
February | 747501000000 | 954890.999 | 28-FEB-15:50 | 270589.05 | 137835.548 | 139956.9 | 0 | 401203.533 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5191.301 | 0 | 0
March | 1045370000000 | 1152193.053 | 17-MAR-15:09 | 270589.05 | 133019.064 | 144924.149 | 0 | 598325.783 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5220.339 | 0 | 0
April | 1089640000000 | 1159381.191 | 26-APR-14:30 | 270589.05 | 137835.548 | 144164.825 | 0 | 601201.875 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5475.225 | 0 | 0
May | 1361330000000 | 1336223.513 | 30-MAY-14:00 | 270589.05 | 137835.548 | 156162.384 | 0 | 765970.168 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5551.696 | 0 | 0
June | 1718990000000 | 1581792.868 | 28-JUN-15:00 | 270589.05 | 133019.064 | 175506.858 | 0 | 997207.212 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5356.017 | 0 | 0
July | 1483550000000 | 1344772.865 | 11-JUL-15:00 | 150327.25 | 73183.824 | 156633.674 | 0 | 959383.045 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5130.405 | 0 | 0
August | 1495980000000 | 1345865.114 | 01-AUG-15:00 | 150327.25 | 73183.824 | 158618.63 | 0 | 958537.412 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5083.33 | 0 | 0
September | 1505550000000 | 1469588.789 | 08-SEP-13:00 | 270589.05 | 145652.643 | 166422.865 | 0 | 881246.453 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5563.11 | 0 | 0
October | 1193230000000 | 1209098.954 | 13-OCT-15:09 | 270589.05 | 133019.064 | 146981.506 | 0 | 652902.382 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5492.284 | 0 | 0
November | 939222000000 | 1076352.119 | 13-NOV-14:00 | 270589.05 | 145652.643 | 144589.159 | 0 | 510019.916 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5386.684 | 0 | 0
December | 796995000000 | 855730.236 | 13-DEC-12:00 | 270589.05 | 151653.867 | 127447.575 | 0 | 300855.851 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5069.226 | 0 | 0
Annual Sum or Average | 14185300000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 747501000000 | 855730.236 |  | 150327.25 | 73183.824 | 127447.575 | 0 | 300855.851 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5069.226 | 0 | 0
Maximum of Months | 1718990000000 | 1581792.868 |  | 270589.05 | 151653.867 | 175506.858 | 0 | 997207.212 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5563.11 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 335791.66 | 17491.21 | 0 | 353282.87
Cost per Total Building Area ($/m2) | 17.14 | 0.89 | 0 | 18.03
Cost per Net Conditioned Building Area ($/m2) | 17.14 | 0.89 | 0 | 18.03

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16838.78 | 859.47 | 859.47
Net Site Energy | 16838.78 | 859.47 | 859.47
Total Source Energy | 44632.66 | 2278.11 | 2278.11
Net Source Energy | 44632.66 | 2278.11 | 2278.11
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4624.69 | 0 | 0 | 0 | 0
Cooling | 2867.2 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1934.41 | 0 | 0 | 0 | 0 | 0
Pumps | 8.78 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 309.33 | 0 | 0 | 0 | 2677.93
Refrigeration | 143.63 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 11551.37 | 5287.41 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1108652.32 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 183171.94 | 123839.48 | 59332.47 | 0.68 | 3.31
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20148.65 | 13622.16 | 6526.49 | 0.68 | 3.31
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 476033.87 | 339900.31 | 136133.55 | 0.71 | 3.21
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 367230.64 | 248278.47 | 118952.17 | 0.68 | 3.09
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 366449.88 | 247750.61 | 118699.26 | 0.68 | 3.09
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 384994.33 | 260288.21 | 124706.12 | 0.68 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7831.16 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12023.86 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9525.89 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13488.29 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9369.9 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13424.83 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9375.52 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13449.38 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9437.23 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13298.25 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9429.59 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13307.41 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9574.1 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13375.05 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7480.38 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16840.09 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6687.14 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16766.58 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6779.89 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16926.86 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49609.98 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5321.59 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11657.9 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29592.03 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 64627.35 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11824.7 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11941.53 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20042.06 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36902.95 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21007.37 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36644.48 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21071.32 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40166.54 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16592.33 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31242.09 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16555.75 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31284.76 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 17418.81 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35169.93 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21352.9 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37584.1 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1089465.52 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 287009.24 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 435786.21 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 44735.69 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 247512.05 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 46966.15 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 82969.66 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 83107.5 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 80228.39 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.38 | 13837.93 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.81 | 941.13 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 22.14 | 37265.66 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.79 | 25055.84 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.76 | 25002.56 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.5 | 26267.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6104.71 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 217586.8093 | 353.3309 | 764.8155 | 0 | 0.0029 | 1359860 | 89698.2711
February | 193373.9195 | 316.1459 | 690.165 | 0 | 0.0026 | 1227160 | 79913.7343
March | 194022.5482 | 346.5749 | 836.4469 | 0 | 0.0031 | 1487620 | 82894.0582
April | 188137.0564 | 351.8443 | 888.4407 | 0 | 0.0033 | 1580260 | 81837.0972
May | 226352.364 | 431.273 | 1107.9275 | 0 | 0.0041 | 1970730 | 99195.4094
June | 265027.5951 | 508.7724 | 1315.9123 | 0 | 0.0048 | 2340720 | 116496.1721
July | 205728.3212 | 394.9317 | 1021.4598 | 0 | 0.0037 | 1816960 | 90430.0565
August | 211692.6077 | 406.1921 | 1050.1461 | 0 | 0.0038 | 1867980 | 93034.2574
September | 234337.6183 | 449.5349 | 1161.9519 | 0 | 0.0042 | 2066860 | 102976.2657
October | 194172.8137 | 362.569 | 914.1832 | 0 | 0.0034 | 1626040 | 84410.5703
November | 186294.7513 | 325.8463 | 769.1861 | 0 | 0.0029 | 1367930 | 78952.9193
December | 202023.7747 | 334.843 | 743.3684 | 0 | 0.0028 | 1321810 | 83909.089
Annual Sum or Average | 2518750 | 4581.8584 | 11264.0032 | 0 | 0.0417 | 20033900 | 1083750
Minimum of Months | 186294.7513 | 316.1459 | 690.165 | 0 | 0.0026 | 1227160 | 78952.9193
Maximum of Months | 265027.5951 | 508.7724 | 1315.9123 | 0 | 0.0048 | 2340720 | 116496.1721
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 784082000000 | 747134.584 | 23-JAN-15:30 | 270589.05 | 137835.548 | 124859.998 | 0 | 208895.067 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4840.254 | 0 | 0
February | 707566000000 | 691665.269 | 27-FEB-14:00 | 270589.05 | 145652.643 | 119332.075 | 0 | 151186.825 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4790.009 | 0 | 0
March | 857749000000 | 921054.448 | 28-MAR-15:20 | 270589.05 | 133019.064 | 134313.56 | 0 | 378094.646 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4923.46 | 0 | 0
April | 911162000000 | 1074550.384 | 14-APR-15:00 | 270589.05 | 133019.064 | 136314.48 | 0 | 529402.098 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5111.024 | 0 | 0
May | 1136310000000 | 1217855.763 | 15-MAY-14:00 | 270589.05 | 137835.548 | 142766.252 | 0 | 661146.911 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5403.335 | 0 | 0
June | 1349640000000 | 1318468.38 | 19-JUN-14:00 | 270589.05 | 137835.548 | 148250.851 | 0 | 756146.471 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5531.794 | 0 | 0
July | 1047640000000 | 1186091.595 | 03-JUL-14:00 | 150327.25 | 78000.308 | 139613.896 | 0 | 812726.66 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5308.814 | 0 | 0
August | 1077060000000 | 1122501.176 | 17-AUG-13:00 | 150327.25 | 84617.158 | 130301.278 | 0 | 751897.669 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5243.152 | 0 | 0
September | 1191730000000 | 1292069.959 | 11-SEP-13:00 | 270589.05 | 145652.643 | 150068.653 | 0 | 720235.959 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5408.987 | 0 | 0
October | 937560000000 | 1160229.063 | 12-OCT-15:00 | 270589.05 | 133019.064 | 135507.707 | 0 | 615761.487 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5237.087 | 0 | 0
November | 788734000000 | 832641.454 | 22-NOV-15:09 | 270589.05 | 137835.548 | 123126.902 | 0 | 295855.339 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5119.948 | 0 | 0
December | 762144000000 | 705672.89 | 01-DEC-14:20 | 270589.05 | 145652.643 | 119114.745 | 0 | 165306.929 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4894.856 | 0 | 0
Annual Sum or Average | 11551400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 707566000000 | 691665.269 |  | 150327.25 | 78000.308 | 119114.745 | 0 | 151186.825 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4790.009 | 0 | 0
Maximum of Months | 1349640000000 | 1318468.38 |  | 270589.05 | 145652.643 | 150068.653 | 0 | 812726.66 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5531.794 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 326641.31 | 51313.95 | 0 | 377955.26
Cost per Total Building Area ($/m2) | 16.67 | 2.62 | 0 | 19.29
Cost per Net Conditioned Building Area ($/m2) | 16.67 | 2.62 | 0 | 19.29

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11750.01 | 599.74 | 599.74
Net Site Energy | 11750.01 | 599.74 | 599.74
Total Source Energy | 32529.33 | 1660.34 | 1660.34
Net Source Energy | 32529.33 | 1660.34 | 1660.34
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1272.93 | 0 | 0 | 0 | 0
Cooling | 1464.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.09 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1624.31 | 0 | 0 | 0 | 0 | 0
Pumps | 4.89 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 289.29 | 0 | 0 | 0 | 2677.93
Refrigeration | 143.79 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9834.41 | 1915.61 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 766725.44 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 140246.16 | 97939.81 | 42306.35 | 0.7 | 3.4
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16292.34 | 11014.98 | 5277.36 | 0.68 | 3.32
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 347609.72 | 265692.09 | 81917.63 | 0.76 | 3.38
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 262286.08 | 191565.06 | 70721.01 | 0.73 | 3.27
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 261716.31 | 191063.72 | 70652.59 | 0.73 | 3.27
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 274483.5 | 200672.58 | 73810.93 | 0.73 | 3.27
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6419.26 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8476.02 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9115.23 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12601.14 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8973.47 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12543.37 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8978.26 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12566.53 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7824.65 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11197.01 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7815.69 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11204.31 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7950.51 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11267.47 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7033 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14707.05 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6237 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14619.89 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6303.12 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14756.2 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40263.25 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5758.94 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11237.02 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26439.24 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 55308.48 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11392.89 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9913.28 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22122.2 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37311.58 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22971.17 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36995.81 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23034.37 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40513.6 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24174.62 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11664.71 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24211.88 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12107.75 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28009.12 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21720.6 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35865.82 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 795660.69 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 206180.04 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 318264.28 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 26418.37 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 180763.5 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 0 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 18614.93 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 18828.74 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 15484.76 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.16 | 11557.32 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 761.01 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.04 | 32049.78 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.9 | 21859.26 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.86 | 21788.05 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.53 | 22931.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 4221.92 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 84472.7607 | 73.1501 | 633.8563 | 0 | 0.0003 | 3824080 | 31170.0352
February | 75777.0104 | 65.61 | 570.371 | 0 | 0.0003 | 3441070 | 27966.73
March | 86089.3541 | 74.3861 | 675.3062 | 0 | 0.0003 | 4074270 | 31856.0028
April | 76801.922 | 66.1542 | 639.5028 | 0 | 0.0003 | 3858400 | 28532.372
May | 83457.9342 | 71.7454 | 720.3271 | 0 | 0.0003 | 4346150 | 31082.6209
June | 84121.6403 | 72.2267 | 742.0423 | 0 | 0.0003 | 4477230 | 31378.5828
July | 60758.086 | 52.1334 | 541.923 | 0 | 0.0002 | 3269800 | 22681.8612
August | 69662.6049 | 59.7649 | 622.9541 | 0 | 0.0003 | 3758720 | 26010.9531
September | 85640.77 | 73.4564 | 768.7856 | 0 | 0.0004 | 4638630 | 31985.9488
October | 83700.1858 | 71.8849 | 734.7321 | 0 | 0.0003 | 4433100 | 31210.4135
November | 80875.6502 | 69.6859 | 669.3509 | 0 | 0.0003 | 4038480 | 30033.3616
December | 80793.2039 | 69.8281 | 630.5131 | 0 | 0.0003 | 3804010 | 29886.3343
Annual Sum or Average | 952151.1225 | 820.0261 | 7949.6644 | 0 | 0.0038 | 47963900 | 353795.2162
Minimum of Months | 60758.086 | 52.1334 | 541.923 | 0 | 0.0002 | 3269800 | 22681.8612
Maximum of Months | 86089.3541 | 74.3861 | 768.7856 | 0 | 0.0004 | 4638630 | 31985.9488
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 784079000000 | 891123.617 | 26-JAN-12:00 | 270589.05 | 151653.867 | 125203.091 | 0 | 338348.68 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5214.262 | 0 | 0
February | 705550000000 | 883504.649 | 13-FEB-11:00 | 270589.05 | 151653.867 | 125817.882 | 0 | 330136.98 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5192.203 | 0 | 0
March | 835378000000 | 837285.966 | 31-MAR-11:00 | 270589.05 | 151653.867 | 122319.332 | 0 | 287480.574 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5128.475 | 0 | 0
April | 791118000000 | 931947.009 | 11-APR-15:00 | 270589.05 | 133019.064 | 125661.133 | 0 | 397466.717 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5096.377 | 0 | 0
May | 891123000000 | 972438.572 | 30-MAY-11:20 | 270589.05 | 151653.867 | 121888.248 | 0 | 422991.657 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5201.082 | 0 | 0
June | 917999000000 | 937056.942 | 28-JUN-12:00 | 270589.05 | 145652.643 | 120120.821 | 0 | 395353.04 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5226.72 | 0 | 0
July | 670431000000 | 722729.515 | 24-JUL-13:50 | 150327.25 | 84617.158 | 114502.907 | 0 | 368230.772 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4936.76 | 0 | 0
August | 770678000000 | 838030.108 | 08-AUG-11:00 | 150327.25 | 88818.015 | 113596.336 | 0 | 480152.115 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5021.724 | 0 | 0
September | 951094000000 | 1069946.175 | 25-SEP-15:09 | 270589.05 | 133019.064 | 144852.624 | 0 | 516058.4 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5312.369 | 0 | 0
October | 908953000000 | 983647.156 | 19-OCT-11:00 | 270589.05 | 151653.867 | 129231.412 | 0 | 426796.294 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5261.865 | 0 | 0
November | 828039000000 | 934653.056 | 20-NOV-12:00 | 270589.05 | 151653.867 | 128630.722 | 0 | 378407.663 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5257.087 | 0 | 0
December | 779964000000 | 917412.321 | 19-DEC-12:00 | 270589.05 | 151653.867 | 128333.768 | 0 | 361492.43 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5228.538 | 0 | 0
Annual Sum or Average | 9834410000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 670431000000 | 722729.515 |  | 150327.25 | 84617.158 | 113596.336 | 0 | 287480.574 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4936.76 | 0 | 0
Maximum of Months | 951094000000 | 1069946.175 |  | 270589.05 | 151653.867 | 144852.624 | 0 | 516058.4 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5312.369 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 178170.78 | 16398.07 | 0 | 194568.85
Cost per Total Building Area ($/m2) | 9.09 | 0.84 | 0 | 9.93
Cost per Net Conditioned Building Area ($/m2) | 9.09 | 0.84 | 0 | 9.93

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15699.57 | 801.33 | 801.33
Net Site Energy | 15699.57 | 801.33 | 801.33
Total Source Energy | 48293.64 | 2464.97 | 2464.97
Net Source Energy | 48293.64 | 2464.97 | 2464.97
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2547.83 | 0 | 0 | 0 | 0
Cooling | 3575.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2209.17 | 0 | 0 | 0 | 0 | 0
Pumps | 6.74 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 263.26 | 0 | 0 | 0 | 2677.93
Refrigeration | 146.09 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 12535.09 | 3164.48 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 962815.11 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 158421.22 | 110167.05 | 48254.17 | 0.7 | 3.39
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16317.45 | 11031.95 | 5285.5 | 0.68 | 3.32
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 413013.89 | 315343.32 | 97670.57 | 0.76 | 3.38
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 318825.5 | 233069.79 | 85755.71 | 0.73 | 3.27
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 318403.99 | 232680.95 | 85723.04 | 0.73 | 3.27
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 333011.6 | 243678.05 | 89333.55 | 0.73 | 3.27
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6837.91 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12428.4 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9890.35 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14279.05 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9740.39 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14216.2 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9746.08 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14240.44 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9643.57 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14042.02 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9634.66 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14050.31 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9775.84 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14116.22 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6374.05 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16597.52 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5615.36 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16514.49 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5706.61 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16679.78 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49852.07 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5053.12 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12089.69 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25436.39 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 64096.33 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10180.2 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10901.61 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20318.61 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39012.21 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21234.29 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38730.54 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21296.77 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42241.97 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15946.4 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32140.1 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15936.89 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32184.7 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16732.45 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36081.87 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20924.29 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38990.76 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 921122.77 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 241295.03 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 368449.11 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 30631.23 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 209266.82 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 16013.26 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 48299.43 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 48464.03 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 45195.6 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.88 | 12911.69 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 762.18 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 22.57 | 37986.09 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.72 | 26629.84 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.68 | 26572.17 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.46 | 27701.07 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5301.67 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 219259.5241 | 327.4632 | 1208.0377 | 0 | 0.0024 | 6023690 | 89235.5858
February | 180851.1428 | 281.1273 | 1100.067 | 0 | 0.0021 | 5485790 | 74750.0186
March | 211742.1737 | 331.5144 | 1310.2258 | 0 | 0.0025 | 6533900 | 87764.1273
April | 214380.124 | 346.5645 | 1429.1894 | 0 | 0.0027 | 7127580 | 89992.5214
May | 264396.0804 | 430.6648 | 1793.1276 | 0 | 0.0034 | 8942720 | 111325.5109
June | 339776.4677 | 555.38 | 2322.5047 | 0 | 0.0044 | 11582900 | 143265.5568
July | 294559.2517 | 481.8401 | 2016.9021 | 0 | 0.0038 | 10058800 | 124238.2998
August | 296915.4627 | 485.5366 | 2031.553 | 0 | 0.0038 | 10131900 | 125215.7017
September | 288978.3263 | 472.1656 | 1973.5644 | 0 | 0.0037 | 9842650 | 121827.7317
October | 233919.2063 | 378.9157 | 1566.6353 | 0 | 0.0029 | 7813080 | 98274.1089
November | 195376.6154 | 307.0239 | 1219.6005 | 0 | 0.0023 | 6082010 | 81098.5162
December | 206252.0312 | 313.0041 | 1183.0629 | 0 | 0.0023 | 5899370 | 84458.0343
Annual Sum or Average | 2946410 | 4711.2001 | 19154.4704 | 0 | 0.0362 | 95524400 | 1231450
Minimum of Months | 180851.1428 | 281.1273 | 1100.067 | 0 | 0.0021 | 5485790 | 74750.0186
Maximum of Months | 339776.4677 | 555.38 | 2322.5047 | 0 | 0.0044 | 11582900 | 143265.5568
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 790453000000 | 694266.286 | 18-JAN-14:00 | 270589.05 | 145652.643 | 124068.987 | 0 | 148913.446 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4927.492 | 0 | 0
February | 719868000000 | 748080.238 | 08-FEB-14:30 | 270589.05 | 145652.643 | 128370.477 | 0 | 198352.198 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5001.202 | 0 | 0
March | 857405000000 | 856881.485 | 31-MAR-15:09 | 270589.05 | 133019.064 | 134786.892 | 0 | 313455.15 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4916.661 | 0 | 0
April | 935310000000 | 1122646.379 | 21-APR-15:09 | 270589.05 | 133019.064 | 154216.88 | 0 | 559443.458 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5263.259 | 0 | 0
May | 1173500000000 | 1241870.486 | 31-MAY-15:00 | 270589.05 | 133019.064 | 158626.451 | 0 | 674224.667 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5296.587 | 0 | 0
June | 1519960000000 | 1435841.593 | 27-JUN-15:00 | 270589.05 | 133019.064 | 184555.827 | 0 | 842246.332 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5316.652 | 0 | 0
July | 1319960000000 | 1216280.957 | 24-JUL-15:00 | 150327.25 | 73183.824 | 173791.149 | 0 | 813837.829 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5026.237 | 0 | 0
August | 1329540000000 | 1191180.53 | 04-AUG-14:00 | 150327.25 | 78000.308 | 162417.072 | 0 | 795028.033 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5293.199 | 0 | 0
September | 1291590000000 | 1259715.837 | 08-SEP-14:00 | 270589.05 | 137835.548 | 158649.795 | 0 | 687013.504 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5513.272 | 0 | 0
October | 1025260000000 | 1121674.191 | 03-OCT-14:00 | 270589.05 | 137835.548 | 149224.415 | 0 | 558462.619 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5447.892 | 0 | 0
November | 798106000000 | 803494.214 | 10-NOV-12:00 | 270589.05 | 151653.867 | 131814.11 | 0 | 244308.537 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5013.982 | 0 | 0
December | 774140000000 | 757968.176 | 05-DEC-13:00 | 270589.05 | 145652.643 | 124802.54 | 0 | 211804.488 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5004.787 | 0 | 0
Annual Sum or Average | 12535100000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 719868000000 | 694266.286 |  | 150327.25 | 73183.824 | 124068.987 | 0 | 148913.446 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4916.661 | 0 | 0
Maximum of Months | 1519960000000 | 1435841.593 |  | 270589.05 | 151653.867 | 184555.827 | 0 | 842246.332 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5513.272 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 353529.82 | 24479.17 | 0 | 378008.99
Cost per Total Building Area ($/m2) | 18.04 | 1.25 | 0 | 19.29
Cost per Net Conditioned Building Area ($/m2) | 18.04 | 1.25 | 0 | 19.29

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13067.07 | 666.96 | 666.96
Net Site Energy | 13067.07 | 666.96 | 666.96
Total Source Energy | 32104.22 | 1638.64 | 1638.64
Net Source Energy | 32104.22 | 1638.64 | 1638.64
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3470.21 | 0 | 0 | 0 | 0
Cooling | 476.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1686.67 | 0 | 0 | 0 | 0 | 0
Pumps | 6.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 339.33 | 0 | 0 | 0 | 2677.93
Refrigeration | 137.54 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8904.14 | 4162.93 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 973170.79 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 364272.8 | 277260.94 | 87011.86 | 0.76 | 3.37
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 97605.51 | 76889.79 | 20715.73 | 0.79 | 3.83
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 162473.38 | 122178.27 | 40295.11 | 0.75 | 3.64
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19793.13 | 14731.38 | 5061.75 | 0.74 | 3.46
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 87214.12 | 64910.61 | 22303.51 | 0.74 | 3.63
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 358983.94 | 286704.41 | 72279.53 | 0.8 | 3.52
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 302540.85 | 241447.03 | 61093.82 | 0.8 | 3.52
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 302422.85 | 241322.85 | 61099.99 | 0.8 | 3.52
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 303754.27 | 242462.88 | 61291.39 | 0.8 | 3.52
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6439.78 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8936.87 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12534.24 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16437.1 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12420.44 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16389.14 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12422.86 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16398.72 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8631.87 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12235.99 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8612.11 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12237.86 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8721.03 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12276.55 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9277.89 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16995.38 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7909.82 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16816.02 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7944.3 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16822.06 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52257.38 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8346.06 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14613.04 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21361.88 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52558.86 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11019.13 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9581.09 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 38517.39 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57938.7 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 40528.92 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57574.41 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 40557.76 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57660.53 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18863.21 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32391.95 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18782.11 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32405.13 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19336.95 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32676.34 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 32235.05 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 48659.58 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 879468.07 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 212165.26 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 367074.81 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 45345.12 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 199803.42 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 0 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 11776.84 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 11851.09 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 11396.17 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.72 | 10733.71 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 8.57 | 16075.76 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.02 | 1160.63 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 21.69 | 36505.75 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 18.25 | 30716.48 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 18.24 | 30696.21 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 18.33 | 30852.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5358.69 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 105918.5016 | 92.7245 | 615.2787 | 0 | 0.0004 | 3711250 | 38535.7627
February | 81161.2559 | 70.5748 | 556.6914 | 0 | 0.0003 | 3358320 | 29788.4906
March | 97383.6707 | 84.8398 | 639.6039 | 0 | 0.0003 | 3858380 | 35656.0586
April | 81650.0613 | 70.8108 | 593.8701 | 0 | 0.0003 | 3582760 | 30071.0979
May | 82922.1782 | 71.619 | 655.9193 | 0 | 0.0003 | 3957320 | 30700.6891
June | 81152.7623 | 69.9932 | 659.3809 | 0 | 0.0003 | 3978280 | 30098.8525
July | 55486.2983 | 47.8404 | 453.6725 | 0 | 0.0002 | 2737180 | 20588.0379
August | 59226.7016 | 51.0714 | 483.1644 | 0 | 0.0002 | 2915110 | 21972.5764
September | 78965.9485 | 67.9343 | 672.5358 | 0 | 0.0003 | 4057760 | 29382.1276
October | 83000.7291 | 71.6246 | 667.6724 | 0 | 0.0003 | 4028280 | 30763.7341
November | 83740.9294 | 72.6455 | 605.2629 | 0 | 0.0003 | 3651480 | 30829.5098
December | 98001.2367 | 85.6482 | 595.2768 | 0 | 0.0003 | 3590750 | 35734.5588
Annual Sum or Average | 988610.2737 | 857.3265 | 7198.329 | 0 | 0.0037 | 43426900 | 364121.4959
Minimum of Months | 55486.2983 | 47.8404 | 453.6725 | 0 | 0.0002 | 2737180 | 20588.0379
Maximum of Months | 105918.5016 | 92.7245 | 672.5358 | 0 | 0.0004 | 4057760 | 38535.7627
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 760947000000 | 615589.189 | 27-JAN-14:00 | 270589.05 | 145652.643 | 115809.361 | 0 | 78755.885 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4667.582 | 0 | 0
February | 688582000000 | 770905.711 | 15-FEB-15:00 | 270589.05 | 137835.548 | 121814.195 | 0 | 235501.156 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5051.095 | 0 | 0
March | 791112000000 | 682949.658 | 01-MAR-12:00 | 270589.05 | 151653.867 | 114325.752 | 0 | 141363.613 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4902.708 | 0 | 0
April | 734601000000 | 775102.596 | 13-APR-14:00 | 270589.05 | 137835.548 | 126647.874 | 0 | 234889.497 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5025.959 | 0 | 0
May | 811400000000 | 850136.37 | 17-MAY-13:00 | 270589.05 | 145652.643 | 119056.446 | 0 | 309465.093 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5258.47 | 0 | 0
June | 815696000000 | 873753.457 | 15-JUN-12:00 | 270589.05 | 145652.643 | 120012.048 | 0 | 332102.941 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5282.107 | 0 | 0
July | 561224000000 | 746691.446 | 03-JUL-12:00 | 150327.25 | 84617.158 | 119049.326 | 0 | 387479.366 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5103.678 | 0 | 0
August | 597707000000 | 700219.159 | 15-AUG-11:00 | 150327.25 | 88818.015 | 113365.581 | 0 | 342590.007 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5003.639 | 0 | 0
September | 831994000000 | 1069282.155 | 28-SEP-14:00 | 270589.05 | 137835.548 | 143328.893 | 0 | 511894.773 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5519.224 | 0 | 0
October | 825948000000 | 853893.661 | 31-OCT-12:00 | 270589.05 | 145652.643 | 125145.183 | 0 | 307190.272 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5201.846 | 0 | 0
November | 748690000000 | 670530.911 | 14-NOV-12:00 | 270589.05 | 151653.867 | 115658.25 | 0 | 127655.591 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4859.486 | 0 | 0
December | 736238000000 | 631076.335 | 07-DEC-14:00 | 270589.05 | 145652.643 | 113670.885 | 0 | 96291.622 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4757.467 | 0 | 0
Annual Sum or Average | 8904140000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 561224000000 | 615589.189 |  | 150327.25 | 84617.158 | 113365.581 | 0 | 78755.885 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4667.582 | 0 | 0
Maximum of Months | 831994000000 | 1069282.155 |  | 270589.05 | 151653.867 | 143328.893 | 0 | 511894.773 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5519.224 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 389592.24 | 35633.12 | 0 | 425225.36
Cost per Total Building Area ($/m2) | 19.89 | 1.82 | 0 | 21.7
Cost per Net Conditioned Building Area ($/m2) | 19.89 | 1.82 | 0 | 21.7

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 19380.34 | 989.2 | 989.2
Net Site Energy | 19380.34 | 989.2 | 989.2
Total Source Energy | 47678.42 | 2433.57 | 2433.57
Net Source Energy | 47678.42 | 2433.57 | 2433.57
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7996.22 | 0 | 0 | 0 | 0
Cooling | 2083.23 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1842.51 | 0 | 0 | 0 | 0 | 0
Pumps | 12.42 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 356.37 | 0 | 0 | 0 | 2677.93
Refrigeration | 139.04 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10674.35 | 8705.98 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1195895.39 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 160451.77 | 108478.75 | 51973.02 | 0.68 | 3.31
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17783.49 | 12023.12 | 5760.37 | 0.68 | 3.32
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 457364.65 | 319007.88 | 138356.77 | 0.7 | 3.15
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 343693.34 | 232365.3 | 111328.04 | 0.68 | 3.09
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 342602.34 | 231627.69 | 110974.65 | 0.68 | 3.09
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 360572.93 | 243777.31 | 116795.62 | 0.68 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8392.54 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10861.79 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9486.26 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13013.03 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9335.35 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12950.63 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9340.97 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12975.27 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8887.05 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12419.86 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8879.2 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12428.46 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9023.01 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12493.95 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7231.24 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15119.34 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6430.9 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15038.23 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6522.54 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15196.68 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 44321.45 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5890.9 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11219.41 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27736.3 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 58011.81 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11423.91 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10031.89 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22319.18 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36971.02 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23172.39 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36655.11 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23238.11 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40178.32 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15482.86 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28000.52 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15456.1 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28047.78 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16316.59 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31941.53 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22625.11 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36347.79 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1212770.34 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 292078.9 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 485108.14 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 43953.17 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 275525.26 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 77015.28 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 107532.17 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 107695.15 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 105206.51 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.46 | 12121.51 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.72 | 830.66 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 20.03 | 33712.51 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.84 | 23449.91 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.8 | 23375.47 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.52 | 24601.59 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 6585.11 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 239622.223 | 360.7447 | 791.9145 | 0 | 0.0034 | 49218.6437 | 96031.1039
February | 199145.3865 | 309.2579 | 710.3232 | 0 | 0.003 | 44152.677 | 80673.6628
March | 193819.1583 | 323.8743 | 817.7012 | 0 | 0.0034 | 50838.4872 | 80608.7957
April | 151122.1633 | 274.3087 | 757.8357 | 0 | 0.0031 | 47125.6322 | 64842.8889
May | 167695.0875 | 322.4557 | 940.6898 | 0 | 0.0038 | 58502.6876 | 73605.716
June | 215574.5983 | 426.7334 | 1276.6988 | 0 | 0.0051 | 79403.3637 | 95737.8757
July | 170374.6106 | 338.0352 | 1013.2945 | 0 | 0.0041 | 63021.3549 | 75735.2513
August | 180211.7124 | 357.2144 | 1069.9324 | 0 | 0.0043 | 66543.8211 | 80077.1286
September | 173113.9247 | 340.404 | 1012.6567 | 0 | 0.0041 | 62980.7772 | 76672.5806
October | 168602.2507 | 314.3345 | 891.3055 | 0 | 0.0036 | 55428.307 | 73101.8202
November | 172452.0986 | 297.096 | 776.8428 | 0 | 0.0032 | 48301.9637 | 72538.4909
December | 216207.4213 | 334.9847 | 766.9338 | 0 | 0.0033 | 47671.1319 | 87515.1479
Annual Sum or Average | 2247940 | 3999.4435 | 10826.1288 | 0 | 0.0445 | 673188.8471 | 957140.4625
Minimum of Months | 151122.1633 | 274.3087 | 710.3232 | 0 | 0.003 | 44152.677 | 64842.8889
Maximum of Months | 239622.223 | 426.7334 | 1276.6988 | 0 | 0.0051 | 79403.3637 | 96031.1039
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 780431000000 | 577595.085 | 05-JAN-13:00 | 270589.05 | 145652.643 | 106629.063 | 0 | 50132.967 | 0 | 125.287 | 0 | 0 | 0 | 0 | 0 | 4466.075 | 0 | 0
February | 700103000000 | 590958.482 | 15-FEB-14:30 | 270589.05 | 145652.643 | 101954.115 | 0 | 67956.169 | 0 | 118.009 | 0 | 0 | 0 | 0 | 0 | 4688.496 | 0 | 0
March | 806116000000 | 881066.159 | 09-MAR-15:00 | 270589.05 | 137835.548 | 108756.038 | 0 | 358529.764 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5241.091 | 0 | 0
April | 747243000000 | 915681.775 | 04-APR-15:00 | 270589.05 | 133019.064 | 122138.765 | 0 | 384852.03 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4968.198 | 0 | 0
May | 927642000000 | 1136267.983 | 31-MAY-15:00 | 270589.05 | 133019.064 | 123805.964 | 0 | 603431.266 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5307.972 | 0 | 0
June | 1259050000000 | 1342546.227 | 30-JUN-13:00 | 270589.05 | 145652.643 | 152075.314 | 0 | 768556.625 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5557.927 | 0 | 0
July | 999292000000 | 1168962.289 | 25-JUL-12:00 | 150327.25 | 84617.158 | 144997.725 | 0 | 783588.32 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5317.168 | 0 | 0
August | 1055150000000 | 1156471.083 | 17-AUG-13:00 | 150327.25 | 84617.158 | 147803.115 | 0 | 768309.199 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5299.693 | 0 | 0
September | 998649000000 | 1212174 | 08-SEP-14:00 | 270589.05 | 137835.548 | 140994.582 | 0 | 657135.354 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5504.798 | 0 | 0
October | 878894000000 | 1047543.43 | 03-OCT-14:09 | 270589.05 | 137835.548 | 126337.615 | 0 | 507368.231 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5298.319 | 0 | 0
November | 765895000000 | 927797.711 | 03-NOV-13:00 | 270589.05 | 145652.643 | 119582.649 | 0 | 386653.064 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5205.638 | 0 | 0
December | 755893000000 | 535632.831 | 08-DEC-11:39 | 270589.05 | 151653.867 | 101470.131 | 0 | 5441.013 | 0 | 153.393 | 0 | 0 | 0 | 0 | 0 | 6325.377 | 0 | 0
Annual Sum or Average | 10674400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 700103000000 | 535632.831 |  | 150327.25 | 84617.158 | 101470.131 | 0 | 5441.013 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4466.075 | 0 | 0
Maximum of Months | 1259050000000 | 1342546.227 |  | 270589.05 | 151653.867 | 152075.314 | 0 | 783588.32 | 0 | 153.393 | 0 | 0 | 0 | 0 | 0 | 6325.377 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 237971.18 | 84435.24 | 0 | 322406.42
Cost per Total Building Area ($/m2) | 12.15 | 4.31 | 0 | 16.46
Cost per Net Conditioned Building Area ($/m2) | 12.15 | 4.31 | 0 | 16.46

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15989.11 | 816.1 | 816.1
Net Site Energy | 15989.11 | 816.1 | 816.1
Total Source Energy | 40268.92 | 2055.38 | 2055.38
Net Source Energy | 40268.92 | 2055.38 | 2055.38
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5041.88 | 0 | 0 | 0 | 0
Cooling | 1589.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1911.84 | 0 | 0 | 0 | 0 | 0
Pumps | 8.6 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 347.3 | 0 | 0 | 0 | 2677.93
Refrigeration | 139.21 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 10246.55 | 5742.57 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 942701.6 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 441068.15 | 310359.73 | 130708.42 | 0.7 | 3.17
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 118209.52 | 86278.05 | 31931.47 | 0.73 | 3.54
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 163306.62 | 118488.9 | 44817.72 | 0.73 | 3.52
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14096.25 | 10165.05 | 3931.2 | 0.72 | 3.42
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 93285.61 | 67527.42 | 25758.19 | 0.72 | 3.53
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 327915.08 | 261891.11 | 66023.98 | 0.8 | 3.52
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 220816.15 | 176355.98 | 44460.17 | 0.8 | 3.7
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 220406.98 | 176029.19 | 44377.79 | 0.8 | 3.7
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 235092.77 | 187758.08 | 47334.69 | 0.8 | 3.53
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7440.91 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9784.46 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7694.43 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11281.86 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7544.19 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11218.54 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7550.97 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11245.03 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7449.41 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11076.33 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7439.95 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11084.67 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7589.88 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11155.4 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5354.95 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13384.91 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4589.15 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13313.69 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4679.33 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13475.56 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39075.35 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3343.49 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8478.09 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20326.79 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51117.67 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9975.64 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8799.59 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14508.18 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28947.03 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15513.53 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28741.92 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15596.34 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32289 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11308.45 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23730.3 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11265.55 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23775 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12165.6 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27699.93 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15893.3 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29598.31 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 963612.67 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 221671.59 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 385445.07 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 32768.8 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 218919.96 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 56121.88 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 82205.74 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 82290.78 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 79667.84 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.81 | 10890.28 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.67 | 779.41 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.81 | 33346.3 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.34 | 22601.02 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.31 | 22559.14 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.2 | 24062.26 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5190.92 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 266055.5523 | 415.2488 | 941.5485 | 0 | 0.0038 | 978739.5628 | 109125.0828
February | 228323.1066 | 363.6774 | 847.6354 | 0 | 0.0034 | 881176.903 | 94366.7836
March | 254636.1541 | 412.2044 | 981.1252 | 0 | 0.0039 | 1020000 | 105890.9334
April | 221978.4856 | 373.7632 | 933.3685 | 0 | 0.0037 | 970460.1442 | 93725.1095
May | 268856.1461 | 465.745 | 1201.1123 | 0 | 0.0047 | 1248930 | 114798.163
June | 299839.3897 | 522.8818 | 1358.278 | 0 | 0.0053 | 1412380 | 128367.386
July | 236855.0171 | 413.6858 | 1076.4255 | 0 | 0.0042 | 1119300 | 101465.3324
August | 233708.2401 | 407.6568 | 1059.2401 | 0 | 0.0041 | 1101430 | 100065.0244
September | 259636.4402 | 451.9757 | 1171.8427 | 0 | 0.0046 | 1218510 | 111077.4759
October | 238206.1033 | 402.7711 | 1010.7177 | 0 | 0.004 | 1050890 | 100742.0359
November | 238558.3881 | 387.8631 | 928.2986 | 0 | 0.0037 | 965093.4637 | 99370.2748
December | 261721.194 | 407.5225 | 921.0056 | 0 | 0.0037 | 957377.4007 | 107252.9975
Annual Sum or Average | 3008370 | 5024.9956 | 12430.5982 | 0 | 0.049 | 12924300 | 1266250
Minimum of Months | 221978.4856 | 363.6774 | 847.6354 | 0 | 0.0034 | 881176.903 | 93725.1095
Maximum of Months | 299839.3897 | 522.8818 | 1358.278 | 0 | 0.0053 | 1412380 | 128367.386
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 775957000000 | 618072.916 | 25-JAN-14:00 | 270589.05 | 145652.643 | 118632.452 | 0 | 78403.187 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4680.916 | 0 | 0
February | 698608000000 | 705543.03 | 14-FEB-15:00 | 270589.05 | 137835.548 | 125591.391 | 0 | 166474.936 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4937.437 | 0 | 0
March | 808669000000 | 721413.597 | 02-MAR-14:00 | 270589.05 | 145652.643 | 126129.913 | 0 | 173906.457 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5020.866 | 0 | 0
April | 769392000000 | 874027.614 | 21-APR-15:00 | 270589.05 | 133019.064 | 144290.313 | 0 | 321040.127 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4974.392 | 0 | 0
May | 990170000000 | 977206.381 | 31-MAY-15:00 | 270589.05 | 133019.064 | 145967.459 | 0 | 422347.418 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5168.723 | 0 | 0
June | 1119750000000 | 1077586.436 | 29-JUN-13:00 | 270589.05 | 145652.643 | 155562.842 | 0 | 500115.081 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5552.151 | 0 | 0
July | 887398000000 | 892520.249 | 31-JUL-14:00 | 150327.25 | 78000.308 | 151828.741 | 0 | 507067.847 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5181.436 | 0 | 0
August | 873228000000 | 883228.429 | 01-AUG-13:00 | 150327.25 | 84617.158 | 148323.465 | 0 | 494548.687 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5297.201 | 0 | 0
September | 966052000000 | 957360.82 | 20-SEP-15:09 | 270589.05 | 133019.064 | 140640.438 | 0 | 407835.618 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5161.982 | 0 | 0
October | 833162000000 | 888333.099 | 11-OCT-15:00 | 270589.05 | 133019.064 | 130482.688 | 0 | 349154.551 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4973.078 | 0 | 0
November | 765138000000 | 680780.106 | 08-NOV-15:09 | 270589.05 | 137835.548 | 124690.05 | 0 | 142648.123 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4902.668 | 0 | 0
December | 759020000000 | 603992.741 | 05-DEC-13:00 | 270589.05 | 145652.643 | 116645.756 | 0 | 66381.233 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4609.391 | 0 | 0
Annual Sum or Average | 10246500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 698608000000 | 603992.741 |  | 150327.25 | 78000.308 | 116645.756 | 0 | 66381.233 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4609.391 | 0 | 0
Maximum of Months | 1119750000000 | 1077586.436 |  | 270589.05 | 145652.643 | 155562.842 | 0 | 507067.847 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5552.151 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 105298.68 | 39761.77 | 0 | 145060.45
Cost per Total Building Area ($/m2) | 5.37 | 2.03 | 0 | 7.4
Cost per Net Conditioned Building Area ($/m2) | 5.37 | 2.03 | 0 | 7.4

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17281.64 | 882.08 | 882.08
Net Site Energy | 17281.64 | 882.08 | 882.08
Total Source Energy | 24590.02 | 1255.11 | 1255.11
Net Source Energy | 24590.02 | 1255.11 | 1255.11
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7757.66 | 0 | 0 | 0 | 0
Cooling | 420.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.75 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1633.41 | 0 | 0 | 0 | 0 | 0
Pumps | 12.14 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 372.94 | 0 | 0 | 0 | 2677.93
Refrigeration | 134.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8797.65 | 8483.99 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 5.835 | 0.54 | 0.384 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 5.835 | 0.54 | 0.384 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 5.835 | 0.54 | 0.384 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 5.835 | 0.54 | 0.384 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 5.835 | 0.54 | 0.384 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 5.835 | 0.54 | 0.384 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 5.835 | 0.54 | 0.384 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 5.835 | 0.54 | 0.384 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 753.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 1335.99 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1013320.21 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 427741.37 | 304615.89 | 123125.48 | 0.71 | 3.2
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 105186.26 | 79193.14 | 25993.12 | 0.75 | 3.65
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 159808.1 | 116981.03 | 42827.06 | 0.73 | 3.55
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11724.86 | 8535.78 | 3189.08 | 0.73 | 3.44
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 90077.1 | 66144.55 | 23932.55 | 0.73 | 3.58
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 296010.9 | 236410.66 | 59600.24 | 0.8 | 3.52
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 236425.08 | 184803.77 | 51621.31 | 0.78 | 3.46
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 235399.51 | 183893.77 | 51505.74 | 0.78 | 3.46
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 247748.12 | 193184.56 | 54563.56 | 0.78 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7146.87 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9100.44 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9869.95 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13491.04 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9732.97 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13433.14 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9738 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13456.75 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7127.76 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10570.59 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7116.13 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10576.08 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7250.63 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10639.2 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5762.83 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13197.29 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4964.53 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13069.1 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5032.99 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13211.1 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35793.27 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6953.65 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12503.28 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 18654.07 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 47377.78 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9591.93 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7579.59 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27779.74 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 43623.86 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28410.63 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 43157.6 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28482.53 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 46708.04 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21831.13 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21863.77 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11541.09 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25693.26 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24997.71 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39234.3 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1048815.86 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 240071.75 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 419526.35 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 30370.67 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 238276.99 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 52842.43 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 75096.47 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 75416.36 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 72799.42 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.56 | 10436.58 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 663.69 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 17.88 | 30101.9 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.62 | 23079.95 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 13.55 | 22949.67 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.2 | 24054.48 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5579.77 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 111171.2937 | 126.5676 | 164.2703 | 0 | 0.0008 | 2166330 | 41224.2419
February | 84946.8829 | 99.9126 | 145.9599 | 0 | 0.0007 | 1925800 | 31842.6367
March | 95241.6271 | 112.9989 | 169.8924 | 0 | 0.0008 | 2241820 | 35806.3885
April | 71309.1768 | 88.5801 | 152.5858 | 0 | 0.0007 | 2014420 | 27234.7112
May | 59299.6598 | 80.6597 | 171.5682 | 0 | 0.0007 | 2266440 | 23397.4607
June | 51644.64 | 74.6429 | 177.4853 | 0 | 0.0007 | 2345270 | 20847.8415
July | 35701.5649 | 52.39 | 127.7377 | 0 | 0.0005 | 1688010 | 14496.5607
August | 37934.0761 | 55.4749 | 134.5046 | 0 | 0.0005 | 1777410 | 15382.5896
September | 51299.5919 | 72.9624 | 168.754 | 0 | 0.0007 | 2229740 | 20581.9822
October | 64722.475 | 83.8016 | 160.2226 | 0 | 0.0007 | 2115930 | 25083.6094
November | 93036.0211 | 109.1849 | 158.3143 | 0 | 0.0007 | 2088750 | 34848.9655
December | 108523.8259 | 123.4713 | 159.8338 | 0 | 0.0008 | 2107800 | 40233.7161
Annual Sum or Average | 864830.8352 | 1080.6471 | 1891.1289 | 0 | 0.0083 | 24967700 | 330980.704
Minimum of Months | 35701.5649 | 52.39 | 127.7377 | 0 | 0.0005 | 1688010 | 14496.5607
Maximum of Months | 111171.2937 | 126.5676 | 177.4853 | 0 | 0.0008 | 2345270 | 41224.2419
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 763331000000 | 528464.964 | 09-JAN-11:39 | 270589.05 | 151653.867 | 98140.556 | 0 | 0 | 0 | 1954.858 | 0 | 0 | 0 | 0 | 0 | 6126.633 | 0 | 0
February | 678578000000 | 595024.497 | 21-FEB-13:30 | 270589.05 | 145652.643 | 99968.198 | 0 | 73932.571 | 0 | 115.992 | 0 | 0 | 0 | 0 | 0 | 4766.042 | 0 | 0
March | 789929000000 | 681273.164 | 29-MAR-15:30 | 270589.05 | 133019.064 | 117406.074 | 0 | 155462.756 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4681.552 | 0 | 0
April | 709802000000 | 636700.656 | 18-APR-13:00 | 270589.05 | 145652.643 | 109779.246 | 0 | 105758.891 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4806.159 | 0 | 0
May | 798605000000 | 828918.484 | 05-MAY-15:00 | 270589.05 | 133019.064 | 122587.746 | 0 | 297644.262 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4963.694 | 0 | 0
June | 826381000000 | 885852.64 | 28-JUN-12:00 | 270589.05 | 145652.643 | 122994.481 | 0 | 341221.148 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5280.65 | 0 | 0
July | 594789000000 | 746419.682 | 24-JUL-14:00 | 150327.25 | 78000.308 | 120768.767 | 0 | 392125.314 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5083.375 | 0 | 0
August | 626289000000 | 701333.438 | 07-AUG-14:00 | 150327.25 | 78000.308 | 118624.63 | 0 | 349273.573 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4993.01 | 0 | 0
September | 785675000000 | 926425.757 | 13-SEP-15:09 | 270589.05 | 133019.064 | 130269.61 | 0 | 387333.313 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5100.053 | 0 | 0
October | 745571000000 | 721481.056 | 17-OCT-12:00 | 270589.05 | 145652.643 | 113204.163 | 0 | 186872.515 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5048.017 | 0 | 0
November | 735993000000 | 540403.286 | 03-NOV-12:00 | 270589.05 | 145652.643 | 104827.921 | 0 | 14435.92 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4783.085 | 0 | 0
December | 742707000000 | 528401.273 | 26-DEC-11:39 | 270589.05 | 151653.867 | 98140.556 | 0 | 0 | 0 | 1867.344 | 0 | 0 | 0 | 0 | 0 | 6150.456 | 0 | 0
Annual Sum or Average | 8797650000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 594789000000 | 528401.273 |  | 150327.25 | 78000.308 | 98140.556 | 0 | 0 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4681.552 | 0 | 0
Maximum of Months | 826381000000 | 926425.757 |  | 270589.05 | 151653.867 | 130269.61 | 0 | 392125.314 | 0 | 1954.858 | 0 | 0 | 0 | 0 | 0 | 6150.456 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 177991.12 | 71288.56 | 0 | 249279.69
Cost per Total Building Area ($/m2) | 9.08 | 3.64 | 0 | 12.72
Cost per Net Conditioned Building Area ($/m2) | 9.08 | 3.64 | 0 | 12.72

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20372.39 | 1039.83 | 1039.83
Net Site Energy | 20372.39 | 1039.83 | 1039.83
Total Source Energy | 46027.44 | 2349.3 | 2349.3
Net Source Energy | 46027.44 | 2349.3 | 2349.3
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9931.99 | 0 | 0 | 0 | 0
Cooling | 1361.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 176.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1583.55 | 0 | 0 | 0 | 0 | 0
Pumps | 12.93 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 396.38 | 0 | 0 | 0 | 2677.93
Refrigeration | 135.93 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9690.63 | 10681.76 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 753.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 1335.99 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1302968.18 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 110056.53 | 74407.37 | 35649.16 | 0.68 | 3.33
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14248.9 | 9633.44 | 4615.46 | 0.68 | 3.32
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 384765.6 | 260133.56 | 124632.03 | 0.68 | 3.09
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 256616.43 | 173494.06 | 83122.37 | 0.68 | 3.1
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 256632.56 | 173504.96 | 83127.59 | 0.68 | 3.1
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 273709.84 | 185050.63 | 88659.21 | 0.68 | 3.09
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9450.96 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12060.83 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6845.56 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9682.66 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6759.17 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9643.06 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6763.5 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9663.26 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6399.12 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9299.57 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6390.28 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9303.67 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6479.78 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9352.52 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5549.75 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11742.33 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4792.75 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11674.57 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4856.98 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11824.23 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35592.48 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4147.31 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8523.62 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 25874.7 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 44007.67 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10885.56 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8100.45 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14117.29 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25633.93 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15261.43 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25468.41 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15323.92 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28975.59 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12211.31 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22590.38 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12231.78 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22614.28 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12670.86 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26361.39 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15644.81 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26320.71 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1416766.07 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 284093.71 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 566706.43 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 41140.94 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 321870.37 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 136763.3 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 154201.27 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 154209.2 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 153768.37 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.43 | 8453.69 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 665.56 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.49 | 26252.23 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.33 | 17778.09 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.33 | 17779.2 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.02 | 18674.99 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7174.7 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 384117.3165 | 586.5279 | 1427.52 | 0 | 0.0046 | 328484.8156 | 155685.8434
February | 329071.5836 | 511.2562 | 1275.586 | 0 | 0.004 | 293540.2678 | 134214.8623
March | 349738.7842 | 560.7589 | 1459.9679 | 0 | 0.0046 | 336002.464 | 144307.1718
April | 272603.0348 | 467.1572 | 1318.2603 | 0 | 0.004 | 303440.5362 | 115355.3657
May | 310388.717 | 553.0895 | 1627.9496 | 0 | 0.0049 | 374756.7342 | 133369.8166
June | 384732.1145 | 696.5648 | 2083.8191 | 0 | 0.0063 | 479713.5876 | 166365.9751
July | 287348.9538 | 521.0059 | 1560.8908 | 0 | 0.0047 | 359331.8582 | 124327.7172
August | 276773.6729 | 500.9481 | 1498.1509 | 0 | 0.0045 | 344887.3669 | 119667.6494
September | 309695.8726 | 558.0159 | 1661.249 | 0 | 0.005 | 382430.6753 | 133661.165
October | 291474.3066 | 508.868 | 1465.6966 | 0 | 0.0045 | 337391.5802 | 124236.9714
November | 316863.1025 | 516.949 | 1376.0941 | 0 | 0.0043 | 316714.5928 | 131593.3118
December | 354998.9283 | 553.613 | 1388.5292 | 0 | 0.0044 | 319534.7816 | 144987.9842
Annual Sum or Average | 3867810 | 6534.7543 | 18143.7134 | 0 | 0.0558 | 4176230 | 1627770
Minimum of Months | 272603.0348 | 467.1572 | 1275.586 | 0 | 0.004 | 293540.2678 | 115355.3657
Maximum of Months | 384732.1145 | 696.5648 | 2083.8191 | 0 | 0.0063 | 479713.5876 | 166365.9751
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 762224000000 | 533817.924 | 17-JAN-12:00 | 270589.05 | 151653.867 | 91784.447 | 0 | 15180.564 | 0 | 162.915 | 0 | 0 | 0 | 0 | 0 | 4447.081 | 0 | 0
February | 681138000000 | 532854.152 | 28-FEB-11:20 | 270589.05 | 151653.867 | 90956.22 | 0 | 13435.424 | 0 | 136.48 | 0 | 0 | 0 | 0 | 0 | 6083.111 | 0 | 0
March | 779668000000 | 700912.37 | 31-MAR-14:00 | 270589.05 | 137835.548 | 98450.794 | 0 | 188903.637 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5018.674 | 0 | 0
April | 704111000000 | 733288.898 | 07-APR-14:00 | 270589.05 | 137835.548 | 104832.447 | 0 | 214882.07 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5035.117 | 0 | 0
May | 869595000000 | 1057301.054 | 30-MAY-15:00 | 270589.05 | 133019.064 | 112840.107 | 0 | 535361.115 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5377.051 | 0 | 0
June | 1113140000000 | 1200774.222 | 08-JUN-12:00 | 270589.05 | 145652.643 | 130807.85 | 0 | 648085.283 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5524.727 | 0 | 0
July | 833803000000 | 1009856.153 | 14-JUL-11:00 | 150327.25 | 88818.015 | 123743.687 | 0 | 641556.473 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5296.06 | 0 | 0
August | 800285000000 | 981317.735 | 04-AUG-14:00 | 150327.25 | 78000.308 | 126956.691 | 0 | 620730.725 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5188.094 | 0 | 0
September | 887402000000 | 1066658.951 | 06-SEP-11:30 | 270589.05 | 151653.867 | 116330.7 | 0 | 522572.539 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5398.127 | 0 | 0
October | 782892000000 | 855606.84 | 31-OCT-11:00 | 270589.05 | 151653.867 | 104067.658 | 0 | 323987.222 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5194.375 | 0 | 0
November | 734912000000 | 844905.448 | 02-NOV-14:39 | 270589.05 | 137835.548 | 103449.699 | 0 | 327729.592 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5186.892 | 0 | 0
December | 741456000000 | 520556.718 | 26-DEC-11:09 | 270589.05 | 151653.867 | 90769.463 | 0 | 0 | 0 | 1628.968 | 0 | 0 | 0 | 0 | 0 | 5915.37 | 0 | 0
Annual Sum or Average | 9690630000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 681138000000 | 520556.718 |  | 150327.25 | 78000.308 | 90769.463 | 0 | 0 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4447.081 | 0 | 0
Maximum of Months | 1113140000000 | 1200774.222 |  | 270589.05 | 151653.867 | 130807.85 | 0 | 648085.283 | 0 | 1628.968 | 0 | 0 | 0 | 0 | 0 | 6083.111 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 225417.7 | 89345.12 | 0 | 314762.82
Cost per Total Building Area ($/m2) | 11.51 | 4.56 | 0 | 16.07
Cost per Net Conditioned Building Area ($/m2) | 11.51 | 4.56 | 0 | 16.07

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 17053.52 | 870.43 | 870.43
Net Site Energy | 17053.52 | 870.43 | 870.43
Total Source Energy | 39050.04 | 1993.16 | 1993.16
Net Source Energy | 39050.04 | 1993.16 | 1993.16
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7130.71 | 0 | 0 | 0 | 0
Cooling | 877.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1556.44 | 0 | 0 | 0 | 0 | 0
Pumps | 10.48 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 392.6 | 0 | 0 | 0 | 2677.93
Refrigeration | 135.17 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9176.82 | 7876.7 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 753.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 1335.99 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1053668.2 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 435211.2 | 307835.39 | 127375.81 | 0.71 | 3.18
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91982.27 | 64295.4 | 27686.87 | 0.7 | 3.42
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 164084.76 | 118824.27 | 45260.48 | 0.72 | 3.51
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12101.37 | 8395.38 | 3705.99 | 0.69 | 3.36
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 103980.49 | 72136.91 | 31843.57 | 0.69 | 3.4
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 242324.39 | 193533.65 | 48790.74 | 0.8 | 3.53
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 174754.46 | 134134.91 | 40619.55 | 0.77 | 3.58
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 174581.68 | 133896.18 | 40685.5 | 0.77 | 3.58
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 186639.42 | 143774.05 | 42865.37 | 0.77 | 3.59
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 8401.43 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11007.83 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5211.23 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8069.84 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5125.28 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8030.04 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5130.86 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8052.87 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4813.07 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7720.17 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4802.3 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7723.68 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4895.26 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7776.9 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3857.48 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9932.7 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3650.73 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9874.32 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3705.67 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10021.18 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30173.89 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3672.76 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7878.5 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22877.66 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36746.41 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9560.16 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6846.37 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10840.98 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20561.96 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10553.88 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20488.31 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10562.25 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24033.53 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10534.46 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18030.27 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10554.74 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18051.24 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10712.92 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21803.2 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11055.7 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21674.89 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1150276.54 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 223879.93 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 460110.62 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 30413.6 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 261327.5 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 109563.56 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 123242.26 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 123253.99 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 122890.94 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.05 | 7725.96 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 606 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.64 | 24802.43 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.66 | 16625.72 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.64 | 16579.29 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.41 | 17902.49 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 5801.95 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 274877.0784 | 418.6514 | 916.6629 | 0 | 0.0037 | 952786.1251 | 111726.5494
February | 242083.759 | 370.4638 | 816.82 | 0 | 0.0033 | 849023.9048 | 98569.8411
March | 260848.7995 | 412.2481 | 950.8658 | 0 | 0.0038 | 988466.902 | 107492.2759
April | 219382.5922 | 361.9646 | 882.2511 | 0 | 0.0035 | 917260.1224 | 91900.4798
May | 234620.8529 | 395.6424 | 989.7323 | 0 | 0.0039 | 1029070 | 99121.1398
June | 249313.0295 | 430.6122 | 1106.8873 | 0 | 0.0043 | 1150950 | 106328.1574
July | 190184.1251 | 331.4299 | 860.3085 | 0 | 0.0034 | 894573.9571 | 81399.4451
August | 195866.8432 | 340.83 | 883.2921 | 0 | 0.0034 | 918469.7823 | 83782.329
September | 226781.8097 | 389.143 | 993.034 | 0 | 0.0039 | 1032550 | 96468.4766
October | 228339.5958 | 383.0796 | 952.5688 | 0 | 0.0038 | 990413.7897 | 96274.1683
November | 243307.9761 | 384.625 | 887.4579 | 0 | 0.0036 | 922552.3978 | 100273.603
December | 271120.7634 | 411.0045 | 893.7125 | 0 | 0.0036 | 928914.5069 | 110010.8485
Annual Sum or Average | 2836730 | 4629.6946 | 11133.5931 | 0 | 0.0442 | 11575000 | 1183350
Minimum of Months | 190184.1251 | 331.4299 | 816.82 | 0 | 0.0033 | 849023.9048 | 81399.4451
Maximum of Months | 274877.0784 | 430.6122 | 1106.8873 | 0 | 0.0043 | 1150950 | 111726.5494
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 755380000000 | 590083.788 | 27-JAN-11:50 | 270589.05 | 151653.867 | 96818.898 | 0 | 64123.217 | 0 | 114.959 | 0 | 0 | 0 | 0 | 0 | 6783.796 | 0 | 0
February | 673116000000 | 572530.124 | 07-FEB-14:00 | 270589.05 | 145652.643 | 101139.216 | 0 | 50405.643 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4628.904 | 0 | 0
March | 783668000000 | 706130.638 | 30-MAR-15:00 | 270589.05 | 133019.064 | 114983.003 | 0 | 182651.318 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4773.535 | 0 | 0
April | 727215000000 | 774961.354 | 25-APR-14:00 | 270589.05 | 137835.548 | 117810.924 | 0 | 243460.906 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5150.258 | 0 | 0
May | 815857000000 | 863351.207 | 23-MAY-15:00 | 270589.05 | 133019.064 | 123596.09 | 0 | 330965.557 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5066.778 | 0 | 0
June | 912486000000 | 966690.747 | 28-JUN-11:00 | 270589.05 | 151653.867 | 125596.524 | 0 | 413265.725 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5470.913 | 0 | 0
July | 709229000000 | 781564.978 | 18-JUL-13:00 | 150327.25 | 84617.158 | 123753.993 | 0 | 417483.989 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5267.92 | 0 | 0
August | 728174000000 | 799885.477 | 30-AUG-13:00 | 150327.25 | 84617.158 | 125572.268 | 0 | 434004.307 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5249.826 | 0 | 0
September | 818616000000 | 913658.615 | 05-SEP-13:00 | 270589.05 | 145652.643 | 124843.114 | 0 | 367024.776 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5434.364 | 0 | 0
October | 785212000000 | 836954.155 | 05-OCT-15:09 | 270589.05 | 133019.064 | 117244.612 | 0 | 310937.616 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5049.145 | 0 | 0
November | 731411000000 | 652418.495 | 10-NOV-13:00 | 270589.05 | 145652.643 | 105717.126 | 0 | 125365.74 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4979.267 | 0 | 0
December | 736455000000 | 568105.385 | 21-DEC-14:09 | 270589.05 | 145652.643 | 99543.029 | 0 | 47584.181 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4621.814 | 0 | 0
Annual Sum or Average | 9176820000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 673116000000 | 568105.385 |  | 150327.25 | 84617.158 | 96818.898 | 0 | 47584.181 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4621.814 | 0 | 0
Maximum of Months | 912486000000 | 966690.747 |  | 270589.05 | 151653.867 | 125596.524 | 0 | 434004.307 | 0 | 114.959 | 0 | 0 | 0 | 0 | 0 | 6783.796 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 94325.75 | 54698.09 | 0 | 149023.83
Cost per Total Building Area ($/m2) | 4.81 | 2.79 | 0 | 7.61
Cost per Net Conditioned Building Area ($/m2) | 4.81 | 2.79 | 0 | 7.61

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 23674.24 | 1208.36 | 1208.36
Net Site Energy | 23674.24 | 1208.36 | 1208.36
Total Source Energy | 47891.56 | 2444.44 | 2444.44
Net Source Energy | 47891.56 | 2444.44 | 2444.44
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13490.43 | 0 | 0 | 0 | 0
Cooling | 1064.06 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1584.43 | 0 | 0 | 0 | 0 | 0
Pumps | 18.42 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 432.01 | 0 | 0 | 0 | 2677.93
Refrigeration | 134.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9398.42 | 14275.83 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 753.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 1335.99 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1408336.45 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 103624.02 | 70058.46 | 33565.56 | 0.68 | 3.33
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14194.49 | 9596.66 | 4597.83 | 0.68 | 3.32
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 349093.89 | 236563.85 | 112530.04 | 0.68 | 3.1
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 242156.25 | 163717.78 | 78438.47 | 0.68 | 3.1
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 242079.51 | 163665.89 | 78413.61 | 0.68 | 3.1
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 259223.78 | 175256.85 | 83966.93 | 0.68 | 3.1
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10209.02 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12801.4 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6635.32 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9006.29 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6548.72 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8966.63 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6553.11 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8987.25 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6036.71 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8488.93 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6027.71 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8492.89 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6116.21 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8541.45 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5307.94 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10137.16 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4548.07 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10065.77 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4613.91 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10216.85 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31359.47 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4638.61 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8897.74 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27706.08 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38479.95 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10613.34 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6521.31 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14875.03 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23978.91 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15990.64 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23805.94 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16054.98 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27296.87 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13831.19 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19988.95 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13852.07 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20011.97 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14000.12 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23754.88 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16050.55 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24010.62 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1531107.56 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 299881.96 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 612443.02 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 44291.48 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 347847.23 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 160999.05 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 172331.95 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 172333.89 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 172866.19 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.17 | 7959.59 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.57 | 663.02 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.15 | 23970.75 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.75 | 16776.3 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.75 | 16770.99 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.44 | 17958.72 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7754.9 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 346396.3938 | 469.0965 | 505.2296 | 0 | 0.0041 | 331509.1559 | 134672.8365
February | 285047.7948 | 396.6229 | 450.2849 | 0 | 0.0036 | 295537.1403 | 111835.35
March | 263114.2267 | 394.3905 | 507.7425 | 0 | 0.0039 | 333445.986 | 105933.7767
April | 190129.4186 | 313.5545 | 459.9075 | 0 | 0.0034 | 302194.8623 | 79279.2583
May | 205498.5129 | 360.926 | 568.8022 | 0 | 0.0042 | 373847.5957 | 87793.1225
June | 234821.1955 | 423.7151 | 686.7215 | 0 | 0.005 | 451395.5136 | 101399.3796
July | 166954.4862 | 302.1264 | 491.0856 | 0 | 0.0036 | 322803.4576 | 72176.764
August | 176379.2432 | 319.0626 | 518.4199 | 0 | 0.0038 | 340770.59 | 76239.8297
September | 183847.2215 | 326.4104 | 520.3074 | 0 | 0.0038 | 341988.1757 | 78878.908
October | 200343.6295 | 330.2114 | 484.0028 | 0 | 0.0036 | 318026.5058 | 83520.3654
November | 246454.2233 | 371.399 | 482.0425 | 0 | 0.0037 | 316579.5287 | 99415.5357
December | 304917.2212 | 427.098 | 490.8818 | 0 | 0.0039 | 322201.9445 | 119901.2486
Annual Sum or Average | 2803900 | 4434.6134 | 6165.4281 | 0 | 0.0465 | 4050300 | 1151050
Minimum of Months | 166954.4862 | 302.1264 | 450.2849 | 0 | 0.0034 | 295537.1403 | 72176.764
Maximum of Months | 346396.3938 | 469.0965 | 686.7215 | 0 | 0.005 | 451395.5136 | 134672.8365
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 769242000000 | 522748.713 | 04-JAN-11:20 | 270589.05 | 151653.867 | 89384.491 | 0 | 0 | 0 | 5225.193 | 0 | 0 | 0 | 0 | 0 | 5896.113 | 0 | 0
February | 685772000000 | 519895.259 | 01-FEB-11:09 | 270589.05 | 151653.867 | 89384.491 | 0 | 0 | 0 | 2366.057 | 0 | 0 | 0 | 0 | 0 | 5901.794 | 0 | 0
March | 773736000000 | 587377.363 | 23-MAR-13:00 | 270589.05 | 145652.643 | 94456.932 | 0 | 71836.163 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4727.907 | 0 | 0
April | 701220000000 | 701163.483 | 14-APR-15:00 | 270589.05 | 133019.064 | 102349.856 | 0 | 190326.423 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4764.422 | 0 | 0
May | 867485000000 | 1024668.593 | 31-MAY-11:00 | 270589.05 | 151653.867 | 112157.658 | 0 | 484765.613 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5387.738 | 0 | 0
June | 1047430000000 | 1148407.172 | 29-JUN-13:00 | 270589.05 | 145652.643 | 128789.922 | 0 | 597777.147 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5483.742 | 0 | 0
July | 749041000000 | 947933.227 | 13-JUL-14:00 | 150327.25 | 78000.308 | 119295.276 | 0 | 594976.558 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5219.168 | 0 | 0
August | 790732000000 | 927646.626 | 25-AUG-15:00 | 150327.25 | 73183.824 | 121459.261 | 0 | 577544.554 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5017.069 | 0 | 0
September | 793558000000 | 1015724.363 | 14-SEP-14:00 | 270589.05 | 137835.548 | 118837.757 | 0 | 482988.557 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5358.783 | 0 | 0
October | 737957000000 | 749468.458 | 06-OCT-14:00 | 270589.05 | 137835.548 | 103948.176 | 0 | 231913.891 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5067.126 | 0 | 0
November | 734599000000 | 641531.99 | 02-NOV-14:00 | 270589.05 | 137835.548 | 101143.693 | 0 | 127016.479 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4832.553 | 0 | 0
December | 747645000000 | 519481.155 | 18-DEC-11:09 | 270589.05 | 151653.867 | 89384.491 | 0 | 0 | 0 | 1949.488 | 0 | 0 | 0 | 0 | 0 | 5904.259 | 0 | 0
Annual Sum or Average | 9398420000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 685772000000 | 519481.155 |  | 150327.25 | 73183.824 | 89384.491 | 0 | 0 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4727.907 | 0 | 0
Maximum of Months | 1047430000000 | 1148407.172 |  | 270589.05 | 151653.867 | 128789.922 | 0 | 597777.147 | 0 | 5225.193 | 0 | 0 | 0 | 0 | 0 | 5904.259 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 168149.81 | 112459.6 | 0 | 280609.41
Cost per Total Building Area ($/m2) | 8.58 | 5.74 | 0 | 14.32
Cost per Net Conditioned Building Area ($/m2) | 8.58 | 5.74 | 0 | 14.32

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 20198.46 | 1030.95 | 1030.95
Net Site Energy | 20198.46 | 1030.95 | 1030.95
Total Source Energy | 43041.24 | 2196.88 | 2196.88
Net Source Energy | 43041.24 | 2196.88 | 2196.88
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10607.56 | 0 | 0 | 0 | 0
Cooling | 488.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.91 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1569.71 | 0 | 0 | 0 | 0 | 0
Pumps | 15.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 435.27 | 0 | 0 | 0 | 2677.93
Refrigeration | 132.04 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8802.23 | 11396.23 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 753.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 1335.99 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1289399.14 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 327098.16 | 261238.67 | 65859.49 | 0.8 | 3.52
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91187.38 | 67159.43 | 24027.95 | 0.74 | 3.59
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130839.27 | 104495.47 | 26343.8 | 0.8 | 3.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10031.4 | 7432.73 | 2598.67 | 0.74 | 3.47
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 88148.52 | 65313.34 | 22835.19 | 0.74 | 3.61
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 248207.38 | 198232.13 | 49975.25 | 0.8 | 3.53
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 151339.78 | 120868.31 | 30471.47 | 0.8 | 3.89
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 151696.18 | 121152.95 | 30543.23 | 0.8 | 3.89
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 163718.4 | 130754.56 | 32963.84 | 0.8 | 3.72
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9791.86 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12508.99 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5424.25 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7900.09 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5340.42 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7860.92 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5345.72 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7883.25 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5052.49 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7247.29 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5057.12 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7250.4 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5072.47 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7303.37 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4153.04 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8837.46 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4375.66 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8840.61 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4427.33 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8874.09 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27039.74 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4511.34 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8741.22 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 26908.44 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38021.87 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9399.71 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6319.41 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13712.49 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21070 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13439.02 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20976.44 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13446.63 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24501.5 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13310 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17317.66 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13331.17 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17323.46 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13484.5 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20185.3 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13002.75 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21098.71 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1395210.11 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 281161.49 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 558084.04 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 36071.91 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 316973.14 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 147199.63 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 157055.11 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 157096.57 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 158112.18 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.58 | 8730.95 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 592.57 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.99 | 25404.57 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 9.14 | 17151.12 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 9.16 | 17191.51 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.89 | 17014.74 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7099.98 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 304243.3984 | 432.8158 | 567.9179 | 0 | 0.0042 | 13457800 | 120441.7108
February | 252298.2441 | 369.2593 | 508.3506 | 0 | 0.0037 | 12048700 | 100877.5868
March | 250216.6599 | 387.2939 | 580.3966 | 0 | 0.0042 | 13760900 | 102083.0832
April | 207604.8575 | 330.3107 | 514.0055 | 0 | 0.0037 | 12188600 | 85565.7211
May | 205904.3677 | 345.8817 | 575.8925 | 0 | 0.004 | 13659300 | 86631.5325
June | 215185.1869 | 372.2806 | 640.9397 | 0 | 0.0045 | 15203900 | 91581.1277
July | 153368.8511 | 269.2682 | 471.0396 | 0 | 0.0033 | 11174200 | 65652.7382
August | 155133.1513 | 269.3332 | 465.4914 | 0 | 0.0032 | 11042200 | 66114.8531
September | 192733.9763 | 329.7801 | 560.8355 | 0 | 0.0039 | 13303200 | 81672.3927
October | 207676.6689 | 340.6114 | 551.0224 | 0 | 0.0039 | 13068100 | 86579.9721
November | 240279.7806 | 368.2731 | 544.1825 | 0 | 0.0039 | 12901600 | 97677.1733
December | 287305.3194 | 412.9492 | 551.596 | 0 | 0.0041 | 13072000 | 114145.2166
Annual Sum or Average | 2671950 | 4228.0572 | 6531.6702 | 0 | 0.0465 | 154881000 | 1099020
Minimum of Months | 153368.8511 | 269.2682 | 465.4914 | 0 | 0.0032 | 11042200 | 65652.7382
Maximum of Months | 304243.3984 | 432.8158 | 640.9397 | 0 | 0.0045 | 15203900 | 120441.7108
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 764840000000 | 528842.492 | 05-JAN-08:09 | 270589.05 | 145652.643 | 91011.583 | 0 | 0 | 11207 | 6501.495 | 0 | 0 | 0 | 0 | 0 | 3880.72 | 0 | 0
February | 684757000000 | 583949.125 | 02-FEB-14:00 | 270589.05 | 145652.643 | 96120.994 | 0 | 66664.907 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4806.863 | 0 | 0
March | 782067000000 | 644310.655 | 30-MAR-15:00 | 270589.05 | 133019.064 | 111260.694 | 0 | 124632.127 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4695.052 | 0 | 0
April | 692704000000 | 610342.093 | 06-APR-15:00 | 270589.05 | 133019.064 | 102816.854 | 0 | 99181.322 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4621.135 | 0 | 0
May | 776292000000 | 738005.993 | 16-MAY-15:00 | 270589.05 | 133019.064 | 115694.851 | 0 | 213699.343 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4889.017 | 0 | 0
June | 864072000000 | 913838.353 | 30-JUN-12:00 | 270589.05 | 145652.643 | 132035.653 | 0 | 359885.165 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5561.174 | 0 | 0
July | 635057000000 | 699604.862 | 21-JUL-14:00 | 150327.25 | 78000.308 | 127621.888 | 0 | 338389.298 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5151.45 | 0 | 0
August | 627552000000 | 654552.017 | 09-AUG-15:00 | 150327.25 | 73183.824 | 110883.058 | 0 | 315139.627 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4903.589 | 0 | 0
September | 756050000000 | 797941.174 | 12-SEP-13:00 | 270589.05 | 145652.643 | 126239.48 | 0 | 250065.454 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5279.879 | 0 | 0
October | 742694000000 | 701828.854 | 06-OCT-15:00 | 270589.05 | 133019.064 | 116023.955 | 0 | 177269.832 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4812.285 | 0 | 0
November | 733230000000 | 543791.495 | 21-NOV-12:00 | 270589.05 | 151653.867 | 92031.791 | 0 | 24790.386 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4611.733 | 0 | 0
December | 742915000000 | 528748.834 | 18-DEC-08:09 | 270589.05 | 145652.643 | 91011.583 | 0 | 0 | 11207 | 6424.514 | 0 | 0 | 0 | 0 | 0 | 3864.045 | 0 | 0
Annual Sum or Average | 8802230000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 627552000000 | 528748.834 |  | 150327.25 | 73183.824 | 91011.583 | 0 | 0 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 3864.045 | 0 | 0
Maximum of Months | 864072000000 | 913838.353 |  | 270589.05 | 151653.867 | 132035.653 | 0 | 359885.165 | 11207 | 6501.495 | 0 | 0 | 0 | 0 | 0 | 5561.174 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 190075.65 | 92896.79 | 0 | 282972.44
Cost per Total Building Area ($/m2) | 9.7 | 4.74 | 0 | 14.44
Cost per Net Conditioned Building Area ($/m2) | 9.7 | 4.74 | 0 | 14.44

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25997.46 | 1326.94 | 1326.94
Net Site Energy | 25997.46 | 1326.94 | 1326.94
Total Source Energy | 48828.58 | 2492.27 | 2492.27
Net Source Energy | 48828.58 | 2492.27 | 2492.27
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16442.68 | 0 | 0 | 0 | 0
Cooling | 390.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 175.8 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1575.51 | 0 | 0 | 0 | 0 | 0
Pumps | 23.51 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 485.25 | 0 | 0 | 0 | 2677.93
Refrigeration | 129.59 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8716.14 | 17281.32 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 753.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 1335.99 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1436276.6 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 490687.86 | 331745.83 | 158942.03 | 0.68 | 3.09
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 112036.05 | 75745.69 | 36290.36 | 0.68 | 3.33
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 196275.14 | 132698.33 | 63576.81 | 0.68 | 3.31
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12183.35 | 8236.96 | 3946.39 | 0.68 | 3.32
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 111477.74 | 75368.23 | 36109.51 | 0.68 | 3.33
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 323571.6 | 228138.59 | 95433.01 | 0.71 | 3.18
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 223754.26 | 151276.5 | 72477.76 | 0.68 | 3.17
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 223585.79 | 151162.6 | 72423.19 | 0.68 | 3.17
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 229699.29 | 155295.83 | 74403.45 | 0.68 | 3.17
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10550.83 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13301.34 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5590.89 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8062.25 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5580.35 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8023.06 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5581.91 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8044.7 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5555.81 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7438.18 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5560.39 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7441.11 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5574.46 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 7492.69 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4455.41 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9152.75 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4682.4 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9155.18 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4730.98 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9203.21 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27552.08 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4884.83 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 9233.52 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 28547.34 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39809.68 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 9258.37 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 6410.89 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15042.44 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21625.2 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14779.28 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21505.89 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14786.26 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25010.83 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14644.33 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18773.62 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14665.25 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18779.06 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14809.39 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20725.84 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14279.81 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 21474.54 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1567205.23 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 313930.12 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 626882.09 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 38912.33 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 356048.14 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 168563.59 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 177169.73 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 177157.31 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 177723.56 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.51 | 8605.74 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 569.08 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.57 | 24687.57 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 9.01 | 16903.76 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 9 | 16891.04 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 9.25 | 17352.89 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 7908.75 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 351082.6809 | 474.2751 | 508.2624 | 0 | 0.0041 | 333490.354 | 136383.1658
February | 297921.7122 | 409.9154 | 455.5764 | 0 | 0.0036 | 298977.8607 | 116444.6275
March | 295829.4621 | 426.6837 | 516.351 | 0 | 0.004 | 339003.6345 | 117504.8541
April | 213663.1856 | 334.4053 | 458.3522 | 0 | 0.0035 | 301091.0177 | 87375.4936
May | 200104.3912 | 332.4451 | 491.9818 | 0 | 0.0037 | 323281.295 | 83671.8248
June | 195505.565 | 347.4955 | 554.5598 | 0 | 0.0041 | 364503.1168 | 83917.8029
July | 141550.5777 | 253.9506 | 409.1851 | 0 | 0.003 | 268959.8456 | 60983.6254
August | 142944.0783 | 250.5283 | 393.929 | 0 | 0.0029 | 258909.3545 | 61017.8788
September | 180604.6963 | 307.9943 | 469.9102 | 0 | 0.0035 | 308813.7353 | 76277.6626
October | 211368.2899 | 338.7195 | 479.1724 | 0 | 0.0036 | 314808.4355 | 87192.7271
November | 258802.6758 | 383.7918 | 485.9551 | 0 | 0.0037 | 319114.0262 | 103802.5403
December | 321557.9695 | 443.6588 | 495.6991 | 0 | 0.0039 | 325317.7272 | 125799.8057
Annual Sum or Average | 2810940 | 4303.8635 | 5718.9344 | 0 | 0.0436 | 3756270 | 1140370
Minimum of Months | 141550.5777 | 250.5283 | 393.929 | 0 | 0.0029 | 258909.3545 | 60983.6254
Maximum of Months | 351082.6809 | 474.2751 | 554.5598 | 0 | 0.0041 | 364503.1168 | 136383.1658
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 773839000000 | 525142.594 | 09-JAN-11:09 | 270589.05 | 151653.867 | 90369.642 | 0 | 0 | 0 | 6654.398 | 0 | 0 | 0 | 0 | 0 | 5875.638 | 0 | 0
February | 693756000000 | 523101.423 | 01-FEB-10:09 | 270589.05 | 151653.867 | 90369.642 | 0 | 0 | 0 | 6502.611 | 0 | 0 | 0 | 0 | 0 | 3986.253 | 0 | 0
March | 786632000000 | 520529.197 | 07-MAR-11:09 | 270589.05 | 151653.867 | 90369.642 | 0 | 0 | 0 | 1992.028 | 0 | 0 | 0 | 0 | 0 | 5924.61 | 0 | 0
April | 698659000000 | 586172.309 | 04-APR-14:00 | 270589.05 | 137835.548 | 95549.593 | 0 | 77369.238 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4714.213 | 0 | 0
May | 750150000000 | 764422.576 | 31-MAY-15:00 | 270589.05 | 133019.064 | 111648.978 | 0 | 244211.217 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4839.599 | 0 | 0
June | 845802000000 | 1015822.931 | 14-JUN-15:09 | 270589.05 | 133019.064 | 124996.279 | 0 | 481777.227 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5326.643 | 0 | 0
July | 624101000000 | 824545.251 | 06-JUL-14:00 | 150327.25 | 78000.308 | 106267.2 | 0 | 484677.209 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5158.617 | 0 | 0
August | 600780000000 | 765674.562 | 11-AUG-14:00 | 150327.25 | 78000.308 | 100971.209 | 0 | 431173.627 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5087.5 | 0 | 0
September | 716579000000 | 908323.661 | 07-SEP-14:00 | 270589.05 | 137835.548 | 114869.776 | 0 | 379690.092 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 5224.527 | 0 | 0
October | 730489000000 | 618288.588 | 06-OCT-14:00 | 270589.05 | 137835.548 | 102473.12 | 0 | 102504.032 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4772.172 | 0 | 0
November | 740480000000 | 532022.077 | 09-NOV-12:00 | 270589.05 | 151653.867 | 93926.291 | 0 | 11119.681 | 0 | 138.56 | 0 | 0 | 0 | 0 | 0 | 4594.628 | 0 | 0
December | 754875000000 | 522081.417 | 11-DEC-10:09 | 270589.05 | 151653.867 | 90369.642 | 0 | 0 | 0 | 5503.72 | 0 | 0 | 0 | 0 | 0 | 3965.138 | 0 | 0
Annual Sum or Average | 8716140000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 600780000000 | 520529.197 |  | 150327.25 | 78000.308 | 90369.642 | 0 | 0 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 3965.138 | 0 | 0
Maximum of Months | 845802000000 | 1015822.931 |  | 270589.05 | 151653.867 | 124996.279 | 0 | 484677.209 | 0 | 6654.398 | 0 | 0 | 0 | 0 | 0 | 5924.61 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 151564.92 | 136057.57 | 0 | 287622.49
Cost per Total Building Area ($/m2) | 7.74 | 6.94 | 0 | 14.68
Cost per Net Conditioned Building Area ($/m2) | 7.74 | 6.94 | 0 | 14.68

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 38470.36 | 1963.57 | 1963.57
Net Site Energy | 38470.36 | 1963.57 | 1963.57
Total Source Energy | 63640.35 | 3248.28 | 3248.28
Net Source Energy | 63640.35 | 3248.28 | 3248.28
Area [m2]
Total Building Area | 19592
Net Conditioned Building Area | 19592
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 28846.62 | 0 | 0 | 0 | 0
Cooling | 157.34 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 4143.3 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 174.73 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 2277.82 | 353.39 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1789.74 | 0 | 0 | 0 | 0 | 0
Pumps | 53.36 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 548.27 | 0 | 0 | 0 | 2677.93
Refrigeration | 125.78 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8722.06 | 29748.29 | 0 | 0 | 0 | 2677.93
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
AUDITORIUM_ZN_1_FLR_1 | 988 | Yes | 7904 | 1 | 512 | 106.4 | 12.08 | 1 | 5
AUX_GYM_ZN_1_FLR_1 | 1248 | Yes | 9984 | 1 | 608 | 212.8 | 11.81 | 3.33 | 5
BATHROOMS_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
BATHROOMS_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 116 | 25.2 | 9.6 | 10 | 4
CAFETERIA_ZN_1_FLR_1 | 624 | Yes | 2496 | 1 | 200 | 70 | 14.38 | 1.39 | 19.26
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | Yes | 396 | 1 | 80 | 28 | 21.52 | 4 | 10
CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 14.38 | 10 | 4
CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | Yes | 1280 | 1 | 20 | 7 | 9.25 | 10 | 4
GYM_ZN_1_FLR_1 | 1976 | Yes | 15808 | 1 | 0 | 0 | 11.38 | 1 | 5
KITCHEN_ZN_1_FLR_1 | 216 | Yes | 864 | 1 | 36 | 12.6 | 16.76 | 6.67 | 1344.4722
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | Yes | 3360 | 1 | 236 | 83.01 | 16.33 | 4.35 | 10
LOBBY_ZN_1_FLR_1 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
LOBBY_ZN_1_FLR_2 | 210 | Yes | 840 | 1 | 60 | 21 | 12 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | Yes | 4560 | 1 | 200 | 49 | 10.74 |  | 4
MECH_ZN_1_FLR_1 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 97.8886
MECH_ZN_1_FLR_2 | 342 | Yes | 1368 | 1 | 0 | 0 | 8.05 | 100 | 4
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 14.38 | 4 | 10
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | Yes | 1908 | 1 | 212 | 74.2 | 21.52 | 4 | 10
OFFICES_ZN_1_FLR_1 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
OFFICES_ZN_1_FLR_2 | 532 | Yes | 2128 | 1 | 208 | 72.8 | 20.09 | 20 | 10.8
Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Conditioned Total | 19592 |  | 95216 |  | 6384 | 2089.18 | 15.3458 | 3.25 | 23.8618
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 152 | 0 | 90 | N
AUDITORIUM_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 104 | 270 | 90 | W
AUDITORIUM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 988 | 270 | 180
AUDITORIUM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 988 | 90 | 0
AUX_GYM_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 96 | 180 | 90 | S
AUX_GYM_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 208 | 90 | 90 | E
AUX_GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1248 | 270 | 180
AUX_GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1248 | 90 | 0
BATHROOMS_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
BATHROOMS_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 12 | 90 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60 | 0 | 90 | N
BATHROOMS_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 210 | 90 | 0
CAFETERIA_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 104 | 90 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 96 | 0 | 90 | N
CAFETERIA_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 624 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 180 | 90 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 99 | 270 | 180
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 44 | 0 | 90 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 270 | 90 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 99 | 90 | 0
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 20 | 270 | 90 | W
CORRIDOR_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 20 | 270 | 90 | W
CORRIDOR_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 320 | 270 | 180
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 20 | 270 | 90 | W
CORRIDOR_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 320 | 90 | 0
GYM_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1976 | 270 | 180
GYM_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1976 | 90 | 0
KITCHEN_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36 | 90 | 90 | E
KITCHEN_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 216 | 270 | 180
LIBRARY_MEDIA_CENTER_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 140 | 90 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 96 | 0 | 90 | N
LIBRARY_MEDIA_CENTER_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 840 | 90 | 0
LOBBY_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 210 | 270 | 180
LOBBY_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60 | 180 | 90 | S
LOBBY_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 210 | 90 | 0
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 1140 | 270 | 180
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 68 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 60 | 90 | 90 | E
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 72 | 270 | 90 | W
MAIN_CORRIDOR_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1140 | 90 | 0
MECH_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 342 | 270 | 180
MECH_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 342 | 90 | 0
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 180 | 90 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 477 | 270 | 180
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 212 | 0 | 90 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 477 | 90 | 0
OFFICES_ZN_1_FLR_1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_1_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 532 | 270 | 180
OFFICES_ZN_1_FLR_2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 152 | 180 | 90 | S
OFFICES_ZN_1_FLR_2_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 56 | 90 | 90 | E
OFFICES_ZN_1_FLR_2_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 532 | 90 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
AUDITORIUM_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_1_WALL_3 | 0 | N
AUDITORIUM_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | AUDITORIUM_ZN_1_FLR_2_WALL_3 | 0 | N
AUX_GYM_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_1_WALL_2 | 90 | E
AUX_GYM_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_1 | 180 | S
AUX_GYM_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 72.8 | 72.8 | 3.525 | 0.407 | 0.316 | No | AUX_GYM_ZN_1_FLR_2_WALL_2 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_1_WALL_4 | 0 | N
BATHROOMS_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 4.2 | 4.2 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_3 | 90 | E
BATHROOMS_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | BATHROOMS_ZN_1_FLR_2_WALL_4 | 0 | N
CAFETERIA_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 36.4 | 36.4 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_2 | 90 | E
CAFETERIA_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | CAFETERIA_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_1_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_1_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_2_ZN_1_FLR_2_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_1_WALL_4 | 270 | W
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 15.4 | 15.4 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | CORNER_CLASS_2_POD_3_ZN_1_FLR_2_WALL_4 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_1_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_2_ZN_1_FLR_2_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_1_WALL_6 | 270 | W
CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6_WINDOW_1 | WINDOW-NONRES-FIXED | 7 | 7 | 3.525 | 0.407 | 0.316 | No | CORRIDOR_POD_3_ZN_1_FLR_2_WALL_6 | 270 | W
KITCHEN_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 12.6 | 12.6 | 3.525 | 0.407 | 0.316 | No | KITCHEN_ZN_1_FLR_1_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 49.41 | 49.41 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_2 | 90 | E
LIBRARY_MEDIA_CENTER_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 33.6 | 33.6 | 3.525 | 0.407 | 0.316 | No | LIBRARY_MEDIA_CENTER_WALL_3 | 0 | N
LOBBY_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_1_WALL_1 | 180 | S
LOBBY_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 21 | 21 | 3.525 | 0.407 | 0.316 | No | LOBBY_ZN_1_FLR_2_WALL_1 | 180 | S
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_1_WALL_7 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11_WINDOW_1 | WINDOW-NONRES-FIXED | 23.8 | 23.8 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_11 | 270 | W
MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7_WINDOW_1 | WINDOW-NONRES-FIXED | 25.2 | 25.2 | 3.525 | 0.407 | 0.316 | No | MAIN_CORRIDOR_ZN_1_FLR_2_WALL_7 | 270 | W
MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_1_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_2_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_1_WALL_1 | 180 | S
MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_1_POD_3_ZN_1_FLR_2_WALL_1 | 180 | S
MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_1_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_2_ZN_1_FLR_2_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_1_WALL_3 | 0 | N
MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3_WINDOW_1 | WINDOW-NONRES-FIXED | 74.2 | 74.2 | 3.525 | 0.407 | 0.316 | No | MULT_CLASS_2_POD_3_ZN_1_FLR_2_WALL_3 | 0 | N
OFFICES_ZN_1_FLR_1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_1_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_1_WALL_2 | 90 | E
OFFICES_ZN_1_FLR_2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 53.2 | 53.2 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_1 | 180 | S
OFFICES_ZN_1_FLR_2_WALL_2_WINDOW_1 | WINDOW-NONRES-FIXED | 19.6 | 19.6 | 3.525 | 0.407 | 0.316 | No | OFFICES_ZN_1_FLR_2_WALL_2 | 90 | E
Total or Average |  |  | 2089.18 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 753.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 1335.99 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 1861354.34 | 0.78
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_1:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 327098.16 | 261238.67 | 65859.49 | 0.8 | 3.52
PSZ-AC_2:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 95317.01 | 76125.43 | 19191.58 | 0.8 | 3.89
PSZ-AC_3:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130839.27 | 104495.47 | 26343.8 | 0.8 | 3.89
PSZ-AC_4:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9295.75 | 7424.1 | 1871.65 | 0.8 | 3.63
PSZ-AC_5:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 74312.34 | 59349.94 | 14962.4 | 0.8 | 3.93
CAV_OTHER_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 293387.23 | 234315.26 | 59071.98 | 0.8 | 3.52
CAV_POD_1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 188881.8 | 150851.45 | 38030.36 | 0.8 | 3.7
CAV_POD_2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 188783.45 | 150772.89 | 38010.55 | 0.8 | 3.7
CAV_POD_3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 189276.92 | 151167.01 | 38109.91 | 0.8 | 3.7
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BATHROOMS_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13382.17 | -
BATHROOMS_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16433.05 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7432.95 | -
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8491.01 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7422.58 | -
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8486.22 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7424.21 | -
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8487.59 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7403.36 | -
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8485.1 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7408.07 | -
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8486.1 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7421.93 | -
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8491.3 | -
CORRIDOR_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6016.75 | -
CORRIDOR_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10719.37 | -
CORRIDOR_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6249.81 | -
CORRIDOR_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10724.27 | -
CORRIDOR_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6297.03 | -
CORRIDOR_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 10760.8 | -
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29971 | -
LOBBY_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6400.08 | -
LOBBY_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11233.74 | -
MAIN_CORRIDOR_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 34109.83 | -
MAIN_CORRIDOR_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 47864.03 | -
MECH_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 7883.84 | -
MECH_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 8404.08 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20125.03 | -
MULT_CLASS_1_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29798.62 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19861.62 | -
MULT_CLASS_1_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29465.27 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19868.89 | -
MULT_CLASS_1_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33042.3 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19748.36 | -
MULT_CLASS_2_POD_1_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24637.28 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19769.86 | -
MULT_CLASS_2_POD_2_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24642.78 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19918.69 | -
MULT_CLASS_2_POD_3_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24733.73 | -
OFFICES_ZN_1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 19255.18 | -
OFFICES_ZN_1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26441.3 | -
PSZ-AC_1:5_HEATC | Coil:Heating:Gas | 1940738.03 | 0.78
PSZ-AC_2:6_HEATC | Coil:Heating:Gas | 413575.32 | 0.78
PSZ-AC_3:7_HEATC | Coil:Heating:Gas | 776295.21 | 0.78
PSZ-AC_4:8_HEATC | Coil:Heating:Gas | 55153.55 | 0.78
PSZ-AC_5:9_HEATC | Coil:Heating:Gas | 440909.81 | 0.78
CAV_OTHER_HEATC | Coil:Heating:Water | 222515.11 | -
CAV_POD_1_HEATC | Coil:Heating:Water | 232910.29 | -
CAV_POD_2_HEATC | Coil:Heating:Water | 232901.35 | -
CAV_POD_3_HEATC | Coil:Heating:Water | 232978.87 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.3 | 110.95 | 1 | Zone Exhaust Fans
CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.63 | 0 | 1 | Zone Exhaust Fans
KITCHEN_ZN_1_FLR_1 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.26 | 0 | 1 | Zone Exhaust Fans
PSZ-AC_1:5_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 19.76 | 33263.22 | 1 | Fan Energy
PSZ-AC_2:6_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.76 | 10802.14 | 1 | Fan Energy
PSZ-AC_3:7_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14827.82 | 1 | Fan Energy
PSZ-AC_4:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 651.35 | 1 | Fan Energy
PSZ-AC_5:9_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.49 | 8562.86 | 1 | Fan Energy
CAV_OTHER_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 17.72 | 29835.09 | 1 | Fan Energy
CAV_POD_1_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.41 | 19332.47 | 1 | Fan Energy
CAV_POD_2_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.4 | 19322.4 | 1 | Fan Energy
CAV_POD_3_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.43 | 19372.91 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 10249.41 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 114.67 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 450777.3795 | 463.8596 | 1144.8741 | 0 | 0.0045 | 229482.5522 | 164426.0223
February | 384405.3099 | 397.9484 | 1026.243 | 0 | 0.004 | 205724.0336 | 140583.4081
March | 349756.581 | 372.5536 | 1152.8833 | 0 | 0.0043 | 231195.5784 | 129523.7026
April | 237175.7043 | 263.7069 | 1013.4313 | 0 | 0.0036 | 203302.9228 | 89536.0163
May | 182934.9119 | 216.5616 | 1057.0491 | 0 | 0.0036 | 212119.6117 | 71085.2209
June | 173411.5596 | 212.1075 | 1144.6986 | 0 | 0.0039 | 229733.8687 | 68434.0945
July | 116072.3076 | 141.7276 | 761.0594 | 0 | 0.0026 | 152739.0775 | 45768.2708
August | 129099.7797 | 153.6184 | 762.4567 | 0 | 0.0026 | 153006.257 | 50287.09
September | 183662.8952 | 213.2136 | 973.1816 | 0 | 0.0034 | 195274.0392 | 70720.2682
October | 270179.2437 | 296.9495 | 1082.2162 | 0 | 0.0039 | 217084.2837 | 101463.8175
November | 370902.4882 | 389.4946 | 1105.7787 | 0 | 0.0042 | 221712.751 | 136495.3874
December | 409288.0763 | 424.8754 | 1117.1003 | 0 | 0.0043 | 223947.0524 | 149863.1316
Annual Sum or Average | 3257670 | 3546.6167 | 12340.9724 | 0 | 0.045 | 2475320 | 1218190
Minimum of Months | 116072.3076 | 141.7276 | 761.0594 | 0 | 0.0026 | 152739.0775 | 45768.2708
Maximum of Months | 450777.3795 | 463.8596 | 1152.8833 | 0 | 0.0045 | 231195.5784 | 164426.0223
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 808607000000 | 545301.967 | 02-JAN-11:09 | 270589.05 | 151653.867 | 95765.864 | 0 | 0 | 11207 | 10280.62 | 0 | 0 | 0 | 0 | 0 | 5805.566 | 0 | 0
February | 724891000000 | 536931.646 | 03-FEB-08:39 | 270589.05 | 145652.643 | 95765.864 | 0 | 0 | 11207 | 9822.669 | 0 | 0 | 0 | 0 | 0 | 3894.419 | 0 | 0
March | 814643000000 | 536525.436 | 14-MAR-07:19 | 270589.05 | 145652.643 | 95765.864 | 0 | 0 | 11207 | 9415.091 | 0 | 0 | 0 | 0 | 0 | 3895.788 | 0 | 0
April | 716360000000 | 530208.272 | 25-APR-14:00 | 270589.05 | 137835.548 | 99261.374 | 0 | 18019.1 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4388.533 | 0 | 0
May | 747426000000 | 634174.064 | 24-MAY-15:09 | 270589.05 | 133019.064 | 111746.4 | 0 | 114049.952 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4654.929 | 0 | 0
June | 809492000000 | 793495.557 | 21-JUN-15:00 | 270589.05 | 133019.064 | 118439.445 | 0 | 266343.303 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4990.026 | 0 | 0
July | 538193000000 | 559426.974 | 21-JUL-15:00 | 150327.25 | 73183.824 | 104775.919 | 0 | 226335.708 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4689.605 | 0 | 0
August | 539134000000 | 559024.594 | 15-AUG-13:00 | 150327.25 | 84617.158 | 102265.476 | 0 | 216779.508 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4920.533 | 0 | 0
September | 688069000000 | 571366.012 | 07-SEP-14:00 | 270589.05 | 137835.548 | 99693.949 | 0 | 58534.101 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 4598.697 | 0 | 0
October | 764920000000 | 535861.241 | 03-OCT-13:00 | 270589.05 | 145652.643 | 97139.854 | 0 | 17869.318 | 0 | 122.486 | 0 | 0 | 0 | 0 | 0 | 4487.89 | 0 | 0
November | 781229000000 | 540526.035 | 27-NOV-10:09 | 270589.05 | 151653.867 | 95765.864 | 0 | 0 | 11207 | 7369.811 | 0 | 0 | 0 | 0 | 0 | 3940.443 | 0 | 0
December | 789102000000 | 544624.006 | 29-DEC-11:09 | 270589.05 | 151653.867 | 95765.864 | 0 | 0 | 11207 | 9556.448 | 0 | 0 | 0 | 0 | 0 | 5851.776 | 0 | 0
Annual Sum or Average | 8722060000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 538193000000 | 530208.272 |  | 150327.25 | 73183.824 | 95765.864 | 0 | 0 | 0 | 114.668 | 0 | 0 | 0 | 0 | 0 | 3894.419 | 0 | 0
Maximum of Months | 814643000000 | 793495.557 |  | 270589.05 | 151653.867 | 118439.445 | 0 | 266343.303 | 11207 | 10280.62 | 0 | 0 | 0 | 0 | 0 | 5851.776 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 232491.53 | 122923.23 | 0 | 355414.77
Cost per Total Building Area ($/m2) | 11.87 | 6.27 | 0 | 18.14
Cost per Net Conditioned Building Area ($/m2) | 11.87 | 6.27 | 0 | 18.14

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38 | 3909.96
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 49.15
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 80.38
|  |  | WE, WinterDesign, Hol, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8 | 4180.91
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 53.25
|  |  | WE, WinterDesign, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 85.8
|  |  | WE, WinterDesign, Hol, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05 | 1045.46
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 20.05
|  |  | WE, WinterDesign, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16 | 425.49
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
|  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 586.61
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1366.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5 | 2255.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2203.29
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 5.1 | 25.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5 | 1494.39
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 6.5 | 32.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25 | 1692.57
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 1.9 | 9.5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 7.45 | 37.25
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
|  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
|  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
Showers_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8 | 1848.37
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8
|  |  | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
|  |  | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | All | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560 | 10920 | 569400
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 03/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 09/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Kitchen_Exhaust_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2137.86
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 9/1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 7.15 | 35.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 3038 | 158410
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 454
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
HTGSETP_SCH_Setback | Temperature | Through 12/31 | SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | WD | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  |  | WE, Hol, Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
CLGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 4788 | 249660
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 | 31 | 660
CLGSETP_SCH_Setup | Temperature | Through 12/31 | SummerDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456 | 5208 | 271560
|  |  | WinterDesign | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WE | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
|  |  | WD, Hol, Other | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744
MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 118 | 6152.86
|  |  | WE, WinterDesign, Hol, Other | [24 empty] | 24 | bar: 1 to 24
MinOA_MotorizedDamper_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Kitchen_Sched | On/Off | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 14 | 70 | 3650
|  |  | WE, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Gym_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Gym_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Gym_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Gym_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720