## BuildingSummary
Building Summary Strip Mall pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Strip Mall
| Available Fuel Types | gas, electricity
| Principal Building Activity | Strip Mall
Form
| Total Floor Area (m2) | 2090 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 4
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105
| Skylight/TDD Percentage | 0.00%
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | 10 stores
| Floor to Ceiling Height (m) | 5.1816
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1184.13
| Net Dimensions - Total Area (m2) | 1059.67
| Wall to Skin Ratio | 0.36
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2090
| Net Dimensions - Total Area (m2) | 2090
| Roof to Skin Ratio | 0.64
Window
| Dimensions - Total Area (m2) | South: 124 East: 0.00 North: 0.00 West: 0.00 Total: 124
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2090
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.23 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
LGStore1 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 276.3003 | 20.75 | 6.1939 | 56.2472 | 60.2778 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.4124
SMStore1 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 60.2778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore2 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore3 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore4 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
LGStore2 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 157.8901 | 20.75 | 6.1939 | 56.2472 | 29.0625 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.1446
SMStore5 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore6 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore7 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
SMStore8 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 197.3602 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.6801
Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 337.4831
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 30.9242 | 32.2602 | 32.3994 | 31.3975 | 21.005 | 26.8056 | 15.2003 | 31.5323 | 21.4181 | 17.6467 | 40.9497 | 29.0944 | 46.4428 | 32.9001 | 49.3239 | 43.9881
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 74.7386 | 76.6973 | 72.2852 | 71.3971 | 52.7737 | 62.5909 | 41.9035 | 68.6541 | 51.0181 | 44.5408 | 64.0966 | 45.4772 | 71.3237 | 54.422 | 70.0655 | 73.3944
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 34.5694 | 35.6514 | 33.461 | 33.4601 | 24.8203 | 28.7329 | 19.6648 | 32.5042 | 23.8302 | 21.3882 | 29.9508 | 21.0982 | 29.2093 | 21.8541 | 28.6936 | 29.7394
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 28.373 | 29.9481 | 29.1791 | 29.1486 | 20.8422 | 24.5842 | 15.6942 | 27.8512 | 18.5668 | 17.5792 | 27.0011 | 18.644 | 30.7008 | 21.7591 | 31.4102 | 29.6449
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 27.7518 | 29.3225 | 28.7687 | 28.7411 | 20.4617 | 24.1812 | 15.3279 | 27.2129 | 18.1727 | 17.2077 | 26.9957 | 18.7902 | 30.6951 | 21.7549 | 31.7735 | 29.641
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 27.6558 | 29.226 | 28.7015 | 28.6771 | 20.3977 | 24.1102 | 15.2575 | 27.107 | 18.0959 | 17.1401 | 27.0138 | 18.8381 | 30.7143 | 21.77 | 31.8736 | 29.6577
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 49.539 | 52.5787 | 53.5737 | 53.2095 | 37.2563 | 44.5821 | 27.2423 | 48.4536 | 32.7774 | 30.9504 | 53.6483 | 38.6081 | 61.0332 | 43.7118 | 66.0625 | 58.9833
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 25.8247 | 27.3791 | 27.5098 | 27.4667 | 19.2788 | 22.9517 | 14.2082 | 25.256 | 16.9695 | 16.0765 | 27.0143 | 19.2504 | 30.7148 | 21.8314 | 33.0239 | 29.658
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 25.7173 | 27.2709 | 27.4442 | 27.3959 | 19.2125 | 22.8893 | 14.1497 | 25.1481 | 16.9079 | 16.0157 | 27.0057 | 19.2684 | 30.7056 | 21.846 | 33.0753 | 29.6482
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 25.8698 | 27.4348 | 27.5878 | 27.5036 | 19.2665 | 23.0035 | 14.1813 | 25.2713 | 16.9545 | 16.0659 | 27.1817 | 19.4001 | 30.8915 | 21.9725 | 33.2202 | 29.7834
Heating (kW)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 13.6194 | 28.6309 | 21.7233 | 34.6272 | 16.9767 | 27.138 | 21.5635 | 39.2475 | 31.9616 | 30.227 | 50.1305 | 41.5873 | 56.3638 | 53.0683 | 59.2004 | 80.1854
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 23.0067 | 49.4146 | 37.4997 | 59.8708 | 29.1431 | 46.929 | 37.2084 | 68.3313 | 55.4454 | 52.5698 | 87.3609 | 72.2667 | 98.2994 | 92.4157 | 103.3788 | 140.4107
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.251 | 21.0603 | 16.049 | 25.5883 | 12.3753 | 20.1307 | 15.8916 | 29.426 | 23.8319 | 22.6211 | 37.5939 | 31.0334 | 42.3155 | 39.7479 | 44.5716 | 60.6809
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9749 | 15.9783 | 25.4889 | 12.3171 | 20.0459 | 15.8235 | 29.3314 | 23.7401 | 22.5434 | 37.4866 | 30.9285 | 42.2027 | 39.6334 | 44.4576 | 60.5518
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9707 | 15.9749 | 25.4843 | 12.314 | 20.042 | 15.8201 | 29.3271 | 23.736 | 22.5397 | 37.4817 | 30.9238 | 42.1975 | 39.6283 | 44.4525 | 60.5465
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.982 | 15.9862 | 25.4987 | 12.3218 | 20.0563 | 15.83 | 29.342 | 23.7515 | 22.5517 | 37.4981 | 30.9407 | 42.2147 | 39.6465 | 44.4707 | 60.5692
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 41.7065 | 31.7089 | 50.6746 | 24.4526 | 39.7877 | 31.4266 | 58.3604 | 47.1633 | 44.8344 | 74.6534 | 61.5261 | 84.0751 | 78.9204 | 88.5689 | 120.6861
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9825 | 15.9865 | 25.4992 | 12.3221 | 20.0567 | 15.8304 | 29.3424 | 23.7519 | 22.5521 | 37.4986 | 30.9411 | 42.2153 | 39.647 | 44.4712 | 60.5697
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9785 | 15.9812 | 25.4929 | 12.3197 | 20.0493 | 15.8265 | 29.3351 | 23.7436 | 22.5465 | 37.4907 | 30.9324 | 42.207 | 39.6377 | 44.4618 | 60.5563
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.251 | 21.1098 | 16.0867 | 25.6435 | 12.4093 | 20.1749 | 15.9295 | 29.4749 | 23.8779 | 22.6615 | 37.6502 | 31.087 | 42.3741 | 39.8066 | 44.6286 | 60.7411
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.5 | 3.47 | 3.58 | 3.6 | 3.97 | 3.44 | 3.75 | 3.93 | 3.21 | 3.71 | 3.19 | 3.73 | 3.19 | 3.45
| PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.14 | 3.2 | 3.18 | 3.35 | 3.36 | 3.45 | 3.22 | 3.45 | 3.44 | 3.21 | 3.45 | 3.15 | 3.45 | 3.28 | 4.18
| PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.45 | 3.46 | 3.53 | 3.51 | 3.64 | 3.63 | 3.77 | 3.48 | 3.77 | 3.75 | 3.46 | 3.77 | 3.47 | 3.77 | 3.54 | 3.73
| PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.49 | 3.47 | 3.59 | 3.59 | 3.99 | 3.44 | 4.01 | 3.94 | 3.44 | 3.97 | 3.44 | 3.77 | 3.48 | 3.73
| PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.49 | 3.46 | 3.59 | 3.58 | 3.98 | 3.44 | 4 | 3.93 | 3.44 | 3.96 | 3.44 | 3.77 | 3.47 | 3.73
| PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.49 | 3.46 | 3.59 | 3.58 | 3.98 | 3.44 | 4 | 3.93 | 3.44 | 3.96 | 3.44 | 3.77 | 3.47 | 3.73
| PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.19 | 3.19 | 3.21 | 3.19 | 3.53 | 3.28 | 3.72 | 3.19 | 3.69 | 3.68 | 3.19 | 3.65 | 3.19 | 3.44 | 3.19 | 4.32
| PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.47 | 3.45 | 3.57 | 3.57 | 3.99 | 3.44 | 3.98 | 3.92 | 3.44 | 3.7 | 3.44 | 3.77 | 3.45 | 3.73
| PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.47 | 3.45 | 3.57 | 3.57 | 3.99 | 3.44 | 3.98 | 3.92 | 3.44 | 3.7 | 3.44 | 3.77 | 3.44 | 3.73
| PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.44 | 3.44 | 3.47 | 3.45 | 3.57 | 3.57 | 3.99 | 3.44 | 3.98 | 3.92 | 3.44 | 3.7 | 3.44 | 3.77 | 3.45 | 3.73
Heating Efficiency (%)
| PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 1.25 | 1.3 | 1.43 | 1.32 | 1.04 | 1.35 | 0.89 | 1.27 | 1.27 | 0.99 | 1.65 | 1.65 | 1.87 | 1.99 | 2.01 | 2.66
| PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 3.14 | 3.26 | 3.44 | 3.28 | 2.82 | 3.38 | 2.53 | 2.97 | 3.08 | 2.66 | 2.73 | 2.75 | 3.09 | 3.29 | 3.34 | 4.43
| PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 1.41 | 1.48 | 1.55 | 1.51 | 1.32 | 1.51 | 1.19 | 1.39 | 1.44 | 1.27 | 1.25 | 1.27 | 1.24 | 1.32 | 1.34 | 1.8
| PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 1.14 | 1.21 | 1.27 | 1.22 | 1.05 | 1.23 | 0.93 | 1.12 | 1.12 | 1 | 1.09 | 1.09 | 1.24 | 1.31 | 1.34 | 1.79
| PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 1.12 | 1.18 | 1.25 | 1.2 | 1.02 | 1.2 | 0.9 | 1.1 | 1.09 | 0.97 | 1.09 | 1.09 | 1.24 | 1.31 | 1.34 | 1.79
| PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 1.11 | 1.18 | 1.24 | 1.19 | 1.02 | 1.19 | 0.9 | 1.09 | 1.08 | 0.97 | 1.09 | 1.09 | 1.24 | 1.32 | 1.34 | 1.79
| PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.99 | 2.12 | 2.24 | 2.14 | 1.8 | 2.14 | 1.57 | 1.95 | 1.91 | 1.71 | 2.16 | 2.16 | 2.46 | 2.61 | 2.66 | 3.56
| PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 1.04 | 1.1 | 1.17 | 1.12 | 0.94 | 1.12 | 0.83 | 1.02 | 1 | 0.9 | 1.09 | 1.09 | 1.24 | 1.32 | 1.34 | 1.79
| PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 1.04 | 1.1 | 1.16 | 1.11 | 0.94 | 1.11 | 0.82 | 1.01 | 0.99 | 0.89 | 1.09 | 1.09 | 1.24 | 1.31 | 1.34 | 1.79
| PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 1.04 | 1.1 | 1.17 | 1.12 | 0.94 | 1.12 | 0.82 | 1.02 | 1 | 0.89 | 1.09 | 1.09 | 1.24 | 1.32 | 1.35 | 1.8
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.087258 | 0.12231 | 0.099023 | 0.0997 | 0.1318 | 0.099522 | 0.14923 | 0.077834 | 0.037317 | 0.075823 | 0.090483 | 0.037331 | 0.062078 | 0.075856 | 0.060798 | 0.095543
| Total Cost ($/m2) | 27.53 | 35.62 | 29.17 | 26.06 | 29.66 | 26.6 | 31.37 | 19.11 | 8.82 | 16.19 | 21.4 | 8.54 | 14.82 | 17.47 | 14.02 | 24.98
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011405 | 0.0080434 | 0.0081489 | 0.0095087 | 0.0086072 | 0.0076337 | 0.0085695 | 0.0096575 | 0.0068717 | 0.0084167 | 0.0083024 | 0.0069072 | 0.0078727 | 0.0080837 | 0.007862 | 0.0041226
| Total Cost ($/m2) | 0.11 | 1.24 | 1.02 | 3.11 | 0.83 | 1.63 | 2.3 | 5.63 | 2.85 | 4.39 | 6.71 | 4.21 | 8.33 | 7.02 | 10.45 | 8.95
Total Utility Costs
| Cost Intensity ($/m2) | 27.64 | 36.86 | 30.18 | 29.18 | 30.49 | 28.23 | 33.67 | 24.74 | 11.67 | 20.58 | 28.11 | 12.75 | 23.15 | 24.49 | 24.48 | 33.93
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 215180.5556 | 159297.2222 | 161144.4444 | 95255.5556 | 34361.1111 | 106708.3333 | 11238.8889 | 68530.5556 | 49336.1111 | 12633.3333 | 46694.4444 | 30036.1111 | 39688.8889 | 16977.7778 | 13744.4444 | 5125
| Interior Lighting | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500
| Exterior Lighting | 25672.2222 | 25661.1111 | 25655.5556 | 25652.7778 | 25633.3333 | 25627.7778 | 25641.6667 | 25625 | 25633.3333 | 25583.3333 | 25627.7778 | 25613.8889 | 25611.1111 | 25605.5556 | 25591.6667 | 25436.1111
| Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 84675 | 89780.5556 | 94916.6667 | 91563.8889 | 76366.6667 | 92366.6667 | 68544.4444 | 85141.6667 | 85322.2222 | 74252.7778 | 88152.7778 | 88377.7778 | 99600 | 104955.5556 | 108813.8889 | 181975
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 659505.5556 | 608716.6667 | 615694.4444 | 546450 | 470338.8889 | 558680.5556 | 439402.7778 | 513277.7778 | 494269.4444 | 446447.2222 | 494452.7778 | 478005.5556 | 498880.5556 | 481516.6667 | 482130.5556 | 546511.1111
Gas (MJ)
| Heating | 20070 | 323550 | 260860 | 684280 | 201250 | 446170 | 560450 | 1217970 | 865990 | 1090190 | 1688860 | 1274330 | 2212990 | 1815220 | 2779530 | 4538970
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 20070 | 323550 | 260860 | 684280 | 201250 | 446170 | 560450 | 1217970 | 865990 | 1090190 | 1688860 | 1274330 | 2212990 | 1815220 | 2779530 | 4538970
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2394290 | 2514930 | 2477360 | 2651490 | 1894470 | 2457410 | 2142300 | 3065760 | 2645360 | 2697400 | 3468890 | 2995150 | 4008950 | 3548680 | 4515200 | 6506420
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 370.5892 | 274.3456 | 277.5269 | 164.0514 | 59.1775 | 183.7757 | 19.3559 | 118.025 | 84.9679 | 21.7574 | 80.4183 | 51.7289 | 68.3532 | 29.2395 | 23.671 | 8.8264
| Interior Lighting (elec) | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506
| Exterior Lighting (elec) | 44.2133 | 44.1942 | 44.1846 | 44.1798 | 44.1464 | 44.1368 | 44.1607 | 44.132 | 44.1464 | 44.0602 | 44.1368 | 44.1129 | 44.1081 | 44.0985 | 44.0746 | 43.8067
| Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 145.8293 | 154.6223 | 163.4678 | 157.6936 | 131.5205 | 159.0761 | 118.0489 | 146.6331 | 146.944 | 127.8799 | 151.8189 | 152.2064 | 171.5335 | 180.757 | 187.4019 | 313.4018
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1135.8165 | 1048.3467 | 1060.364 | 941.1095 | 810.0291 | 962.1733 | 756.7502 | 883.9795 | 851.2429 | 768.8823 | 851.5586 | 823.2328 | 859.1842 | 829.2797 | 830.337 | 941.2147
Gas (MJ/m2)
| Heating (gas) | 9.6014 | 154.7849 | 124.7943 | 327.3566 | 96.2771 | 213.4458 | 268.1168 | 582.6716 | 414.2859 | 521.5422 | 807.9433 | 609.6339 | 1058.6848 | 868.3934 | 1329.7151 | 2171.4235
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 9.6014 | 154.7849 | 124.7943 | 327.3566 | 96.2771 | 213.4458 | 268.1168 | 582.6716 | 414.2859 | 521.5422 | 807.9433 | 609.6339 | 1058.6848 | 868.3934 | 1329.7151 | 2171.4235
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1145.4179 | 1203.1316 | 1185.1583 | 1268.4613 | 906.3062 | 1175.6143 | 1024.867 | 1466.6463 | 1265.5287 | 1290.4244 | 1659.5019 | 1432.8667 | 1917.8643 | 1697.6731 | 2160.052 | 3112.643
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 156.7858 | 147.545 | 132.7008 | 119.0716 | 128.1769 | 106.9628 | 99.2332 | 101.9945 | 102.0319 | 100.1572 | 102.4179 | 102.4609 | 104.3232 | 105.4559 | 105.7777 | 118.2173
| Feb | 164.1647 | 150.7083 | 139.4303 | 125.2027 | 124.1461 | 113.307 | 111.6877 | 101.9945 | 112.2096 | 100.1572 | 102.4179 | 102.4609 | 104.3232 | 105.4559 | 105.7777 | 118.2173
| Mar | 165.1596 | 154.7464 | 159.9526 | 134.5042 | 123.7903 | 127.2912 | 99.2332 | 128.5606 | 113.4608 | 104.0686 | 110.471 | 113.4054 | 104.3232 | 103.823 | 105.7777 | 118.2173
| Apr | 173.1874 | 175.3048 | 164.163 | 152.3814 | 132.3277 | 154.3552 | 117.2869 | 129.7423 | 131.8799 | 111.8866 | 113.8411 | 120.7578 | 118.6401 | 100.4892 | 101.59 | 112.3443
| May | 182.899 | 186.1855 | 185.7558 | 165.1371 | 129.4468 | 165.6708 | 119.0276 | 150.1617 | 136.8379 | 119.7763 | 145.7194 | 128.8313 | 174.3453 | 122.3815 | 121.5427 | 119.335
| Jun | 189.4036 | 187.7017 | 209.7804 | 177.9551 | 131.2448 | 190.7565 | 120.7125 | 181.2684 | 150.0523 | 124.8237 | 174.5768 | 141.0621 | 172.5632 | 148.3259 | 147.0612 | 141.589
| Jul | 184.2419 | 194.6958 | 207.5129 | 193.6818 | 139.5948 | 188.7469 | 129.9898 | 188.383 | 154.1478 | 135.6911 | 177.1088 | 147.9573 | 180.2291 | 148.4077 | 163.0302 | 149.0407
| Aug | 191.0918 | 194.4443 | 207.1161 | 185.0296 | 148.5076 | 187.3745 | 126.7521 | 189.8395 | 153.4311 | 131.5705 | 174.8374 | 150.4188 | 171.2228 | 143.0476 | 162.4619 | 140.6394
| Sep | 183.6725 | 192.1791 | 197.5627 | 173.9731 | 145.662 | 181.6622 | 141.6451 | 166.4931 | 140.712 | 148.4209 | 150.9934 | 139.9592 | 148.8367 | 135.1862 | 136.5718 | 113.7029
| Oct | 180.7823 | 171.4629 | 167.0242 | 159.3557 | 136.9903 | 155.9961 | 119.1003 | 144.9196 | 128.0012 | 109.698 | 126.3217 | 128.6958 | 132.488 | 117.7999 | 128.5413 | 118.2173
| Nov | 167.833 | 154.3861 | 152.2316 | 126.4635 | 131.0619 | 118.4147 | 99.2926 | 133.9356 | 108.4556 | 100.1902 | 125.5309 | 107.7488 | 104.8525 | 105.4559 | 105.7777 | 118.2173
| Dec | 158.3662 | 149.4271 | 131.4239 | 114.832 | 130.8495 | 116.1925 | 99.2332 | 101.9945 | 102.0319 | 100.1572 | 102.4179 | 102.4609 | 104.3232 | 105.4559 | 105.7777 | 118.2173
Time of Peak Electrical Demand
| Jan | 24-JAN-13:00 | 03-JAN-13:00 | 28-JAN-14:00 | 23-JAN-15:00 | 26-JAN-13:50 | 18-JAN-16:49 | 02-JAN-16:00 | 02-JAN-16:49 | 02-JAN-17:10 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 25-FEB-13:39 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-14:50 | 13-FEB-11:00 | 07-FEB-17:10 | 15-FEB-15:00 | 01-FEB-17:30 | 14-FEB-15:00 | 01-FEB-17:10 | 01-FEB-16:00 | 01-FEB-17:19 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 01-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-12:39 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-14:09 | 31-MAR-14:39 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-15:09 | 29-MAR-15:50 | 31-MAR-14:00 | 30-MAR-15:00 | 01-MAR-17:00 | 30-MAR-16:00 | 01-MAR-17:49 | 01-MAR-17:00
| Apr | 01-APR-14:39 | 29-APR-14:09 | 01-APR-15:39 | 15-APR-14:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 06-APR-16:00 | 04-APR-14:00 | 01-APR-09:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-14:00 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-14:00 | 04-MAY-14:50 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:50 | 29-JUN-14:09 | 28-JUN-14:39 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-14:00 | 24-JUL-14:09 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-14:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-16:00
| Aug | 21-AUG-14:30 | 31-AUG-14:09 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 05-AUG-12:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:09 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
| Sep | 07-SEP-13:00 | 16-SEP-13:50 | 09-SEP-14:00 | 11-SEP-13:50 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:09 | 02-SEP-14:00 | 02-SEP-15:09 | 05-SEP-14:09 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 02-SEP-15:00
| Oct | 06-OCT-14:20 | 12-OCT-14:00 | 14-OCT-13:00 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-14:50 | 31-OCT-12:00 | 20-OCT-14:39 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 23-OCT-08:09
| Nov | 07-NOV-15:09 | 03-NOV-14:30 | 13-NOV-15:09 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-16:40 | 13-NOV-16:00 | 04-NOV-12:00 | 08-NOV-17:10 | 04-NOV-16:49 | 02-NOV-14:00 | 10-NOV-13:00 | 02-NOV-16:00 | 06-NOV-17:10 | 13-NOV-17:00 | 01-NOV-08:09
| Dec | 16-DEC-12:00 | 19-DEC-15:09 | 09-DEC-15:20 | 01-DEC-15:09 | 19-DEC-12:00 | 05-DEC-14:00 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 7897.21 | 8312.41 | 7295.64 | 7364.95 | 5460.28 | 7681.44 | 5507.83 | 7937.74 | 6849.62 | 3990.25 | 8156.23 | 7101.25 | 8589.32 | 8007.73 | 9000.74 | 11984.27
| Total Source Energy (MJ/m2) | 3777.99 | 3976.62 | 3490.21 | 3523.36 | 2612.17 | 3674.77 | 2634.92 | 3797.38 | 3276.83 | 1908.92 | 3901.91 | 3397.21 | 4109.1 | 3830.87 | 4305.92 | 5733.23
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 181231.1801 | 208878.6158 | 190566.9049 | 180665.8252 | 58595.5923 | 196474.2228 | 61457.4932 | 160473.8553 | 217524.5918 | 52175.7012 | 294072.2216 | 218243.9106 | 210669.1784 | 208697.8112 | 215152.2816 | 235631.6148
| CO2 (kg) | 419858.1814 | 526352.886 | 450684.2167 | 417684.5389 | 157236.442 | 469540.7991 | 166298.1086 | 374070.8108 | 515584.3432 | 134041.5259 | 696226.6888 | 521377.3215 | 508972.5713 | 503843.4 | 525272.2157 | 621706.0341
| NOX (kg) | 739.5693 | 684.9897 | 751.0976 | 770.073 | 135.1052 | 752.9961 | 143.8349 | 678.6545 | 866.4126 | 175.6748 | 1187.4192 | 858.5641 | 823.0611 | 812.354 | 825.7393 | 697.3075
| SO2 (kg) | 2822.9528 | 2903.665 | 2475.8994 | 1918.221 | 1368.6823 | 3073.3031 | 1278.7574 | 1873.9929 | 2158.612 | 345.3598 | 3332.6733 | 2087.696 | 1178.029 | 1286.1957 | 1138.649 | 2783.183
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0129 | 0.0082 | 0.0067 | 0.0071 | 0.0006 | 0.0058 | 0.0006 | 0.0077 | 0.0085 | 0.0015 | 0.0102 | 0.0083 | 0.0088 | 0.0091 | 0.0086 | 0.0099
| Water for Electricity (m3) | 349.3783 | 990.4533 | 18288.8 | 3411.81 | 8258.09 | 15326.8 | 7714.91 | 116.5332 | 2244.38 | 4561.26 | 767.1149 | 2170.53 | 773.982 | 30501.3 | 747.9959 | 558.3607

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2394.29 | 1145.42 | 1145.42
Net Site Energy | 2394.29 | 1145.42 | 1145.42
Total Source Energy | 7897.21 | 3777.99 | 3777.99
Net Source Energy | 7897.21 | 3777.99 | 3777.99
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 20.07 | 0 | 0 | 0 | 0
Cooling | 774.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 304.83 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2374.22 | 20.07 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30924.24 | 20907.36 | 10016.88 | 0.68 | 3.44
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 74738.55 | 51335.13 | 23403.42 | 0.69 | 3.13
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34569.4 | 23507.77 | 11061.63 | 0.68 | 3.45
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28373.02 | 19182.52 | 9190.5 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27751.75 | 18762.49 | 8989.26 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27655.84 | 18697.65 | 8958.19 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 49539.04 | 33492.51 | 16046.53 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25824.7 | 17459.65 | 8365.05 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25717.35 | 17387.07 | 8330.28 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25869.81 | 17490.14 | 8379.66 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13619.43 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23006.7 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20501.92 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 10250.96 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.25 | 1418.66 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.14 | 3436.28 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.41 | 1611.34 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.14 | 1301.62 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1273.12 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1268.72 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.99 | 2181.72 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1184.72 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1179.79 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1186.79 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 30935.1181 | 54.2031 | 205.7255 | 0 | 0.0009 | 25461.077 | 13324.2072
February | 28489.6482 | 50.0729 | 190.68 | 0 | 0.0009 | 23599.1258 | 12286.4063
March | 32704.0005 | 57.4681 | 218.7932 | 0 | 0.001 | 27078.4899 | 14102.6944
April | 33541.213 | 59.1317 | 225.9089 | 0 | 0.001 | 27959.292 | 14483.0018
May | 37328.4011 | 65.8326 | 251.607 | 0 | 0.0011 | 31139.8008 | 16120.723
June | 38419.9236 | 67.7576 | 258.9642 | 0 | 0.0012 | 32050.362 | 16592.1103
July | 40200.6043 | 70.898 | 270.9667 | 0 | 0.0012 | 33535.8273 | 17361.1189
August | 40917.3016 | 72.162 | 275.7975 | 0 | 0.0013 | 34133.7048 | 17670.6333
September | 37891.1168 | 66.825 | 255.3999 | 0 | 0.0012 | 31609.225 | 16363.7387
October | 36339.1112 | 64.0878 | 244.9381 | 0 | 0.0011 | 30314.4319 | 15693.4768
November | 32446.7044 | 57.2099 | 218.5977 | 0 | 0.001 | 27054.4456 | 14011.1684
December | 30645.0386 | 53.9207 | 205.5744 | 0 | 0.0009 | 25442.5473 | 13221.9011
Annual Sum or Average | 419858.1814 | 739.5693 | 2822.9528 | 0 | 0.0129 | 349378.3293 | 181231.1801
Minimum of Months | 28489.6482 | 50.0729 | 190.68 | 0 | 0.0009 | 23599.1258 | 12286.4063
Maximum of Months | 40917.3016 | 72.162 | 275.7975 | 0 | 0.0013 | 34133.7048 | 17670.6333
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 173022000000 | 156785.753 | 24-JAN-13:00 | 72368.391 | 8089.532 | 16042.754 | 0 | 60285.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 160369000000 | 164164.67 | 25-FEB-13:39 | 72368.391 | 8089.532 | 16042.754 | 0 | 67663.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 184013000000 | 165159.562 | 13-MAR-14:00 | 72368.391 | 8089.532 | 16042.754 | 0 | 68658.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 189999000000 | 173187.351 | 01-APR-14:39 | 72368.391 | 8089.532 | 16042.754 | 0 | 76686.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 211612000000 | 182899.042 | 24-MAY-14:00 | 72368.391 | 8089.532 | 16042.754 | 0 | 86398.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 217800000000 | 189403.563 | 27-JUN-14:00 | 72368.391 | 8089.532 | 16042.754 | 0 | 92902.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 227895000000 | 184241.853 | 13-JUL-14:00 | 72368.391 | 8089.532 | 16042.754 | 0 | 87741.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 231957000000 | 191091.773 | 21-AUG-14:30 | 72368.391 | 8089.532 | 16042.754 | 0 | 94591.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 214802000000 | 183672.478 | 07-SEP-13:00 | 72368.391 | 8089.532 | 16042.754 | 0 | 87171.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 206003000000 | 180782.261 | 06-OCT-14:20 | 72368.391 | 8089.532 | 16042.754 | 0 | 84281.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 183850000000 | 167832.953 | 07-NOV-15:09 | 72368.391 | 8089.532 | 16042.754 | 0 | 71332.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 172896000000 | 158366.213 | 16-DEC-12:00 | 72368.391 | 8089.532 | 16042.754 | 0 | 61865.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2374220000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 160369000000 | 156785.753 |  | 72368.391 | 8089.532 | 16042.754 | 0 | 60285.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 231957000000 | 191091.773 |  | 72368.391 | 8089.532 | 16042.754 | 0 | 94591.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 57547.42 | 228.9 | 0 | 57776.31
Cost per Total Building Area ($/m2) | 27.53 | 0.11 | 0 | 27.64
Cost per Net Conditioned Building Area ($/m2) | 27.53 | 0.11 | 0 | 27.64

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2514.93 | 1203.13 | 1203.13
Net Site Energy | 2514.93 | 1203.13 | 1203.13
Total Source Energy | 8312.41 | 3976.62 | 3976.62
Net Source Energy | 8312.41 | 3976.62 | 3976.62
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 323.55 | 0 | 0 | 0 | 0
Cooling | 573.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 323.21 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2191.38 | 323.55 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32260.15 | 21810.55 | 10449.6 | 0.68 | 3.44
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 76697.29 | 52914.77 | 23782.52 | 0.69 | 3.14
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35651.4 | 24372.55 | 11278.85 | 0.68 | 3.46
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29948.09 | 20247.4 | 9700.69 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29322.48 | 19824.44 | 9498.04 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29226.04 | 19759.23 | 9466.8 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52578.75 | 35547.61 | 17031.14 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27379.14 | 18510.58 | 8868.56 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27270.94 | 18437.43 | 8833.52 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27434.77 | 18548.19 | 8886.58 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28630.94 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 49414.55 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21060.28 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20974.92 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20970.67 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20981.99 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 41706.49 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20982.46 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20978.53 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21109.76 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.3 | 1479.95 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.26 | 3568.43 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.48 | 1685.92 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.21 | 1373.88 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.18 | 1345.18 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.18 | 1340.75 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.12 | 2315.59 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.1 | 1256.03 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.1 | 1251.06 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.1 | 1258.58 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39431.6586 | 49.8753 | 197.3505 | 0 | 0.0006 | 67310.7419 | 15462.4158
February | 35273.3966 | 44.5992 | 176.3084 | 0 | 0.0005 | 60133.7699 | 13829.706
March | 38475.0953 | 49.9099 | 209.9932 | 0 | 0.0006 | 71628.9087 | 15247.7335
April | 39849.717 | 52.24 | 225.1559 | 0 | 0.0006 | 76803.3964 | 15862.9978
May | 46652.3853 | 61.2893 | 265.4341 | 0 | 0.0007 | 90543.3533 | 18587.8948
June | 51080.6548 | 67.1408 | 291.1047 | 0 | 0.0008 | 99300.0861 | 20356.643
July | 54167.7373 | 71.1985 | 308.6979 | 0 | 0.0009 | 105301.3824 | 21586.9073
August | 54199.8173 | 71.2404 | 308.8768 | 0 | 0.0009 | 105362.4066 | 21599.6557
September | 47767.4359 | 62.7848 | 272.207 | 0 | 0.0008 | 92853.8046 | 19036.1139
October | 43693.6433 | 57.3098 | 247.3051 | 0 | 0.0007 | 84358.8722 | 17397.1135
November | 37427.945 | 48.7859 | 207.5615 | 0 | 0.0006 | 70800.5067 | 14862.9661
December | 38333.3996 | 48.6158 | 193.6701 | 0 | 0.0006 | 66056.0738 | 15048.4684
Annual Sum or Average | 526352.886 | 684.9897 | 2903.665 | 0 | 0.0082 | 990453.3025 | 208878.6158
Minimum of Months | 35273.3966 | 44.5992 | 176.3084 | 0 | 0.0005 | 60133.7699 | 13829.706
Maximum of Months | 54199.8173 | 71.2404 | 308.8768 | 0 | 0.0009 | 105362.4066 | 21599.6557
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 148925000000 | 147544.954 | 03-JAN-13:00 | 72368.391 | 8089.532 | 16875.368 | 0 | 50211.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 133046000000 | 150708.346 | 23-FEB-15:09 | 72368.391 | 8089.532 | 16875.368 | 0 | 53375.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 158479000000 | 154746.35 | 25-MAR-12:39 | 72368.391 | 8089.532 | 16875.368 | 0 | 57413.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 169928000000 | 175304.828 | 29-APR-14:09 | 72368.391 | 8089.532 | 16875.368 | 0 | 77971.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 200327000000 | 186185.514 | 26-MAY-14:00 | 72368.391 | 8089.532 | 16875.368 | 0 | 88852.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 219702000000 | 187701.667 | 13-JUN-14:00 | 72368.391 | 8089.532 | 16875.368 | 0 | 90368.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 232980000000 | 194695.835 | 18-JUL-12:00 | 72368.391 | 8089.532 | 16875.368 | 0 | 97362.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 233115000000 | 194444.333 | 31-AUG-14:09 | 72368.391 | 8089.532 | 16875.368 | 0 | 97111.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 205439000000 | 192179.138 | 16-SEP-13:50 | 72368.391 | 8089.532 | 16875.368 | 0 | 94845.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 186644000000 | 171462.864 | 12-OCT-14:00 | 72368.391 | 8089.532 | 16875.368 | 0 | 74129.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 156646000000 | 154386.131 | 03-NOV-14:30 | 72368.391 | 8089.532 | 16875.368 | 0 | 57052.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 146149000000 | 149427.126 | 19-DEC-15:09 | 72368.391 | 8089.532 | 16875.368 | 0 | 52093.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2191380000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 133046000000 | 147544.954 |  | 72368.391 | 8089.532 | 16875.368 | 0 | 50211.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 233115000000 | 194695.835 |  | 72368.391 | 8089.532 | 16875.368 | 0 | 97362.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 74451.63 | 2602.43 | 0 | 77054.06
Cost per Total Building Area ($/m2) | 35.62 | 1.24 | 0 | 36.86
Cost per Net Conditioned Building Area ($/m2) | 35.62 | 1.24 | 0 | 36.86

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2477.36 | 1185.16 | 1185.16
Net Site Energy | 2477.36 | 1185.16 | 1185.16
Total Source Energy | 7295.64 | 3490.21 | 3490.21
Net Source Energy | 7295.64 | 3490.21 | 3490.21
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 260.86 | 0 | 0 | 0 | 0
Cooling | 580.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 341.7 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2216.5 | 260.86 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32399.39 | 22662.88 | 9736.51 | 0.7 | 3.5
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 72285.19 | 52121.14 | 20164.05 | 0.72 | 3.2
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33461.03 | 23833.66 | 9627.37 | 0.71 | 3.53
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29179.06 | 20312.05 | 8867.01 | 0.7 | 3.49
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28768.68 | 19977.1 | 8791.58 | 0.69 | 3.49
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28701.47 | 19922.3 | 8779.17 | 0.69 | 3.49
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 53573.68 | 36734.37 | 16839.3 | 0.69 | 3.21
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27509.81 | 18952.9 | 8556.92 | 0.69 | 3.47
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27444.2 | 18899.66 | 8544.55 | 0.69 | 3.47
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27587.77 | 19016.14 | 8571.64 | 0.69 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21723.33 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37499.68 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16048.95 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15978.3 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15974.89 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15986.17 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31708.93 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15986.55 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15981.22 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16086.69 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.43 | 1628.26 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.44 | 3767.53 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.55 | 1761.76 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1448.02 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.25 | 1418.43 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1413.6 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.24 | 2451.79 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.17 | 1328.28 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.16 | 1323.61 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.17 | 1333.83 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 31546.8351 | 50.7622 | 160.1928 | 0 | 0.0004 | 1183210 | 13155.9151
February | 28924.4876 | 46.558 | 146.9885 | 0 | 0.0004 | 1085680 | 12063.8856
March | 33976.0697 | 56.4716 | 185.5532 | 0 | 0.0005 | 1370630 | 14351.0446
April | 34822.9698 | 58.4496 | 194.3043 | 0 | 0.0005 | 1435300 | 14766.4381
May | 38909.0406 | 65.6949 | 219.9025 | 0 | 0.0006 | 1624410 | 16538.2328
June | 44474.2903 | 75.1671 | 251.9034 | 0 | 0.0007 | 1860800 | 18911.3899
July | 47594.6138 | 80.4426 | 269.5902 | 0 | 0.0007 | 1991450 | 20238.401
August | 47402.9993 | 80.1188 | 268.5048 | 0 | 0.0007 | 1983430 | 20156.9218
September | 42477.1344 | 71.7923 | 240.596 | 0 | 0.0007 | 1777270 | 18062.2222
October | 36677.1878 | 61.7341 | 205.8967 | 0 | 0.0006 | 1520940 | 15570.128
November | 31452.5938 | 52.247 | 171.5525 | 0 | 0.0005 | 1267210 | 13282.0966
December | 32425.9945 | 51.6595 | 160.9143 | 0 | 0.0004 | 1188510 | 13470.2292
Annual Sum or Average | 450684.2167 | 751.0976 | 2475.8994 | 0 | 0.0067 | 18288800 | 190566.9049
Minimum of Months | 28924.4876 | 46.558 | 146.9885 | 0 | 0.0004 | 1085680 | 12063.8856
Maximum of Months | 47594.6138 | 80.4426 | 269.5902 | 0 | 0.0007 | 1991450 | 20238.401
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 143398000000 | 132700.847 | 28-JAN-14:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 34367.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 131579000000 | 139430.341 | 28-FEB-15:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 41097.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 166112000000 | 159952.556 | 17-MAR-14:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 61619.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 173950000000 | 164163.025 | 01-APR-15:39 | 72368.391 | 8089.532 | 17875.099 | 0 | 65830.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 196868000000 | 185755.836 | 27-MAY-14:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 87422.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 225518000000 | 209780.38 | 28-JUN-15:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 111447.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 241352000000 | 207512.931 | 11-JUL-15:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 109179.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 240380000000 | 207116.094 | 01-AUG-15:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 108783.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 215395000000 | 197562.679 | 09-SEP-14:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 99229.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 184329000000 | 167024.2 | 14-OCT-13:00 | 72368.391 | 8089.532 | 17875.099 | 0 | 68691.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 153578000000 | 152231.62 | 13-NOV-15:09 | 72368.391 | 8089.532 | 17875.099 | 0 | 53898.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 144041000000 | 131423.932 | 09-DEC-15:20 | 72368.391 | 8089.532 | 17875.099 | 0 | 33090.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2216500000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 131579000000 | 131423.932 |  | 72368.391 | 8089.532 | 17875.099 | 0 | 33090.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 241352000000 | 209780.38 |  | 72368.391 | 8089.532 | 17875.099 | 0 | 111447.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 60967.8 | 2125.72 | 0 | 63093.52
Cost per Total Building Area ($/m2) | 29.17 | 1.02 | 0 | 30.18
Cost per Net Conditioned Building Area ($/m2) | 29.17 | 1.02 | 0 | 30.18

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2651.49 | 1268.46 | 1268.46
Net Site Energy | 2651.49 | 1268.46 | 1268.46
Total Source Energy | 7364.95 | 3523.36 | 3523.36
Net Source Energy | 7364.95 | 3523.36 | 3523.36
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 684.28 | 0 | 0 | 0 | 0
Cooling | 342.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 329.63 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1967.22 | 684.28 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31397.46 | 21562.27 | 9835.18 | 0.69 | 3.47
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 71397.15 | 50706.62 | 20690.53 | 0.71 | 3.18
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33460.08 | 23585.38 | 9874.7 | 0.7 | 3.51
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29148.58 | 20010.19 | 9138.39 | 0.69 | 3.47
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28741.13 | 19675.76 | 9065.37 | 0.68 | 3.46
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28677.13 | 19623.3 | 9053.83 | 0.68 | 3.46
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 53209.48 | 35974.04 | 17235.44 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27466.74 | 18634.27 | 8832.48 | 0.68 | 3.45
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27395.9 | 18576.58 | 8819.32 | 0.68 | 3.45
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27503.56 | 18664.21 | 8839.35 | 0.68 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34627.21 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 59870.76 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25588.28 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25488.91 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25484.27 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25498.74 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 50674.65 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25499.22 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25492.87 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25643.48 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1503.07 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.28 | 3582.13 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.51 | 1715.36 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.22 | 1393.98 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.2 | 1364.25 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.19 | 1359.59 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.14 | 2343.36 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1272.11 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1267.03 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1274.75 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 36768.7096 | 61.1597 | 136.3613 | 0 | 0.0005 | 242471.8271 | 15291.7114
February | 32263.6952 | 54.6862 | 124.654 | 0 | 0.0005 | 221666.8324 | 13512.3247
March | 32157.5516 | 58.343 | 143.0518 | 0 | 0.0005 | 254427.4918 | 13822.2038
April | 31101.2073 | 58.2958 | 147.5163 | 0 | 0.0005 | 262386.6228 | 13540.7946
May | 34242.476 | 65.9373 | 171.0113 | 0 | 0.0006 | 304193.7205 | 15070.3734
June | 37346.3589 | 72.1116 | 187.4804 | 0 | 0.0007 | 333490.7194 | 16454.652
July | 40076.6307 | 77.3829 | 201.1837 | 0 | 0.0007 | 357866.2194 | 17657.5463
August | 40535.1842 | 78.2723 | 203.5054 | 0 | 0.0007 | 361996.007 | 17859.954
September | 36031.0488 | 69.56 | 180.8193 | 0 | 0.0007 | 321641.7586 | 15874.0348
October | 31646.8801 | 59.8408 | 152.664 | 0 | 0.0006 | 271547.8943 | 13826.5903
November | 30570.3643 | 55.0433 | 133.9318 | 0 | 0.0005 | 238202.6793 | 13101.1875
December | 34944.4322 | 59.4402 | 136.0416 | 0 | 0.0005 | 241919.3886 | 14654.4523
Annual Sum or Average | 417684.5389 | 770.073 | 1918.221 | 0 | 0.0071 | 3411810 | 180665.8252
Minimum of Months | 30570.3643 | 54.6862 | 124.654 | 0 | 0.0005 | 221666.8324 | 13101.1875
Maximum of Months | 40535.1842 | 78.2723 | 203.5054 | 0 | 0.0007 | 361996.007 | 17859.954
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 139807000000 | 119071.601 | 23-JAN-15:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 21538.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 127811000000 | 125202.653 | 18-FEB-14:50 | 72368.391 | 8089.532 | 17075.636 | 0 | 27669.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 146700000000 | 134504.183 | 28-MAR-14:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 36970.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 151290000000 | 152381.442 | 15-APR-14:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 54847.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 175395000000 | 165137.143 | 15-MAY-14:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 67603.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 192288000000 | 177955.144 | 19-JUN-14:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 80421.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 206342000000 | 193681.781 | 03-JUL-14:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 96148.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 208723000000 | 185029.614 | 17-AUG-13:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 87496.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 185456000000 | 173973.076 | 11-SEP-13:50 | 72368.391 | 8089.532 | 17075.636 | 0 | 76439.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 156572000000 | 159355.685 | 12-OCT-15:00 | 72368.391 | 8089.532 | 17075.636 | 0 | 61822.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 137345000000 | 126463.541 | 22-NOV-15:09 | 72368.391 | 8089.532 | 17075.636 | 0 | 28929.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 139488000000 | 114831.983 | 01-DEC-15:09 | 72368.391 | 8089.532 | 17075.636 | 0 | 17298.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1967220000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 127811000000 | 114831.983 |  | 72368.391 | 8089.532 | 17075.636 | 0 | 17298.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 208723000000 | 193681.781 |  | 72368.391 | 8089.532 | 17075.636 | 0 | 96148.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 54481.28 | 6506.59 | 0 | 60987.87
Cost per Total Building Area ($/m2) | 26.06 | 3.11 | 0 | 29.18
Cost per Net Conditioned Building Area ($/m2) | 26.06 | 3.11 | 0 | 29.18

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1894.47 | 906.31 | 906.31
Net Site Energy | 1894.47 | 906.31 | 906.31
Total Source Energy | 5460.28 | 2612.17 | 2612.17
Net Source Energy | 5460.28 | 2612.17 | 2612.17
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 201.25 | 0 | 0 | 0 | 0
Cooling | 123.7 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 274.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1693.22 | 201.25 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21004.97 | 15382.82 | 5622.16 | 0.73 | 3.58
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52773.68 | 39897.89 | 12875.79 | 0.76 | 3.35
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24820.32 | 18718.45 | 6101.87 | 0.75 | 3.64
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20842.18 | 15349.35 | 5492.83 | 0.74 | 3.59
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20461.7 | 15029.91 | 5431.79 | 0.73 | 3.59
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 20397.72 | 14976.25 | 5421.47 | 0.73 | 3.59
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37256.31 | 26998.64 | 10257.66 | 0.72 | 3.53
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19278.79 | 14040.63 | 5238.16 | 0.73 | 3.57
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19212.46 | 13985.35 | 5227.11 | 0.73 | 3.57
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19266.51 | 14030.41 | 5236.1 | 0.73 | 3.57
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16976.7 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29143.11 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12375.27 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12317.05 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12313.96 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12321.78 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 24452.63 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12322.14 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12319.69 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 12409.3 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.04 | 1184.81 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.82 | 3082.21 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1501.37 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.05 | 1191.67 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.02 | 1162.58 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.02 | 1157.69 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.8 | 1966.08 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.94 | 1072.83 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.94 | 1067.84 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.94 | 1071.91 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13870.1128 | 11.9783 | 109.9202 | 0 | 0.0001 | 663176.2927 | 5135.8315
February | 12371.9551 | 10.6786 | 99.1018 | 0 | 0 | 597910.6958 | 4584.3103
March | 13559.8691 | 11.6826 | 112.4391 | 0 | 0.0001 | 678393.2602 | 5036.1408
April | 12549.3456 | 10.7987 | 106.4235 | 0 | 0 | 642107.503 | 4668.0436
May | 12645.5678 | 10.8537 | 112.225 | 0 | 0.0001 | 677129.1747 | 4719.0464
June | 12320.1189 | 10.5601 | 111.8831 | 0 | 0.0001 | 675075.0721 | 4605.3648
July | 13267.8651 | 11.3558 | 123.475 | 0 | 0.0001 | 745027.7865 | 4968.7477
August | 14461.5187 | 12.3772 | 134.6218 | 0 | 0.0001 | 812285.7724 | 5415.8816
September | 13232.2842 | 11.3262 | 122.992 | 0 | 0.0001 | 742113.0307 | 4954.9595
October | 12880.0744 | 11.0392 | 117.1284 | 0 | 0.0001 | 706724.2973 | 4815.1695
November | 12524.606 | 10.7681 | 107.8825 | 0 | 0.0001 | 650916.3898 | 4663.9325
December | 13553.1243 | 11.6868 | 110.5898 | 0 | 0.0001 | 667228.683 | 5028.1641
Annual Sum or Average | 157236.442 | 135.1052 | 1368.6823 | 0 | 0.0006 | 8258090 | 58595.5923
Minimum of Months | 12320.1189 | 10.5601 | 99.1018 | 0 | 0 | 597910.6958 | 4584.3103
Maximum of Months | 14461.5187 | 12.3772 | 134.6218 | 0 | 0.0001 | 812285.7724 | 5415.8816
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 135976000000 | 128176.933 | 26-JAN-13:50 | 72368.391 | 8089.532 | 14458.993 | 0 | 33260.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 122594000000 | 124146.111 | 13-FEB-11:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 29229.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 139096000000 | 123790.287 | 31-MAR-14:09 | 72368.391 | 8089.532 | 14458.993 | 0 | 28873.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 131656000000 | 132327.684 | 11-APR-15:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 37410.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 138837000000 | 129446.79 | 30-MAY-12:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 34529.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 138416000000 | 131244.826 | 28-JUN-12:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 36327.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 152759000000 | 139594.807 | 24-JUL-14:09 | 72368.391 | 8089.532 | 14458.993 | 0 | 44677.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 166549000000 | 148507.583 | 08-AUG-12:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 53590.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 152161000000 | 145661.996 | 25-SEP-14:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 50745.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 144905000000 | 136990.295 | 05-OCT-14:09 | 72368.391 | 8089.532 | 14458.993 | 0 | 42073.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 133462000000 | 131061.924 | 20-NOV-12:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 36145.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 136807000000 | 130849.549 | 19-DEC-12:00 | 72368.391 | 8089.532 | 14458.993 | 0 | 35932.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1693220000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 122594000000 | 123790.287 |  | 72368.391 | 8089.532 | 14458.993 | 0 | 28873.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 166549000000 | 148507.583 |  | 72368.391 | 8089.532 | 14458.993 | 0 | 53590.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 61992.99 | 1732.19 | 0 | 63725.18
Cost per Total Building Area ($/m2) | 29.66 | 0.83 | 0 | 30.49
Cost per Net Conditioned Building Area ($/m2) | 29.66 | 0.83 | 0 | 30.49

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2457.41 | 1175.62 | 1175.62
Net Site Energy | 2457.41 | 1175.62 | 1175.62
Total Source Energy | 7681.44 | 3674.77 | 3674.77
Net Source Energy | 7681.44 | 3674.77 | 3674.77
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 446.17 | 0 | 0 | 0 | 0
Cooling | 384.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 332.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2011.25 | 446.17 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26805.57 | 19770.26 | 7035.31 | 0.74 | 3.6
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 62590.92 | 47527.28 | 15063.64 | 0.76 | 3.36
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28732.94 | 21581.33 | 7151.61 | 0.75 | 3.63
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24584.23 | 18059.78 | 6524.45 | 0.73 | 3.59
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24181.16 | 17719.81 | 6461.35 | 0.73 | 3.58
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24110.2 | 17660.01 | 6450.19 | 0.73 | 3.58
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 44582.1 | 32264.05 | 12318.06 | 0.72 | 3.28
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22951.73 | 16685.72 | 6266.02 | 0.73 | 3.57
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 22889.33 | 16633.35 | 6255.98 | 0.73 | 3.57
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23003.45 | 16729.11 | 6274.34 | 0.73 | 3.57
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27137.97 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46929 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20130.71 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20045.92 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20042.04 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20056.31 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39787.69 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20056.71 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20049.25 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20174.91 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.35 | 1538.09 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.38 | 3692.85 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.51 | 1721.6 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1397.13 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.2 | 1366.01 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.19 | 1360.54 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.14 | 2344.87 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1271.63 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.11 | 1266.86 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1275.58 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37930.0279 | 57.1415 | 213.6156 | 0 | 0.0004 | 1065180 | 15488.2537
February | 30996.6199 | 48.5901 | 192.3681 | 0 | 0.0004 | 959313.9239 | 12853.9194
March | 35269.1402 | 55.3316 | 219.296 | 0 | 0.0004 | 1093600 | 14630.2391
April | 34755.1145 | 56.482 | 234.493 | 0 | 0.0004 | 1169460 | 14620.4051
May | 38909.4611 | 63.6252 | 266.2049 | 0 | 0.0005 | 1327630 | 16408.7308
June | 45461.881 | 74.5483 | 312.9943 | 0 | 0.0006 | 1560990 | 19193.6641
July | 48569.283 | 79.6501 | 334.4473 | 0 | 0.0006 | 1667980 | 20506.2414
August | 49329.9487 | 80.8975 | 339.6851 | 0 | 0.0006 | 1694100 | 20827.3972
September | 42730.9859 | 70.0701 | 294.1923 | 0 | 0.0006 | 1467220 | 18040.6956
October | 36562.566 | 59.509 | 247.5303 | 0 | 0.0005 | 1234490 | 15390.0594
November | 32233.1423 | 51.1006 | 205.4193 | 0 | 0.0004 | 1024420 | 13426.151
December | 36792.6285 | 56.0501 | 213.0569 | 0 | 0.0004 | 1062420 | 15088.4661
Annual Sum or Average | 469540.7991 | 752.9961 | 3073.3031 | 0 | 0.0058 | 15326800 | 196474.2228
Minimum of Months | 30996.6199 | 48.5901 | 192.3681 | 0 | 0.0004 | 959313.9239 | 12853.9194
Maximum of Months | 49329.9487 | 80.8975 | 339.6851 | 0 | 0.0006 | 1694100 | 20827.3972
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 139778000000 | 106962.815 | 18-JAN-16:49 | 72368.391 | 8089.532 | 17235.162 | 0 | 3396.73 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 125885000000 | 113306.982 | 07-FEB-17:10 | 72368.391 | 8089.532 | 17235.162 | 0 | 9740.896 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 143507000000 | 127291.201 | 31-MAR-14:39 | 72368.391 | 8089.532 | 17235.162 | 0 | 29598.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 153462000000 | 154355.221 | 21-APR-14:00 | 72368.391 | 8089.532 | 17235.162 | 0 | 56662.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 174217000000 | 165670.838 | 31-MAY-15:00 | 72368.391 | 8089.532 | 17235.162 | 0 | 67977.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 204839000000 | 190756.484 | 27-JUN-15:00 | 72368.391 | 8089.532 | 17235.162 | 0 | 93063.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 218879000000 | 188746.943 | 24-JUL-15:00 | 72368.391 | 8089.532 | 17235.162 | 0 | 91053.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 222307000000 | 187374.473 | 05-AUG-12:00 | 72368.391 | 8089.532 | 17235.162 | 0 | 89681.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 192534000000 | 181662.181 | 01-SEP-14:00 | 72368.391 | 8089.532 | 17235.162 | 0 | 83969.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 161994000000 | 155996.072 | 03-OCT-14:50 | 72368.391 | 8089.532 | 17235.162 | 0 | 58302.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 134429000000 | 118414.747 | 10-NOV-16:40 | 72368.391 | 8089.532 | 17235.162 | 0 | 14848.662 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 139415000000 | 116192.471 | 05-DEC-14:00 | 72368.391 | 8089.532 | 17235.162 | 0 | 18499.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2011250000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 125885000000 | 106962.815 |  | 72368.391 | 8089.532 | 17235.162 | 0 | 3396.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 222307000000 | 190756.484 |  | 72368.391 | 8089.532 | 17235.162 | 0 | 93063.399 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 55600.82 | 3405.92 | 0 | 59006.74
Cost per Total Building Area ($/m2) | 26.6 | 1.63 | 0 | 28.23
Cost per Net Conditioned Building Area ($/m2) | 26.6 | 1.63 | 0 | 28.23

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2142.3 | 1024.87 | 1024.87
Net Site Energy | 2142.3 | 1024.87 | 1024.87
Total Source Energy | 5507.83 | 2634.92 | 2634.92
Net Source Energy | 5507.83 | 2634.92 | 2634.92
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 560.45 | 0 | 0 | 0 | 0
Cooling | 40.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 246.76 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1581.85 | 560.45 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15200.26 | 11950.57 | 3249.69 | 0.79 | 3.97
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 41903.53 | 33466.48 | 8437.06 | 0.8 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19664.75 | 15705.36 | 3959.39 | 0.8 | 3.77
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15694.15 | 12415.21 | 3278.94 | 0.79 | 3.99
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15327.86 | 12103.23 | 3224.63 | 0.79 | 3.98
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 15257.51 | 12043.36 | 3214.16 | 0.79 | 3.98
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27242.3 | 21311.49 | 5930.81 | 0.78 | 3.72
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14208.25 | 11152.46 | 3055.79 | 0.78 | 3.99
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14149.67 | 11102.85 | 3046.83 | 0.78 | 3.99
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14181.34 | 11129.69 | 3051.65 | 0.78 | 3.99
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21563.54 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37208.42 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15891.6 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15823.55 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15820.13 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15830.05 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31426.61 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15830.43 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15826.46 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 15929.53 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1010.65 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.53 | 2768.4 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.19 | 1353.3 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.93 | 1057.78 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1028.93 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1023.4 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.57 | 1791.35 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.83 | 958.4 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.82 | 953.76 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.82 | 956.27 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16962.9338 | 14.8057 | 106.4415 | 0 | 0.0001 | 642078.7409 | 6195.6487
February | 13211.9402 | 11.4559 | 96.4806 | 0 | 0 | 582059.9556 | 4867.0333
March | 15058.8528 | 13.0664 | 108.346 | 0 | 0.0001 | 653635.8939 | 5542.4537
April | 13584.5456 | 11.7561 | 103.295 | 0 | 0.0001 | 623187.5911 | 5016.7829
May | 13266.715 | 11.4419 | 107.8818 | 0 | 0.0001 | 650889.0232 | 4920.7755
June | 12620.6654 | 10.8661 | 105.9645 | 0 | 0.0001 | 639334.0495 | 4691.327
July | 12663.2187 | 10.8883 | 108.893 | 0 | 0.0001 | 657012.8474 | 4714.9896
August | 13262.6582 | 11.4085 | 113.1898 | 0 | 0.0001 | 682934.5 | 4935.5659
September | 12828.608 | 11.0301 | 110.3909 | 0 | 0.0001 | 666050.4038 | 4776.801
October | 13226.6456 | 11.3971 | 109.3864 | 0 | 0.0001 | 659973.7255 | 4911.4978
November | 13298.4362 | 11.5011 | 102.4329 | 0 | 0.0001 | 617991.9376 | 4915.1298
December | 16312.8891 | 14.2177 | 106.055 | 0 | 0.0001 | 639765.6847 | 5969.488
Annual Sum or Average | 166298.1086 | 143.8349 | 1278.7574 | 0 | 0.0006 | 7714910 | 61457.4932
Minimum of Months | 12620.6654 | 10.8661 | 96.4806 | 0 | 0 | 582059.9556 | 4691.327
Maximum of Months | 16962.9338 | 14.8057 | 113.1898 | 0 | 0.0001 | 682934.5 | 6195.6487
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 131650000000 | 99233.151 | 02-JAN-16:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119344000000 | 111687.696 | 15-FEB-15:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 18327.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 134020000000 | 99233.151 | 01-MAR-17:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 127777000000 | 117286.912 | 29-APR-13:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 23926.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 133457000000 | 119027.628 | 17-MAY-13:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 25667.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 131087000000 | 120712.465 | 15-JUN-12:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 27352.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 134712000000 | 129989.847 | 03-JUL-12:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 36629.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 140027000000 | 126752.109 | 15-AUG-11:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 33391.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 136565000000 | 141645.065 | 28-SEP-14:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 48284.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 135319000000 | 119100.343 | 31-OCT-12:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 25740.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 126712000000 | 99292.637 | 13-NOV-16:00 | 72368.391 | 8089.532 | 12902.228 | 0 | 59.485 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 131176000000 | 99233.151 | 01-DEC-16:49 | 72368.391 | 8089.532 | 12902.228 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1581850000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119344000000 | 99233.151 |  | 72368.391 | 8089.532 | 12902.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 140027000000 | 141645.065 |  | 72368.391 | 8089.532 | 12902.228 | 0 | 48284.913 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 65571.7 | 4802.79 | 0 | 70374.49
Cost per Total Building Area ($/m2) | 31.37 | 2.3 | 0 | 33.67
Cost per Net Conditioned Building Area ($/m2) | 31.37 | 2.3 | 0 | 33.67

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3065.76 | 1466.65 | 1466.65
Net Site Energy | 3065.76 | 1466.65 | 1466.65
Total Source Energy | 7937.74 | 3797.38 | 3797.38
Net Source Energy | 7937.74 | 3797.38 | 3797.38
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1217.97 | 0 | 0 | 0 | 0
Cooling | 246.71 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 306.51 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1847.8 | 1217.97 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31532.27 | 21318.44 | 10213.83 | 0.68 | 3.44
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 68654.14 | 47691.63 | 20962.51 | 0.69 | 3.22
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32504.19 | 22498.51 | 10005.67 | 0.69 | 3.48
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27851.15 | 18829.69 | 9021.45 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27212.9 | 18398.19 | 8814.71 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27107.03 | 18326.61 | 8780.42 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 48453.55 | 32758.63 | 15694.92 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25256.05 | 17075.19 | 8180.86 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25148.05 | 17002.17 | 8145.87 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25271.29 | 17085.5 | 8185.8 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39247.52 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 68331.29 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29425.96 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29331.43 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29327.08 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29341.96 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 58360.38 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29342.41 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29335.1 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 29474.92 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1446.55 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.97 | 3252.79 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.39 | 1589.03 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1277.68 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.1 | 1248.4 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1243.54 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.95 | 2133.91 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.02 | 1158.63 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.01 | 1153.68 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.02 | 1159.33 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39682.2896 | 61.3792 | 140.1915 | 0 | 0.0006 | 8713.9803 | 16052.9195
February | 33519.6034 | 53.2758 | 126.3093 | 0 | 0.0005 | 7851.8099 | 13690.5426
March | 31289.5052 | 54.2631 | 142.9279 | 0 | 0.0006 | 8887.0091 | 13194.062
April | 25845.6951 | 47.8895 | 134.9969 | 0 | 0.0006 | 8395.0604 | 11178.991
May | 26566.1573 | 51.9579 | 153.853 | 0 | 0.0006 | 9568.5869 | 11740.55
June | 30517.8945 | 60.9184 | 183.5397 | 0 | 0.0007 | 11415.2689 | 13599.5897
July | 33020.453 | 66.0028 | 199.0818 | 0 | 0.0008 | 12381.9384 | 14722.9328
August | 33918.8912 | 67.7659 | 204.3172 | 0 | 0.0008 | 12707.5493 | 15120.5205
September | 27597.5838 | 54.826 | 164.5245 | 0 | 0.0007 | 10232.543 | 12274.1776
October | 27137.8964 | 51.5911 | 148.9646 | 0 | 0.0006 | 9264.1083 | 11857.4381
November | 28377.4424 | 50.3788 | 136.0635 | 0 | 0.0006 | 8460.642 | 12072.7195
December | 36597.3989 | 58.406 | 139.2231 | 0 | 0.0006 | 8654.6892 | 14969.4119
Annual Sum or Average | 374070.8108 | 678.6545 | 1873.9929 | 0 | 0.0077 | 116533.1857 | 160473.8553
Minimum of Months | 25845.6951 | 47.8895 | 126.3093 | 0 | 0.0005 | 7851.8099 | 11178.991
Maximum of Months | 39682.2896 | 67.7659 | 204.3172 | 0 | 0.0008 | 12707.5493 | 16052.9195
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 138172000000 | 101994.475 | 02-JAN-16:49 | 72368.391 | 8089.532 | 15663.552 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 124501000000 | 101994.475 | 01-FEB-17:30 | 72368.391 | 8089.532 | 15663.552 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 140916000000 | 128560.603 | 09-MAR-15:00 | 72368.391 | 8089.532 | 15663.552 | 0 | 32439.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 133115000000 | 129742.341 | 04-APR-15:00 | 72368.391 | 8089.532 | 15663.552 | 0 | 33620.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 151723000000 | 150161.749 | 31-MAY-15:00 | 72368.391 | 8089.532 | 15663.552 | 0 | 54040.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 181005000000 | 181268.413 | 30-JUN-14:50 | 72368.391 | 8089.532 | 15663.552 | 0 | 85146.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 196333000000 | 188382.974 | 25-JUL-12:00 | 72368.391 | 8089.532 | 15663.552 | 0 | 92261.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 201496000000 | 189839.454 | 17-AUG-14:00 | 72368.391 | 8089.532 | 15663.552 | 0 | 93717.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 162251000000 | 166493.117 | 09-SEP-14:09 | 72368.391 | 8089.532 | 15663.552 | 0 | 70371.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 146895000000 | 144919.588 | 20-OCT-14:39 | 72368.391 | 8089.532 | 15663.552 | 0 | 48798.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 134155000000 | 133935.59 | 04-NOV-12:00 | 72368.391 | 8089.532 | 15663.552 | 0 | 37814.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 137232000000 | 101994.475 | 01-DEC-16:40 | 72368.391 | 8089.532 | 15663.552 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1847800000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 124501000000 | 101994.475 |  | 72368.391 | 8089.532 | 15663.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 201496000000 | 189839.454 |  | 72368.391 | 8089.532 | 15663.552 | 0 | 93717.979 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 39950.35 | 11762.54 | 0 | 51712.89
Cost per Total Building Area ($/m2) | 19.11 | 5.63 | 0 | 24.74
Cost per Net Conditioned Building Area ($/m2) | 19.11 | 5.63 | 0 | 24.74

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2645.36 | 1265.53 | 1265.53
Net Site Energy | 2645.36 | 1265.53 | 1265.53
Total Source Energy | 6849.62 | 3276.83 | 3276.83
Net Source Energy | 6849.62 | 3276.83 | 3276.83
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 865.99 | 0 | 0 | 0 | 0
Cooling | 177.61 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 307.16 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1779.37 | 865.99 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21418.13 | 16970.28 | 4447.85 | 0.79 | 3.75
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 51018.07 | 40745.85 | 10272.22 | 0.8 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23830.25 | 19032.16 | 4798.1 | 0.8 | 3.77
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18566.81 | 14827 | 3739.81 | 0.8 | 4.01
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18172.65 | 14469.97 | 3702.69 | 0.8 | 4
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18095.9 | 14400.52 | 3695.38 | 0.8 | 4
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32777.38 | 25725.5 | 7051.88 | 0.78 | 3.69
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16969.53 | 13384.3 | 3585.22 | 0.79 | 3.98
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16907.92 | 13328.89 | 3579.03 | 0.79 | 3.98
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16954.46 | 13370.75 | 3583.71 | 0.79 | 3.98
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31961.62 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55445.38 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23831.87 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23740.14 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23736 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23751.49 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 47163.3 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23751.92 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23743.62 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 23877.94 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1448.62 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.08 | 3370.56 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.44 | 1639.97 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.12 | 1277.47 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1242.44 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.08 | 1235.63 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.91 | 2084.19 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1136.28 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1130.88 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1134.96 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 46380.815 | 72.9185 | 167.0023 | 0 | 0.0007 | 173603.2313 | 19075.4214
February | 39881.4866 | 64.0635 | 150.9777 | 0 | 0.0006 | 156956.2034 | 16536.0869
March | 42997.3549 | 70.4727 | 170.3726 | 0 | 0.0007 | 177129.8732 | 17965.7414
April | 38528.9025 | 65.4345 | 165.0374 | 0 | 0.0006 | 171599.7465 | 16322.8598
May | 41859.7826 | 72.7676 | 188.3778 | 0 | 0.0007 | 195879.5641 | 17898.4166
June | 43684.9037 | 76.5501 | 199.8916 | 0 | 0.0008 | 207855.8074 | 18738.6141
July | 46480.1434 | 81.5475 | 213.2188 | 0 | 0.0008 | 221714.6922 | 19947.361
August | 46609.2485 | 81.751 | 213.6868 | 0 | 0.0008 | 222201.1487 | 20000.5151
September | 41755.6684 | 73.0737 | 190.5458 | 0 | 0.0007 | 198137.106 | 17901.6818
October | 39783.4963 | 67.8868 | 172.1523 | 0 | 0.0007 | 178999.738 | 16885.9211
November | 40854.0642 | 66.7096 | 160.5258 | 0 | 0.0006 | 166890.7236 | 17045.6605
December | 46768.4771 | 73.237 | 166.823 | 0 | 0.0007 | 173414.4843 | 19206.3121
Annual Sum or Average | 515584.3432 | 866.4126 | 2158.612 | 0 | 0.0085 | 2244380 | 217524.5918
Minimum of Months | 38528.9025 | 64.0635 | 150.9777 | 0 | 0.0006 | 156956.2034 | 16322.8598
Maximum of Months | 46768.4771 | 81.751 | 213.6868 | 0 | 0.0008 | 222201.1487 | 20000.5151
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 137635000000 | 102031.907 | 02-JAN-17:10 | 72368.391 | 8089.532 | 15700.984 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 124437000000 | 112209.594 | 14-FEB-15:00 | 72368.391 | 8089.532 | 15700.984 | 0 | 16050.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 140431000000 | 113460.787 | 02-MAR-15:09 | 72368.391 | 8089.532 | 15700.984 | 0 | 17301.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 136046000000 | 131879.899 | 22-APR-13:00 | 72368.391 | 8089.532 | 15700.984 | 0 | 35720.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 155296000000 | 136837.873 | 31-MAY-14:00 | 72368.391 | 8089.532 | 15700.984 | 0 | 40678.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 164791000000 | 150052.267 | 29-JUN-14:09 | 72368.391 | 8089.532 | 15700.984 | 0 | 53893.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 175778000000 | 154147.83 | 31-JUL-14:00 | 72368.391 | 8089.532 | 15700.984 | 0 | 57988.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 176164000000 | 153431.092 | 01-AUG-14:09 | 72368.391 | 8089.532 | 15700.984 | 0 | 57272.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 157085000000 | 140712.013 | 02-SEP-14:00 | 72368.391 | 8089.532 | 15700.984 | 0 | 44553.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 141913000000 | 128001.184 | 13-OCT-14:00 | 72368.391 | 8089.532 | 15700.984 | 0 | 31842.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 132313000000 | 108455.618 | 08-NOV-17:10 | 72368.391 | 8089.532 | 15700.984 | 0 | 6423.71 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 137485000000 | 102031.907 | 01-DEC-16:00 | 72368.391 | 8089.532 | 15700.984 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1779370000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 124437000000 | 102031.907 |  | 72368.391 | 8089.532 | 15700.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 176164000000 | 154147.83 |  | 72368.391 | 8089.532 | 15700.984 | 0 | 57988.923 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18444.89 | 5950.79 | 0 | 24395.68
Cost per Total Building Area ($/m2) | 8.82 | 2.85 | 0 | 11.67
Cost per Net Conditioned Building Area ($/m2) | 8.82 | 2.85 | 0 | 11.67

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2697.4 | 1290.43 | 1290.43
Net Site Energy | 2697.4 | 1290.43 | 1290.43
Total Source Energy | 3990.25 | 1908.92 | 1908.92
Net Source Energy | 3990.25 | 1908.92 | 1908.92
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1090.19 | 0 | 0 | 0 | 0
Cooling | 45.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 267.31 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1607.21 | 1090.19 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 5.835 | 0.54 | 0.384 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17646.73 | 13650.01 | 3996.73 | 0.77 | 3.93
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 44540.78 | 35369.85 | 9170.93 | 0.79 | 3.44
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21388.25 | 16917.28 | 4470.97 | 0.79 | 3.75
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17579.22 | 13653.39 | 3925.83 | 0.78 | 3.94
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17207.67 | 13336.93 | 3870.74 | 0.78 | 3.93
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 17140.09 | 13279.42 | 3860.68 | 0.77 | 3.93
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30950.36 | 23734.54 | 7215.82 | 0.77 | 3.68
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16076.48 | 12376.12 | 3700.36 | 0.77 | 3.92
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16015.66 | 12324.59 | 3691.07 | 0.77 | 3.92
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16065.87 | 12367.14 | 3698.73 | 0.77 | 3.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30227 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 52569.82 | 0.8
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22621.1 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22543.41 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22539.67 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22551.66 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44834.45 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22552.06 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22546.54 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 22661.46 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.99 | 1131.38 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.66 | 2906.17 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1441.11 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1 | 1137.46 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1108.2 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.97 | 1102.89 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.71 | 1945.75 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.9 | 1019.61 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1014.87 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.89 | 1018.79 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16889.2505 | 19.842 | 28.8749 | 0 | 0.0001 | 380971.6794 | 6328.5619
February | 12801.6785 | 15.6776 | 25.9588 | 0 | 0.0001 | 342659.1736 | 4865.2194
March | 13737.4642 | 17.0451 | 29.2706 | 0 | 0.0001 | 386422.3315 | 5244.5829
April | 10747.8334 | 14.0485 | 27.4518 | 0 | 0.0001 | 362557.1844 | 4179.5695
May | 8801.5185 | 12.5031 | 28.8565 | 0 | 0.0001 | 381278.1981 | 3529.6459
June | 7724.6148 | 11.4938 | 28.6491 | 0 | 0.0001 | 378607.8702 | 3153.526
July | 7497.3339 | 11.5637 | 30.4121 | 0 | 0.0001 | 401953.4816 | 3104.4517
August | 7647.321 | 11.8867 | 31.6053 | 0 | 0.0001 | 417733.5977 | 3176.3669
September | 8111.8947 | 11.9429 | 29.2738 | 0 | 0.0001 | 386848.252 | 3298.0154
October | 9738.9153 | 13.2891 | 28.4465 | 0 | 0.0001 | 375788.3936 | 3847.1366
November | 13483.7096 | 16.5759 | 27.7441 | 0 | 0.0001 | 366238.4948 | 5131.1701
December | 16859.9916 | 19.8063 | 28.8163 | 0 | 0.0001 | 380198.5386 | 6317.455
Annual Sum or Average | 134041.5259 | 175.6748 | 345.3598 | 0 | 0.0015 | 4561260 | 52175.7012
Minimum of Months | 7497.3339 | 11.4938 | 25.9588 | 0 | 0.0001 | 342659.1736 | 3104.4517
Maximum of Months | 16889.2505 | 19.842 | 31.6053 | 0 | 0.0001 | 417733.5977 | 6328.5619
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 134239000000 | 100157.169 | 02-JAN-16:30 | 72368.391 | 8089.532 | 13826.246 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 120740000000 | 100157.169 | 01-FEB-17:10 | 72368.391 | 8089.532 | 13826.246 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 136160000000 | 104068.62 | 29-MAR-15:50 | 72368.391 | 8089.532 | 13826.246 | 0 | 9784.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 127751000000 | 111886.593 | 29-APR-14:00 | 72368.391 | 8089.532 | 13826.246 | 0 | 17602.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 134347000000 | 119776.276 | 04-MAY-14:50 | 72368.391 | 8089.532 | 13826.246 | 0 | 25492.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 133407000000 | 124823.66 | 28-JUN-14:39 | 72368.391 | 8089.532 | 13826.246 | 0 | 30539.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 141633000000 | 135691.086 | 24-JUL-14:00 | 72368.391 | 8089.532 | 13826.246 | 0 | 41406.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 147193000000 | 131570.517 | 07-AUG-14:00 | 72368.391 | 8089.532 | 13826.246 | 0 | 37286.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 136310000000 | 148420.882 | 02-SEP-15:09 | 72368.391 | 8089.532 | 13826.246 | 0 | 54136.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 132413000000 | 109698.041 | 17-OCT-14:00 | 72368.391 | 8089.532 | 13826.246 | 0 | 15413.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 129048000000 | 100190.219 | 04-NOV-16:49 | 72368.391 | 8089.532 | 13826.246 | 0 | 33.05 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 133967000000 | 100157.169 | 01-DEC-16:19 | 72368.391 | 8089.532 | 13826.246 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1607210000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 120740000000 | 100157.169 |  | 72368.391 | 8089.532 | 13826.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 147193000000 | 148420.882 |  | 72368.391 | 8089.532 | 13826.246 | 0 | 54136.713 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33850.78 | 9175.76 | 0 | 43026.54
Cost per Total Building Area ($/m2) | 16.19 | 4.39 | 0 | 20.58
Cost per Net Conditioned Building Area ($/m2) | 16.19 | 4.39 | 0 | 20.58

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3468.89 | 1659.5 | 1659.5
Net Site Energy | 3468.89 | 1659.5 | 1659.5
Total Source Energy | 8156.23 | 3901.91 | 3901.91
Net Source Energy | 8156.23 | 3901.91 | 3901.91
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1688.86 | 0 | 0 | 0 | 0
Cooling | 168.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 317.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1780.03 | 1688.86 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40949.69 | 27685.4 | 13264.29 | 0.68 | 3.21
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 64096.65 | 44210.04 | 19886.61 | 0.69 | 3.21
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29950.76 | 20516.66 | 9434.1 | 0.69 | 3.46
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27001.08 | 18254.98 | 8746.1 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26995.68 | 18251.32 | 8744.35 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27013.76 | 18263.55 | 8750.21 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 53648.28 | 36270.7 | 17377.58 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27014.32 | 18263.93 | 8750.39 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27005.65 | 18258.07 | 8747.58 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 27181.68 | 18377.07 | 8804.6 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 50130.51 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 87360.91 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37593.9 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37486.61 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37481.71 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37498.09 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 74653.36 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37498.6 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37490.75 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37650.18 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.65 | 1878.58 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.73 | 2980.14 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.25 | 1424.06 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1238.68 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1238.44 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1239.27 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.16 | 2362.69 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1239.29 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1238.89 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1246.97 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 68530.2014 | 105.7477 | 261.3103 | 0 | 0.0008 | 60131.9052 | 27881.5396
February | 58547.7685 | 92.2974 | 234.9572 | 0 | 0.0007 | 54071.2525 | 24006.9564
March | 60636.2165 | 98.9272 | 263.3452 | 0 | 0.0008 | 60610.1432 | 25182.3956
April | 50290.0256 | 86.747 | 246.5832 | 0 | 0.0008 | 56759.9935 | 21334.91
May | 51729.0151 | 92.7785 | 274.9168 | 0 | 0.0008 | 63287.1286 | 22284.7466
June | 57475.3346 | 104.5043 | 313.9652 | 0 | 0.0009 | 72278.1402 | 24895.9629
July | 63235.0577 | 115.1157 | 346.2605 | 0 | 0.001 | 79713.0454 | 27404.1122
August | 61988.642 | 112.8114 | 339.224 | 0 | 0.001 | 78093.1267 | 26860.5829
September | 52023.7108 | 94.2493 | 282.1313 | 0 | 0.0009 | 64949.1924 | 22501.7861
October | 50971.7844 | 89.6869 | 260.5007 | 0 | 0.0008 | 59966.156 | 21792.7939
November | 55109.0339 | 91.6241 | 249.6179 | 0 | 0.0008 | 57453.5469 | 23050.857
December | 65689.8984 | 102.9297 | 259.861 | 0 | 0.0008 | 59801.2994 | 26875.5784
Annual Sum or Average | 696226.6888 | 1187.4192 | 3332.6733 | 0 | 0.0102 | 767114.9299 | 294072.2216
Minimum of Months | 50290.0256 | 86.747 | 234.9572 | 0 | 0.0007 | 54071.2525 | 21334.91
Maximum of Months | 68530.2014 | 115.1157 | 346.2605 | 0 | 0.001 | 79713.0454 | 27881.5396
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 139532000000 | 102417.935 | 02-JAN-16:30 | 72368.391 | 8089.532 | 16087.012 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 125468000000 | 102417.935 | 01-FEB-16:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 140641000000 | 110470.957 | 31-MAR-14:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 13926.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 131707000000 | 113841.114 | 07-APR-14:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 17296.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 146853000000 | 145719.351 | 30-MAY-15:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 49174.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 167716000000 | 174576.778 | 08-JUN-12:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 78031.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 184968000000 | 177108.827 | 13-JUL-14:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 80563.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 181209000000 | 174837.381 | 04-AUG-14:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 78292.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 150710000000 | 150993.432 | 05-SEP-14:09 | 72368.391 | 8089.532 | 16087.012 | 0 | 54448.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 139147000000 | 126321.678 | 31-OCT-13:30 | 72368.391 | 8089.532 | 16087.012 | 0 | 29776.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 133317000000 | 125530.857 | 02-NOV-14:00 | 72368.391 | 8089.532 | 16087.012 | 0 | 28985.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 138764000000 | 102417.935 | 01-DEC-16:19 | 72368.391 | 8089.532 | 16087.012 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1780030000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 125468000000 | 102417.935 |  | 72368.391 | 8089.532 | 16087.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 184968000000 | 177108.827 |  | 72368.391 | 8089.532 | 16087.012 | 0 | 80563.892 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 44739.49 | 14021.57 | 0 | 58761.06
Cost per Total Building Area ($/m2) | 21.4 | 6.71 | 0 | 28.11
Cost per Net Conditioned Building Area ($/m2) | 21.4 | 6.71 | 0 | 28.11

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2995.15 | 1432.87 | 1432.87
Net Site Energy | 2995.15 | 1432.87 | 1432.87
Total Source Energy | 7101.25 | 3397.21 | 3397.21
Net Source Energy | 7101.25 | 3397.21 | 3397.21
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1274.33 | 0 | 0 | 0 | 0
Cooling | 108.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 318.16 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1720.82 | 1274.33 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29094.36 | 22584.15 | 6510.2 | 0.78 | 3.71
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 45477.15 | 36320.57 | 9156.58 | 0.8 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21098.22 | 16850.21 | 4248.02 | 0.8 | 3.77
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18644 | 14647.16 | 3996.85 | 0.79 | 3.97
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18790.22 | 14708.65 | 4081.57 | 0.78 | 3.96
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 18838.14 | 14734.76 | 4103.38 | 0.78 | 3.96
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38608.11 | 29756.48 | 8851.63 | 0.77 | 3.65
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19250.42 | 14912.61 | 4337.82 | 0.77 | 3.7
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19268.42 | 14917.56 | 4350.86 | 0.77 | 3.7
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19400.14 | 15024.13 | 4376.01 | 0.77 | 3.7
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 41587.27 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 72266.72 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31033.38 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30928.47 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30923.75 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30940.66 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 61526.14 | 0.8
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30941.14 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30932.43 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 31086.96 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.65 | 1880.15 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.75 | 3004.49 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.27 | 1451.95 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1237.58 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1237.29 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1238.31 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.16 | 2356.95 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1238.34 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1237.81 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.09 | 1247.14 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50028.6706 | 76.5383 | 168.6878 | 0 | 0.0007 | 175338.3049 | 20368.2131
February | 43421.3913 | 67.4414 | 151.8843 | 0 | 0.0006 | 157880.9819 | 17777.4087
March | 45860.6072 | 73.2727 | 171.4728 | 0 | 0.0007 | 178259.8256 | 18976.4339
April | 39539.6348 | 65.7664 | 161.8727 | 0 | 0.0006 | 168299.9114 | 16615.2458
May | 39865.3729 | 68.0223 | 172.4835 | 0 | 0.0007 | 179344.0982 | 16920.2549
June | 40160.9324 | 69.8567 | 180.9618 | 0 | 0.0007 | 188168.5572 | 17176.176
July | 43685.4194 | 76.616 | 200.2456 | 0 | 0.0008 | 208224.3726 | 18745.2089
August | 44298.9393 | 77.5959 | 202.5378 | 0 | 0.0008 | 210607.2426 | 18999.0415
September | 39812.0759 | 68.8202 | 177.064 | 0 | 0.0007 | 184112.7255 | 16984.8237
October | 40764.8068 | 68.4519 | 170.3937 | 0 | 0.0007 | 177163.8152 | 17193.6086
November | 43460.9581 | 69.2912 | 161.7022 | 0 | 0.0006 | 168101.3567 | 17969.0274
December | 50478.5129 | 76.8912 | 168.3898 | 0 | 0.0007 | 175025.6351 | 20518.4681
Annual Sum or Average | 521377.3215 | 858.5641 | 2087.696 | 0 | 0.0083 | 2170530 | 218243.9106
Minimum of Months | 39539.6348 | 65.7664 | 151.8843 | 0 | 0.0006 | 157880.9819 | 16615.2458
Maximum of Months | 50478.5129 | 77.5959 | 202.5378 | 0 | 0.0008 | 210607.2426 | 20518.4681
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 139010000000 | 102460.945 | 02-JAN-16:49 | 72368.391 | 8089.532 | 16130.022 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 125170000000 | 102460.945 | 01-FEB-17:19 | 72368.391 | 8089.532 | 16130.022 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 141327000000 | 113405.381 | 30-MAR-15:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 16817.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 133430000000 | 120757.795 | 25-APR-14:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 24169.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 142186000000 | 128831.346 | 23-MAY-15:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 32243.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 149182000000 | 141062.135 | 28-JUN-13:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 44474.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 165083000000 | 147957.317 | 17-JUL-14:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 51369.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 166972000000 | 150418.753 | 30-AUG-13:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 53830.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 145967000000 | 139959.193 | 02-SEP-14:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 43371.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 140458000000 | 128695.787 | 05-OCT-14:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 32107.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 133273000000 | 107748.772 | 10-NOV-13:00 | 72368.391 | 8089.532 | 16130.022 | 0 | 11160.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 138762000000 | 102460.945 | 01-DEC-16:40 | 72368.391 | 8089.532 | 16130.022 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1720820000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 125170000000 | 102460.945 |  | 72368.391 | 8089.532 | 16130.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 166972000000 | 150418.753 |  | 72368.391 | 8089.532 | 16130.022 | 0 | 53830.807 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17844.27 | 8802.09 | 0 | 26646.35
Cost per Total Building Area ($/m2) | 8.54 | 4.21 | 0 | 12.75
Cost per Net Conditioned Building Area ($/m2) | 8.54 | 4.21 | 0 | 12.75

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4008.95 | 1917.87 | 1917.87
Net Site Energy | 4008.95 | 1917.87 | 1917.87
Total Source Energy | 8589.32 | 4109.1 | 4109.1
Net Source Energy | 8589.32 | 4109.1 | 4109.1
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2212.99 | 0 | 0 | 0 | 0
Cooling | 142.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 358.56 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1795.97 | 2212.99 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 46442.79 | 31399.19 | 15043.6 | 0.68 | 3.19
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 71323.65 | 49574.4 | 21749.26 | 0.7 | 3.15
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29209.25 | 20144.21 | 9065.04 | 0.69 | 3.47
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30700.81 | 20756.3 | 9944.51 | 0.68 | 3.44
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30695.12 | 20752.45 | 9942.66 | 0.68 | 3.44
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30714.26 | 20765.4 | 9948.86 | 0.68 | 3.44
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 61033.2 | 41263.52 | 19769.68 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30714.84 | 20765.79 | 9949.05 | 0.68 | 3.44
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30705.6 | 20759.54 | 9946.06 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30891.51 | 20885.23 | 10006.28 | 0.68 | 3.44
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 56363.83 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 98299.44 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42315.49 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42202.65 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42197.53 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42214.74 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 84075.06 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42215.26 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42206.96 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42374.05 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.87 | 2045.36 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.09 | 3384.37 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1414.17 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1408.41 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1408.15 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1409.03 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.46 | 2687.92 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1409.05 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1408.63 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.24 | 1417.16 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 60900.6837 | 84.3324 | 94.8804 | 0 | 0.0008 | 62270.3286 | 23854.8613
February | 50056.4089 | 71.4742 | 85.0139 | 0 | 0.0007 | 55810.2359 | 19813.4716
March | 45317.4663 | 70.0675 | 94.4181 | 0 | 0.0007 | 62018.7523 | 18450.0234
April | 34963.4954 | 58.9219 | 88.681 | 0 | 0.0007 | 58276.0623 | 14699.481
May | 34674.4179 | 61.9764 | 99.4802 | 0 | 0.0007 | 65388.0508 | 14916.4861
June | 36847.2672 | 67.045 | 109.5722 | 0 | 0.0008 | 72026.0481 | 15964.4759
July | 39155.7159 | 71.3912 | 116.9119 | 0 | 0.0009 | 76851.2836 | 16978.5842
August | 39927.1257 | 72.8187 | 119.2836 | 0 | 0.0009 | 78410.3656 | 17315.088
September | 32430.1726 | 58.3201 | 94.1975 | 0 | 0.0007 | 61917.1417 | 13984.9771
October | 35918.2143 | 60.8416 | 92.1145 | 0 | 0.0007 | 60533.7039 | 15130.5739
November | 42830.8918 | 66.2879 | 89.4492 | 0 | 0.0007 | 58755.2552 | 17443.8866
December | 55950.7116 | 79.584 | 94.0264 | 0 | 0.0007 | 61724.7908 | 22117.2693
Annual Sum or Average | 508972.5713 | 823.0611 | 1178.029 | 0 | 0.0088 | 773982.0188 | 210669.1784
Minimum of Months | 32430.1726 | 58.3201 | 85.0139 | 0 | 0.0007 | 55810.2359 | 13984.9771
Maximum of Months | 60900.6837 | 84.3324 | 119.2836 | 0 | 0.0009 | 78410.3656 | 23854.8613
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 144494000000 | 104323.167 | 02-JAN-16:40 | 72368.391 | 8089.532 | 17992.244 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 129503000000 | 104323.167 | 01-FEB-17:19 | 72368.391 | 8089.532 | 17992.244 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 143910000000 | 104323.167 | 01-MAR-17:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 135225000000 | 118640.057 | 01-APR-16:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 20189.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 151728000000 | 174345.331 | 27-MAY-14:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 75895.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 167131000000 | 172563.154 | 29-JUN-14:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 74112.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 178328000000 | 180229.139 | 15-JUL-14:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 81778.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 181945000000 | 171222.787 | 25-AUG-15:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 72772.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 143674000000 | 148836.696 | 14-SEP-14:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 50386.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 140464000000 | 132487.988 | 07-OCT-14:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 34037.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 136337000000 | 104852.471 | 02-NOV-16:00 | 72368.391 | 8089.532 | 17992.244 | 0 | 529.304 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 143228000000 | 104323.167 | 01-DEC-16:30 | 72368.391 | 8089.532 | 17992.244 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1795970000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 129503000000 | 104323.167 |  | 72368.391 | 8089.532 | 17992.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 181945000000 | 180229.139 |  | 72368.391 | 8089.532 | 17992.244 | 0 | 81778.973 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 30969.64 | 17422.3 | 0 | 48391.94
Cost per Total Building Area ($/m2) | 14.82 | 8.33 | 0 | 23.15
Cost per Net Conditioned Building Area ($/m2) | 14.82 | 8.33 | 0 | 23.15

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3548.68 | 1697.67 | 1697.67
Net Site Energy | 3548.68 | 1697.67 | 1697.67
Total Source Energy | 8007.73 | 3830.87 | 3830.87
Net Source Energy | 8007.73 | 3830.87 | 3830.87
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1815.22 | 0 | 0 | 0 | 0
Cooling | 61.12 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 377.84 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1733.46 | 1815.22 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32900.07 | 26275.82 | 6624.26 | 0.8 | 3.73
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 54422.04 | 43464.45 | 10957.59 | 0.8 | 3.45
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21854.14 | 17453.92 | 4400.22 | 0.8 | 3.77
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21759.13 | 17378.05 | 4381.09 | 0.8 | 3.77
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21754.9 | 17374.67 | 4380.23 | 0.8 | 3.77
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21770 | 17386.73 | 4383.28 | 0.8 | 3.77
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 43711.83 | 34733.54 | 8978.29 | 0.79 | 3.44
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21831.38 | 17413.34 | 4418.04 | 0.8 | 3.77
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21846.05 | 17416.82 | 4429.22 | 0.8 | 3.77
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 21972.47 | 17522.86 | 4449.61 | 0.8 | 3.77
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 53068.3 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 92415.67 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39747.86 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39633.39 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39628.29 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39646.48 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 78920.35 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39647 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39637.7 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 39806.64 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.99 | 2173.58 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.29 | 3595.44 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1503.97 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.31 | 1497.44 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.31 | 1497.14 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1498.18 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.61 | 2856.03 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1498.21 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.31 | 1497.68 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1507.33 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 55294.285 | 79.9417 | 107.8454 | 0 | 0.0008 | 2555890 | 22013.2591
February | 46787.9957 | 69.2137 | 96.9324 | 0 | 0.0007 | 2297610 | 18778.5667
March | 44651.8431 | 70.3477 | 108.0361 | 0 | 0.0008 | 2561720 | 18336.2866
April | 38488.3445 | 62.8167 | 101.0053 | 0 | 0.0007 | 2395410 | 16015.9181
May | 36495.2955 | 62.1194 | 105.0171 | 0 | 0.0007 | 2490980 | 15433.5928
June | 36290.7379 | 63.4497 | 110.4989 | 0 | 0.0008 | 2621270 | 15509.3393
July | 38085.1452 | 67.4035 | 118.9152 | 0 | 0.0008 | 2821040 | 16355.1224
August | 38039.8339 | 67.1023 | 117.9745 | 0 | 0.0008 | 2798690 | 16314.302
September | 35388.4481 | 61.2662 | 105.5599 | 0 | 0.0007 | 2504020 | 15065.1532
October | 38391.3799 | 63.7388 | 104.6579 | 0 | 0.0007 | 2482210 | 16079.9977
November | 43057.0602 | 67.3702 | 102.4962 | 0 | 0.0007 | 2430280 | 17636.4503
December | 52873.031 | 77.5842 | 107.2568 | 0 | 0.0008 | 2542200 | 21159.8229
Annual Sum or Average | 503843.4 | 812.354 | 1286.1957 | 0 | 0.0091 | 30501300 | 208697.8112
Minimum of Months | 35388.4481 | 61.2662 | 96.9324 | 0 | 0.0007 | 2297610 | 15065.1532
Maximum of Months | 55294.285 | 79.9417 | 118.9152 | 0 | 0.0008 | 2821040 | 22013.2591
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 145257000000 | 105455.939 | 02-JAN-16:49 | 72368.391 | 8089.532 | 19125.016 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 130579000000 | 105455.939 | 01-FEB-17:30 | 72368.391 | 8089.532 | 19125.016 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 145589000000 | 103822.969 | 30-MAR-16:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 4240.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 136137000000 | 100489.234 | 06-APR-16:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 906.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 141568000000 | 122381.529 | 16-MAY-16:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 22798.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 148973000000 | 148325.92 | 30-JUN-14:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 48742.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 160326000000 | 148407.724 | 21-JUL-16:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 48824.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 159056000000 | 143047.649 | 09-AUG-16:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 43464.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 142309000000 | 135186.204 | 01-SEP-16:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 35603.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 141070000000 | 117799.871 | 06-OCT-15:00 | 72368.391 | 8089.532 | 19125.016 | 0 | 18216.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 138118000000 | 105455.939 | 06-NOV-17:10 | 72368.391 | 8089.532 | 19125.016 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 144479000000 | 105455.939 | 01-DEC-16:40 | 72368.391 | 8089.532 | 19125.016 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1733460000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 130579000000 | 100489.234 |  | 72368.391 | 8089.532 | 19125.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 160326000000 | 148407.724 |  | 72368.391 | 8089.532 | 19125.016 | 0 | 48824.785 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 36526.16 | 14673.63 | 0 | 51199.79
Cost per Total Building Area ($/m2) | 17.47 | 7.02 | 0 | 24.49
Cost per Net Conditioned Building Area ($/m2) | 17.47 | 7.02 | 0 | 24.49

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4515.2 | 2160.05 | 2160.05
Net Site Energy | 4515.2 | 2160.05 | 2160.05
Total Source Energy | 9000.74 | 4305.92 | 4305.92
Net Source Energy | 9000.74 | 4305.92 | 4305.92
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2779.53 | 0 | 0 | 0 | 0
Cooling | 49.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 92.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 391.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1735.67 | 2779.53 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 49323.91 | 33504.53 | 15819.37 | 0.68 | 3.19
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70065.53 | 50510.29 | 19555.25 | 0.72 | 3.28
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28693.6 | 20542.46 | 8151.14 | 0.72 | 3.54
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31410.23 | 21681.57 | 9728.66 | 0.69 | 3.48
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31773.47 | 21836.72 | 9936.75 | 0.69 | 3.47
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31873.64 | 21884.96 | 9988.67 | 0.69 | 3.47
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 66062.46 | 44663.72 | 21398.74 | 0.68 | 3.19
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33023.94 | 22380.89 | 10643.05 | 0.68 | 3.45
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33075.26 | 22400.38 | 10674.88 | 0.68 | 3.44
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 33220.19 | 22509.28 | 10710.91 | 0.68 | 3.45
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 59200.36 | 0.8
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 103378.79 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44571.61 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44457.59 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44452.54 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44470.74 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 88568.9 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44471.25 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44461.83 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 44628.55 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.01 | 2200.54 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.34 | 3649.98 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1530.32 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1524.37 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1524.11 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1525.06 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.66 | 2909.41 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1525.08 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.34 | 1524.59 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.35 | 1533.28 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 62572.6009 | 86.3992 | 96.6764 | 0 | 0.0008 | 63447.3388 | 24486.0133
February | 53833.7429 | 75.5283 | 87.0675 | 0 | 0.0007 | 57149.706 | 21180.5876
March | 51979.958 | 76.8425 | 96.8173 | 0 | 0.0007 | 63575.9953 | 20825.4511
April | 39961.5365 | 63.8386 | 89.9413 | 0 | 0.0007 | 59089.0033 | 16465.6317
May | 35412.9421 | 60.6049 | 92.8348 | 0 | 0.0007 | 61009.7034 | 14976.9109
June | 32755.4471 | 58.8558 | 94.9818 | 0 | 0.0007 | 62432.4639 | 14120.5339
July | 35389.5105 | 64.23 | 104.7081 | 0 | 0.0008 | 68828.0712 | 15317.3518
August | 35586.4468 | 64.1228 | 103.7777 | 0 | 0.0008 | 68214.7834 | 15358.1739
September | 33187.415 | 58.0393 | 91.0484 | 0 | 0.0007 | 59840.9211 | 14154.5118
October | 38440.6457 | 63.4313 | 93.1032 | 0 | 0.0007 | 61176.1605 | 16032.2726
November | 46680.4442 | 70.4121 | 91.5179 | 0 | 0.0007 | 60104.4098 | 18836.4303
December | 59471.526 | 83.4346 | 96.1746 | 0 | 0.0008 | 63127.3691 | 23398.4127
Annual Sum or Average | 525272.2157 | 825.7393 | 1138.649 | 0 | 0.0086 | 747995.9259 | 215152.2816
Minimum of Months | 32755.4471 | 58.0393 | 87.0675 | 0 | 0.0007 | 57149.706 | 14120.5339
Maximum of Months | 62572.6009 | 86.3992 | 104.7081 | 0 | 0.0008 | 68828.0712 | 24486.0133
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 147225000000 | 105777.668 | 02-JAN-16:30 | 72368.391 | 8089.532 | 19446.745 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 132612000000 | 105777.668 | 01-FEB-17:10 | 72368.391 | 8089.532 | 19446.745 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 147523000000 | 105777.668 | 01-MAR-17:49 | 72368.391 | 8089.532 | 19446.745 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 137112000000 | 101589.962 | 04-APR-14:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 1685.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 141568000000 | 121542.688 | 31-MAY-15:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 21638.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 144870000000 | 147061.225 | 14-JUN-14:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 47156.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 159710000000 | 163030.185 | 08-JUL-15:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 63125.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 158287000000 | 162461.873 | 12-AUG-14:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 62557.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 138856000000 | 136571.803 | 07-SEP-14:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 36667.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 141955000000 | 128541.289 | 07-OCT-14:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 28636.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 139468000000 | 105777.668 | 13-NOV-17:00 | 72368.391 | 8089.532 | 19446.745 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 146482000000 | 105777.668 | 01-DEC-16:19 | 72368.391 | 8089.532 | 19446.745 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1735670000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 132612000000 | 101589.962 |  | 72368.391 | 8089.532 | 19446.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 159710000000 | 163030.185 |  | 72368.391 | 8089.532 | 19446.745 | 0 | 63125.518 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 29312.41 | 21852.63 | 0 | 51165.04
Cost per Total Building Area ($/m2) | 14.02 | 10.45 | 0 | 24.48
Cost per Net Conditioned Building Area ($/m2) | 14.02 | 10.45 | 0 | 24.48

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6506.42 | 3112.64 | 3112.64
Net Site Energy | 6506.42 | 3112.64 | 3112.64
Total Source Energy | 11984.27 | 5733.23 | 5733.23
Net Source Energy | 11984.27 | 5733.23 | 5733.23
Area [m2]
Total Building Area | 2090.32
Net Conditioned Building Area | 2090.32
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4538.97 | 0 | 0 | 0 | 0
Cooling | 18.45 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1053 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 91.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 149.32 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 655.11 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1967.44 | 4538.97 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
LGSTORE1 | 348.39 | Yes | 1805.2 | 1 | 276.3 | 20.75 | 60.26 | 6.19 | 4.3
LGSTORE2 | 348.39 | Yes | 1805.2 | 1 | 157.89 | 20.7 | 29.05 | 6.19 | 4.3
SMSTORE1 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.37 | 60.26 | 6.19 | 4.3
SMSTORE2 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE3 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE4 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 35.51 | 6.19 | 4.3
SMSTORE5 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE6 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE7 | 174.19 | Yes | 902.6 | 1 | 78.94 | 10.35 | 29.05 | 6.19 | 4.3
SMSTORE8 | 174.19 | Yes | 902.6 | 1 | 197.36 | 10.35 | 29.05 | 6.19 | 4.3
Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Conditioned Total | 2090.32 |  | 10831.2 |  | 1184.15 | 124.29 | 38.4675 | 6.19 | 4.3
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
LGSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 78.94 | 180 | 90 | S
LGSTORE1_WALL_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 118.41 | 270 | 90 | W
LGSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 78.94 | 0 | 90 | N
LGSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 270 | 0
LGSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 78.94 | 180 | 90 | S
LGSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 78.94 | 0 | 90 | N
LGSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 348.39 | 270 | 180
LGSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 270 | 0
SMSTORE1_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE1_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE1_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE1_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE2_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE2_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE2_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE2_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE3_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE3_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE3_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE3_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE4_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE4_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE4_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE4_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE5_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE5_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE5_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE5_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE6_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE6_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE6_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE6_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE7_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE7_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE7_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE7_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
SMSTORE8_WALL_1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 180 | 90 | S
SMSTORE8_WALL_3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 39.47 | 0 | 90 | N
SMSTORE8_WALL_4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 118.41 | 90 | 90 | E
SMSTORE8_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 174.19 | 270 | 180
SMSTORE8_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 174.19 | 270 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
LGSTORE1_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE1_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE1_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_1 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_DOOR_2 | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_3 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
LGSTORE2_WALL_1_WINDOW_4 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | LGSTORE2_WALL_1 | 180 | S
SMSTORE1_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.9 | 3.9 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE1_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE1_WALL_1 | 180 | S
SMSTORE2_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE2_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE2_WALL_1 | 180 | S
SMSTORE3_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE3_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE3_WALL_1 | 180 | S
SMSTORE4_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE4_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE4_WALL_1 | 180 | S
SMSTORE5_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE5_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE5_WALL_1 | 180 | S
SMSTORE6_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE6_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE6_WALL_1 | 180 | S
SMSTORE7_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE7_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE7_WALL_1 | 180 | S
SMSTORE8_WALL_1_DOOR | WINDOW-NONRES-FIXED | 3.88 | 3.88 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_1 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
SMSTORE8_WALL_1_WINDOW_2 | WINDOW-NONRES-FIXED | 3.24 | 3.24 | 3.525 | 0.407 | 0.316 | No | SMSTORE8_WALL_1 | 180 | S
Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 124.29 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 43988.13 | 35131.35 | 8856.78 | 0.8 | 3.45
PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 73394.4 | 58616.82 | 14777.58 | 0.8 | 4.18
PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29739.4 | 23751.52 | 5987.87 | 0.8 | 3.73
PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29644.94 | 23676.09 | 5968.85 | 0.8 | 3.73
PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29641.05 | 23672.98 | 5968.07 | 0.8 | 3.73
PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29657.65 | 23686.24 | 5971.41 | 0.8 | 3.73
PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 58983.27 | 47107.3 | 11875.97 | 0.8 | 4.32
PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29658.03 | 23686.54 | 5971.49 | 0.8 | 3.73
PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29648.21 | 23678.7 | 5969.51 | 0.8 | 3.73
PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29783.39 | 23786.66 | 5996.73 | 0.8 | 3.73
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 80185.4 | 0.78
PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 140410.7 | 0.78
PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60680.94 | 0.8
PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60551.8 | 0.8
PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60546.47 | 0.8
PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60569.18 | 0.8
PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 120686.12 | 0.78
PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60569.69 | 0.8
PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60556.27 | 0.8
PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 60741.1 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
PSZ-AC_10:10_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.66 | 2906.12 | 1 | Unitary Fans
PSZ-AC_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.43 | 8457.08 | 1 | Unitary Fans
PSZ-AC_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.8 | 1964.76 | 1 | Unitary Fans
PSZ-AC_3:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.79 | 1958.52 | 1 | Unitary Fans
PSZ-AC_4:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.79 | 1958.26 | 1 | Unitary Fans
PSZ-AC_5:5_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.79 | 1959.36 | 1 | Unitary Fans
PSZ-AC_6:6_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.56 | 6796.52 | 1 | Unitary Fans
PSZ-AC_7:7_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.79 | 1959.39 | 1 | Unitary Fans
PSZ-AC_8:8_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.79 | 1958.74 | 1 | Unitary Fans
PSZ-AC_9:9_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.8 | 1967.67 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 80279.0009 | 84.6868 | 247.3649 | 0 | 0.0009 | 49600.3597 | 29602.4276
February | 69532.8981 | 73.6943 | 221.4421 | 0 | 0.0008 | 44404.8645 | 25692.7446
March | 63402.562 | 69.1495 | 242.7653 | 0 | 0.0009 | 48693.9807 | 23728.0052
April | 46017.0855 | 52.4042 | 222.5592 | 0 | 0.0008 | 44653.5422 | 17562.6202
May | 35212.7701 | 42.7076 | 224.8537 | 0 | 0.0008 | 45125.5402 | 13840.3444
June | 32397.5286 | 40.1462 | 224.7222 | 0 | 0.0008 | 45102.0443 | 12865.0799
July | 32939.3854 | 40.9815 | 231.9095 | 0 | 0.0008 | 46545.051 | 13105.4719
August | 34167.3371 | 42.147 | 232.975 | 0 | 0.0008 | 46757.7876 | 13538.2782
September | 36564.4111 | 43.7551 | 221.1011 | 0 | 0.0008 | 44370.4447 | 14280.5176
October | 49913.7209 | 56.4455 | 233.1157 | 0 | 0.0008 | 46769.7753 | 18988.8143
November | 66027.3252 | 71.1236 | 234.2254 | 0 | 0.0009 | 46976.0099 | 24573.5656
December | 75252.0092 | 80.0661 | 246.149 | 0 | 0.0009 | 49361.3477 | 27853.7452
Annual Sum or Average | 621706.0341 | 697.3075 | 2783.183 | 0 | 0.0099 | 558360.7478 | 235631.6148
Minimum of Months | 32397.5286 | 40.1462 | 221.1011 | 0 | 0.0008 | 44370.4447 | 12865.0799
Maximum of Months | 80279.0009 | 84.6868 | 247.3649 | 0 | 0.0009 | 49600.3597 | 29602.4276
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 174772000000 | 118217.345 | 02-JAN-09:09 | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 156465000000 | 118217.345 | 01-FEB-09:09 | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 171579000000 | 118217.345 | 01-MAR-17:00 | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 157342000000 | 112344.345 | 01-APR-09:09 | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 159005000000 | 119335.027 | 24-MAY-14:00 | 72368.391 | 8089.532 | 31886.422 | 0 | 6990.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 158922000000 | 141588.966 | 20-JUN-16:00 | 72368.391 | 8089.532 | 31886.422 | 0 | 29244.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 164007000000 | 149040.694 | 29-JUL-16:00 | 72368.391 | 8089.532 | 31886.422 | 0 | 36696.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 164756000000 | 140639.417 | 15-AUG-16:00 | 72368.391 | 8089.532 | 31886.422 | 0 | 28295.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 156344000000 | 113702.88 | 02-SEP-15:00 | 72368.391 | 8089.532 | 31886.422 | 0 | 1358.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 164798000000 | 118217.345 | 23-OCT-08:09 | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 165525000000 | 118217.345 | 01-NOV-08:09 | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 173930000000 | 118217.345 | 01-DEC-09:09 | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1967440000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 156344000000 | 112344.345 |  | 72368.391 | 8089.532 | 31886.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 174772000000 | 149040.694 |  | 72368.391 | 8089.532 | 31886.422 | 0 | 36696.349 | 5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 52215.46 | 18712.51 | 0 | 70927.97
Cost per Total Building Area ($/m2) | 24.98 | 8.95 | 0 | 33.93
Cost per Net Conditioned Building Area ($/m2) | 24.98 | 8.95 | 0 | 33.93

## Picture
DOE Commercial Building Benchmark - Strip Mall

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0