## BuildingSummary
Building Summary Warehouse pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Warehouse
| Available Fuel Types | gas, electricity
| Principal Building Activity | Nonrefrigerated warehouse
Form
| Total Floor Area (m2) | 4835.13 | Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory
| Building Shape | Rectangle
| Aspect Ratio | 0.45
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.0286
| East | 0
| North | 0
| West | 0.0076
| Total | 0.0058
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Bulk storage, fine storage, office
| Floor to Ceiling Height (m) | 8.53
| Floor to Floor Height (m) | 8.53
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Metal building wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.35192
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4598.25
| Net Dimensions - Total Area (m2) | 4598.25
| Roof to Skin Ratio | 0.64808
Window Dimensions (m2)
| South | 11.15
| East | 0
| North | 0
| West | 6.51
| Total Area (m2) | 17.66
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 8in slab-on-grade
| Dimensions - Total Area (m2) | 4598.25
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 539.71
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9670.26
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.74 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC office, semi-conditioned storage | 2003 CBECS
| Heating Type | Gas furnace office, gas unit heaters storage | 2003 CBECS
| Cooling Type | PACU office | 2003 CBECS
| Fan Control | SZ CAV | 2003 CBECS
Service Water Heating
| SWH Type | n/a
| Fuel | n/a
| Thermal Efficiency (%) | n/a
| Temperature Setpoint (ºC ) | n/a
| Water Consumption (m3 ) | n/a

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.5601 | 17.66 | 47.376 | 5 | 21.6974 | 8.0729 |  |  | 10 |  | 50 |  | 0.60391
FineStorage | Yes | 1 | 1393.41 | 10880.57 | 7.8086 | 760.8007 | 0 |  | 0 | 11.6478 | 0 |  |  |  | 0.25 | 348.3525 |  | 0.80806
BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.6315 | 0 |  | 0 | 3.3409 | 2.691 |  |  |  | 0.25 | 801.21 |  | 0.71502
Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report
[5] Liu, B, R.E. Jarnagin, W. Jiang, and K. Gowri. (2007). Technical Support Document: The Development of the Advanced Energy Design Guide for Small Warehouse and Self-Storage Buildings. PNNL-17056. Richland, WA: Pacific Northwest National Laboratory

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
| R-value (m2·K / W) | 0.57405 | 0.57405 | 0.57405 | 0.59137 | 0.57405 | 0.57405 | 0.59453 | 0.79808 | 0.7657 | 0.815 | 0.93721 | 0.90253 | 1.0235 | 1.0235 | 1.1038 | 1.218
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
| R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
HVAC
HVAC Sizing
Air Conditioning (kW)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 28.1306 | 29.3838 | 29.5402 | 28.9683 | 16.453 | 24.4822 | 14.6138 | 30.828 | 24.9543 | 19.0077 | 39.2767 | 30.616 | 42.7934 | 35.369 | 44.2633 | 43.9752
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 83.2864 | 97.7712 | 127.6112 | 131.6273 | 44.1422 | 93.2999 | 52.0757 | 146.9484 | 124.1721 | 90.8406 | 203.6741 | 189.8856 | 234.747 | 196.528 | 255.4275 | 229.3456
Heating (kW)
| BULKSTORAGE UNIT HEATER COIL | 39.3476 | 39.2032 | 37.8007 | 69.5236 | 39.2079 | 36.3558 | 39.3336 | 115.5233 | 69.3196 | 43.155 | 232.871 | 172.1471 | 297.631 | 282.3407 | 331.1059 | 549.716
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 14.6703 | 27.2566 | 21.8197 | 32.6141 | 17.7068 | 26.6902 | 21.3682 | 34.6698 | 30.0129 | 27.5552 | 42.492 | 36.8984 | 47.1162 | 45.158 | 48.998 | 63.9235
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 35.8026 | 123.3941 | 85.023 | 160.1143 | 56.073 | 117.7855 | 82.4899 | 184.9919 | 151.222 | 132.9623 | 251.8387 | 210.7964 | 287.9859 | 274.6432 | 306.5407 | 426.8626
HVAC Efficiency
Air Conditioning (COP)
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.34 | 3.36 | 3.48 | 3.41 | 3.51 | 3.59 | 3.61 | 3.38 | 3.6 | 3.61 | 3.34 | 3.56 | 3.17 | 3.56 | 3.19 | 3.35
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 2.97 | 3.33 | 3.31 | 3.31 | 3.1 | 3.47 | 3.22 | 3.31 | 3.49 | 3.5 | 3.31 | 3.38 | 3.1 | 3.48 | 3.1 | 3.53
Heating Efficiency (%)
| BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BULKSTORAGE UNIT HEATERFAN | 0.8 | 0.8 | 0.8 | 1.44 | 0.8 | 0.8 | 0.8 | 2.44 | 1.7 | 0.8 | 5.23 | 4.58 | 6.8 | 7.24 | 7.77 | 12.65
| FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.23 | 1.32 | 1.56 | 1.4 | 0.87 | 1.47 | 0.88 | 1.43 | 1.51 | 1.15 | 1.78 | 1.85 | 1.99 | 2.14 | 2.11 | 2.66
| FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 3.35 | 3.94 | 5.14 | 5.3 | 1.78 | 4.28 | 2.62 | 5.92 | 5.87 | 4.28 | 8.2 | 8.2 | 9.45 | 10.11 | 10.29 | 13.85
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.092747 | 0.12534 | 0.11324 | 0.10432 | 0.1366 | 0.10249 | 0.1522 | 0.082328 | 0.037852 | 0.072471 | 0.053476 | 0.03779 | 0.065703 | 0.079702 | 0.062946 | 0.10144
| Total Cost ($/m2) | 3.91 | 5.51 | 5.73 | 4.46 | 4.55 | 4.67 | 5.18 | 3.59 | 1.63 | 2.81 | 2.49 | 1.75 | 3.12 | 3.79 | 3.07 | 5.64
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011416 | 0.0080549 | 0.0080483 | 0.009428 | 0.008865 | 0.0075725 | 0.0087026 | 0.0096434 | 0.0068427 | 0.0084566 | 0.0082518 | 0.0068637 | 0.0079248 | 0.0079738 | 0.0078899 | 0.0041055
| Total Cost ($/m2) | 0.01 | 0.4 | 0.26 | 1.06 | 0.14 | 0.54 | 0.58 | 1.98 | 1.01 | 1.28 | 2.55 | 1.63 | 3.87 | 2.93 | 5.01 | 5.46
Total Utility Costs
| Cost Intensity ($/m2) | 3.92 | 5.91 | 5.99 | 5.51 | 4.69 | 5.21 | 5.76 | 5.57 | 2.64 | 4.09 | 5.04 | 3.38 | 6.99 | 6.72 | 8.08 | 11.1
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 36344.4444 | 29380.5556 | 50691.6667 | 13972.2222 | 1441.6667 | 31538.8889 | 422.2222 | 10791.6667 | 8569.4444 | 488.8889 | 6586.1111 | 4625 | 4627.7778 | 1800 | 1052.7778 | 80.5556
| Interior Lighting | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111
| Exterior Lighting | 32122.2222 | 32111.1111 | 32102.7778 | 32100 | 32075 | 32066.6667 | 32083.3333 | 32063.8889 | 32077.7778 | 32013.8889 | 32069.4444 | 32052.7778 | 32050 | 32041.6667 | 32022.2222 | 31827.7778
| Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 17647.2222 | 33311.1111 | 44291.6667 | 43016.6667 | 10111.1111 | 39016.6667 | 14330.5556 | 50352.7778 | 50097.2222 | 37302.7778 | 68997.2222 | 69041.6667 | 75533.3333 | 78452.7778 | 85319.4444 | 119261.1111
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 203683.3333 | 212366.6667 | 244655.5556 | 206655.5556 | 161194.4444 | 220188.8889 | 164405.5556 | 210775 | 208313.8889 | 187372.2222 | 225219.4444 | 223283.3333 | 229777.7778 | 229861.1111 | 235963.8889 | 268736.1111
Gas (MJ)
| Heating | 5550 | 240550 | 158930 | 541260 | 76880 | 346430 | 323160 | 993510 | 711710 | 732870 | 1492500 | 1151280 | 2359650 | 1775200 | 3070850 | 6435570
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5550 | 240550 | 158930 | 541260 | 76880 | 346430 | 323160 | 993510 | 711710 | 732870 | 1492500 | 1151280 | 2359650 | 1775200 | 3070850 | 6435570
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 738800 | 1005080 | 1039690 | 1285220 | 657180 | 1139110 | 915020 | 1752300 | 1461640 | 1407410 | 2303290 | 1955100 | 3186850 | 2602690 | 3920320 | 7403030
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 27.0603 | 21.8753 | 37.7425 | 10.403 | 1.0734 | 23.4823 | 0.31437 | 8.0349 | 6.3804 | 0.364 | 4.9037 | 3.4435 | 3.4456 | 1.3402 | 0.78385 | 0.059978
| Interior Lighting (elec) | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382
| Exterior Lighting (elec) | 23.9166 | 23.9084 | 23.9021 | 23.9001 | 23.8815 | 23.8753 | 23.8877 | 23.8732 | 23.8835 | 23.836 | 23.8773 | 23.8649 | 23.8629 | 23.8566 | 23.8422 | 23.6974
| Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 13.1393 | 24.8018 | 32.9774 | 32.0281 | 7.5282 | 29.0499 | 10.6698 | 37.4902 | 37.2999 | 27.7738 | 51.3719 | 51.405 | 56.2384 | 58.4121 | 63.5247 | 88.796
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 151.6526 | 158.1178 | 182.1585 | 153.8656 | 120.0175 | 163.9418 | 122.4083 | 156.9327 | 155.1003 | 139.5081 | 167.6873 | 166.2458 | 171.0812 | 171.1433 | 175.6871 | 200.0877
Gas (MJ/m2)
| Heating (gas) | 1.1478 | 49.7505 | 32.8699 | 111.9432 | 15.9003 | 71.6485 | 66.8358 | 205.4774 | 147.1956 | 151.5719 | 308.6784 | 238.1074 | 488.022 | 367.1463 | 635.1122 | 1331.0025
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1.1478 | 49.7505 | 32.8699 | 111.9432 | 15.9003 | 71.6485 | 66.8358 | 205.4774 | 147.1956 | 151.5719 | 308.6784 | 238.1074 | 488.022 | 367.1463 | 635.1122 | 1331.0025
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 152.7984 | 207.8703 | 215.0283 | 265.8088 | 135.9178 | 235.5904 | 189.2441 | 362.4101 | 302.2959 | 291.0801 | 476.3657 | 404.3531 | 659.1033 | 538.2875 | 810.7993 | 1531.0922
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 53.0818 | 51.1363 | 51.346 | 50.1982 | 48.337 | 55.224 | 49.2517 | 58.1148 | 50.7708 | 54.8555 | 63.1274 | 63.1469 | 64.3764 | 65.7098 | 66.0335 | 72.8629
| Feb | 58.9544 | 57.0772 | 53.6025 | 49.8933 | 42.7757 | 48.1423 | 42.7626 | 50.9179 | 50.9666 | 47.5065 | 62.7158 | 55.7979 | 57.0274 | 58.3608 | 58.6845 | 72.8629
| Mar | 63.6418 | 52.1049 | 70.6118 | 51.5757 | 42.5467 | 49.6486 | 41.9027 | 52.7024 | 51.1994 | 47.9551 | 55.9148 | 56.2445 | 57.0274 | 58.3608 | 58.6845 | 65.5139
| Apr | 68.5882 | 64.7055 | 73.363 | 61.707 | 43.2749 | 68.4492 | 42.9759 | 52.8866 | 56.0168 | 47.5065 | 56.316 | 57.1347 | 56.47 | 57.7628 | 58.6845 | 65.5139
| May | 77.559 | 81.8814 | 88.078 | 73.8526 | 42.725 | 78.4352 | 43.3528 | 61.9748 | 67.6947 | 49.0259 | 68.7727 | 67.4461 | 69.4798 | 59.3248 | 59.5087 | 64.4133
| Jun | 78.409 | 83.8507 | 101.3162 | 84.7247 | 42.9303 | 84.2806 | 43.4737 | 88.8646 | 78.8008 | 52.2196 | 91.9345 | 78.6325 | 91.9445 | 82.2197 | 69.9597 | 69.9424
| Jul | 77.2229 | 84.6387 | 101.5872 | 95.038 | 49.1673 | 84.1977 | 52.7224 | 94.8634 | 81.0308 | 61.4448 | 94.7168 | 85.1676 | 89.4316 | 81.5153 | 84.1987 | 70.774
| Aug | 78.3639 | 84.8486 | 101.2051 | 85.6884 | 53.9351 | 84.0137 | 44.0521 | 92.4311 | 81.3361 | 56.4842 | 90.3629 | 85.7921 | 87.4294 | 76.412 | 75.793 | 68.4869
| Sep | 76.8857 | 82.4159 | 95.8537 | 77.1081 | 55.152 | 82.8452 | 59.2556 | 76.1723 | 64.792 | 55.347 | 74.9903 | 71.8634 | 70.4427 | 63.5171 | 60.6542 | 64.4133
| Oct | 73.0089 | 71.177 | 74.0835 | 63.6832 | 43.8868 | 67.3274 | 43.3718 | 59.213 | 53.1182 | 48.4144 | 57.6107 | 61.4017 | 57.4751 | 58.9388 | 58.0376 | 72.8629
| Nov | 62.4909 | 56.8403 | 63.4583 | 51.0297 | 48.7715 | 55.7666 | 49.2517 | 58.1148 | 58.1198 | 54.8555 | 62.7158 | 62.7964 | 64.3764 | 65.1118 | 66.0335 | 72.8629
| Dec | 54.7011 | 50.7402 | 51.1702 | 49.945 | 48.6211 | 55.224 | 49.2517 | 58.1148 | 58.1198 | 54.8555 | 62.7158 | 63.1469 | 64.3764 | 65.7098 | 66.0335 | 72.8629
Time of Peak Electrical Demand
| Jan | 24-JAN-13:00 | 03-JAN-14:30 | 26-JAN-15:50 | 23-JAN-15:00 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 02-JAN-16:49 | 02-JAN-09:09 | 02-JAN-16:30 | 06-JAN-16:30 | 05-JAN-16:49 | 02-JAN-16:40 | 03-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
| Feb | 22-FEB-13:00 | 23-FEB-15:50 | 28-FEB-16:40 | 27-FEB-15:00 | 13-FEB-11:00 | 08-FEB-15:00 | 15-FEB-15:00 | 08-FEB-09:09 | 14-FEB-15:00 | 01-FEB-09:09 | 01-FEB-16:00 | 14-FEB-09:09 | 01-FEB-09:09 | 06-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
| Mar | 13-MAR-15:00 | 24-MAR-15:50 | 17-MAR-15:39 | 28-MAR-14:00 | 31-MAR-14:20 | 31-MAR-14:50 | 01-MAR-09:09 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-15:30 | 31-MAR-14:00 | 30-MAR-15:00 | 06-MAR-09:09 | 02-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09
| Apr | 03-APR-14:50 | 21-APR-14:00 | 26-APR-15:39 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:20 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 03-APR-08:09 | 07-APR-14:00 | 25-APR-14:00 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-13:39 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 01-MAY-08:09
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:39 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-14:39 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 10-JUL-13:00 | 31-JUL-13:00 | 11-JUL-15:00 | 03-JUL-14:00 | 10-JUL-15:00 | 25-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:50 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-14:50 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-15:30 | 15-AUG-12:09 | 17-AUG-14:00 | 01-AUG-14:09 | 07-AUG-15:39 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-15:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:00 | 01-SEP-15:00 | 05-SEP-13:00 | 06-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 01-SEP-08:09
| Oct | 06-OCT-14:30 | 06-OCT-15:00 | 02-OCT-15:39 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 31-OCT-13:20 | 03-OCT-14:00 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-15:00 | 06-OCT-14:00 | 06-OCT-15:00 | 02-OCT-08:09 | 23-OCT-08:09
| Nov | 07-NOV-14:00 | 03-NOV-14:50 | 13-NOV-15:39 | 22-NOV-14:00 | 20-NOV-16:49 | 10-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 06-NOV-16:49 | 27-NOV-16:40 | 08-NOV-16:00 | 21-NOV-16:30 | 01-NOV-08:09
| Dec | 13-DEC-13:00 | 19-DEC-15:20 | 11-DEC-15:39 | 01-DEC-15:30 | 18-DEC-16:49 | 01-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 05-DEC-16:30 | 08-DEC-16:40 | 04-DEC-16:19 | 01-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 2438.28 | 3039.43 | 2959.4 | 3093.73 | 1879.99 | 3213.73 | 2184.7 | 3798.35 | 3265.44 | 1975.34 | 4504.87 | 3924.28 | 5419.82 | 4814.89 | 6272.99 | 10483.39
| Total Source Energy (MJ/m2) | 504.28 | 628.61 | 612.06 | 639.84 | 388.82 | 664.66 | 451.84 | 785.57 | 675.36 | 408.54 | 931.7 | 811.62 | 1120.92 | 995.81 | 1297.38 | 2168.17
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 55960.0806 | 75175.3131 | 76721.5013 | 73417.6241 | 20224.5507 | 80511.4659 | 25040.8879 | 74794.6511 | 97929.5305 | 26862.7026 | 146989.4601 | 111971.7993 | 121201.9361 | 116011.054 | 136144.4599 | 191670.1084
| CO2 (kg) | 129635.935 | 190284.3873 | 181966.2239 | 172676.1406 | 54300.2414 | 193945.1409 | 68133.2801 | 179314.8591 | 235360.7721 | 70600.8263 | 354806.3344 | 272512.3923 | 304259.4058 | 287859.5196 | 346194.8739 | 524720.8674
| NOX (kg) | 228.3794 | 245.0163 | 301.075 | 304.5854 | 46.6774 | 304.843 | 59.1838 | 302.0233 | 381.5551 | 86.7528 | 575.069 | 427.3489 | 442.4902 | 430.7703 | 485.039 | 541.7191
| SO2 (kg) | 871.8475 | 1013.0567 | 983.853 | 725.5026 | 469.0804 | 1211.3103 | 478.487 | 769.6824 | 909.8526 | 145.0208 | 1518.1991 | 975.3455 | 542.9423 | 614.2293 | 557.7354 | 1369.705
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.004 | 0.0029 | 0.0027 | 0.0027 | 0.0002 | 0.0023 | 0.0002 | 0.0032 | 0.0036 | 0.0006 | 0.0047 | 0.0039 | 0.0042 | 0.0044 | 0.0044 | 0.0053
| Water for Electricity (m3) | 107.9029 | 345.5466 | 7267.36 | 1290.27 | 2830.23 | 6040.67 | 2886.59 | 47.854 | 945.9081 | 1914.35 | 349.4145 | 1013.89 | 356.4849 | 14560.3 | 366.0838 | 274.5635

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 738.8 | 152.8 | 152.8
Net Site Energy | 738.8 | 152.8 | 152.8
Total Source Energy | 2438.28 | 504.28 | 504.28
Net Source Energy | 2438.28 | 504.28 | 504.28
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5.55 | 0 | 0 | 0 | 0
Cooling | 130.84 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 63.53 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 733.26 | 5.55 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28130.56 | 19602.6 | 8527.96 | 0.7 | 3.34
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 83286.36 | 56308.51 | 26977.85 | 0.68 | 2.97
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39347.64 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 14670.25 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 35802.63 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.23 | 1399.81 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 3.35 | 3667.96 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9592.0804 | 16.7597 | 63.4186 | 0 | 0.0003 | 7848.8015 | 4126.7274
February | 8615.8393 | 15.1677 | 57.8592 | 0 | 0.0003 | 7160.8476 | 3718.1218
March | 9969.808 | 17.5391 | 66.8559 | 0 | 0.0003 | 8274.2952 | 4301.2
April | 9811.8631 | 17.302 | 66.1179 | 0 | 0.0003 | 8182.9962 | 4237.1483
May | 11512.3831 | 20.3033 | 77.5976 | 0 | 0.0004 | 9603.7683 | 4971.7624
June | 12492.2371 | 22.0314 | 84.2022 | 0 | 0.0004 | 10421.1743 | 5394.9242
July | 12933.4445 | 22.8095 | 87.1761 | 0 | 0.0004 | 10789.2348 | 5585.465
August | 13539.5796 | 23.8785 | 91.2617 | 0 | 0.0004 | 11294.88 | 5847.2318
September | 11548.724 | 20.3674 | 77.8426 | 0 | 0.0004 | 9634.0844 | 4987.4566
October | 10742.3412 | 18.9453 | 72.4073 | 0 | 0.0003 | 8961.3901 | 4639.2104
November | 9647.1749 | 17.0124 | 65.0145 | 0 | 0.0003 | 8046.4344 | 4166.1103
December | 9230.4598 | 16.2633 | 62.0938 | 0 | 0.0003 | 7684.9484 | 3984.7225
Annual Sum or Average | 129635.935 | 228.3794 | 871.8475 | 0 | 0.004 | 107902.8553 | 55960.0806
Minimum of Months | 8615.8393 | 15.1677 | 57.8592 | 0 | 0.0003 | 7160.8476 | 3718.1218
Maximum of Months | 13539.5796 | 23.8785 | 91.2617 | 0 | 0.0004 | 11294.88 | 5847.2318
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 53337000000 | 53081.791 | 24-JAN-13:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 9980.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 48661900000 | 58954.373 | 22-FEB-13:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 15852.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 56228400000 | 63641.817 | 13-MAR-15:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 20540.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 55608000000 | 68588.226 | 03-APR-14:50 | 28855.207 | 9104.397 | 5142.179 | 0 | 25486.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65262900000 | 77559.044 | 24-MAY-14:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 34457.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 70817700000 | 78408.952 | 28-JUN-14:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 35307.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 73318800000 | 77222.875 | 10-JUL-13:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 34121.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 76755000000 | 78363.877 | 21-AUG-14:50 | 28855.207 | 9104.397 | 5142.179 | 0 | 35262.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 65469000000 | 76885.733 | 07-SEP-13:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 33783.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 60897600000 | 73008.899 | 06-OCT-14:30 | 28855.207 | 9104.397 | 5142.179 | 0 | 29907.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 54680000000 | 62490.893 | 07-NOV-14:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 19389.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 52223500000 | 54701.122 | 13-DEC-13:00 | 28855.207 | 9104.397 | 5142.179 | 0 | 11599.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 733260000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 48661900000 | 53081.791 |  | 28855.207 | 9104.397 | 5142.179 | 0 | 9980.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 76755000000 | 78408.952 |  | 28855.207 | 9104.397 | 5142.179 | 0 | 35307.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18891.09 | 63.36 | 0 | 18954.45
Cost per Total Building Area ($/m2) | 3.91 | 0.01 | 0 | 3.92
Cost per Net Conditioned Building Area ($/m2) | 3.91 | 0.01 | 0 | 3.92

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1005.08 | 207.87 | 207.87
Net Site Energy | 1005.08 | 207.87 | 207.87
Total Source Energy | 3039.43 | 628.61 | 628.61
Net Source Energy | 3039.43 | 628.61 | 628.61
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 240.55 | 0 | 0 | 0 | 0
Cooling | 105.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.6 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 119.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 764.52 | 240.55 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29383.79 | 20682.07 | 8701.72 | 0.7 | 3.36
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 97771.18 | 66101.45 | 31669.73 | 0.68 | 3.33
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39203.23 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27256.55 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 123394.07 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1500.77 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.94 | 7510.02 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17584.1833 | 21.4605 | 77.0701 | 0 | 0.0002 | 26282.629 | 6794.668
February | 15375.1036 | 18.8744 | 68.928 | 0 | 0.0002 | 23506.596 | 5955.2362
March | 14474.116 | 18.6478 | 77.2055 | 0 | 0.0002 | 26334.2997 | 5719.6125
April | 12792.8239 | 16.7801 | 72.4164 | 0 | 0.0002 | 24702.166 | 5093.6921
May | 15190.2349 | 19.9629 | 86.5215 | 0 | 0.0002 | 29513.7293 | 6053.1786
June | 17728.1697 | 23.3021 | 101.0315 | 0 | 0.0003 | 34463.3332 | 7065.0239
July | 18801.4473 | 24.7128 | 107.148 | 0 | 0.0003 | 36549.7709 | 7492.7461
August | 18981.9993 | 24.9501 | 108.1768 | 0 | 0.0003 | 36900.6875 | 7564.6976
September | 15207.3543 | 19.9885 | 86.6633 | 0 | 0.0002 | 29562.1434 | 6060.409
October | 13848.8008 | 18.1762 | 78.5489 | 0 | 0.0002 | 26794.0566 | 5515.5733
November | 13584.1723 | 17.5885 | 73.6805 | 0 | 0.0002 | 25132.3655 | 5379.1881
December | 16715.9819 | 20.5724 | 75.6661 | 0 | 0.0002 | 25804.7947 | 6481.2879
Annual Sum or Average | 190284.3873 | 245.0163 | 1013.0567 | 0 | 0.0029 | 345546.5718 | 75175.3131
Minimum of Months | 12792.8239 | 16.7801 | 68.928 | 0 | 0.0002 | 23506.596 | 5093.6921
Maximum of Months | 18981.9993 | 24.9501 | 108.1768 | 0 | 0.0003 | 36900.6875 | 7564.6976
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 58150400000 | 51136.289 | 03-JAN-14:30 | 28855.207 | 9104.397 | 9085.196 | 0 | 4091.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 52008400000 | 57077.237 | 23-FEB-15:50 | 28855.207 | 9104.397 | 9085.196 | 0 | 10032.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 58264700000 | 52104.925 | 24-MAR-15:50 | 28855.207 | 9104.397 | 9085.196 | 0 | 5060.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 54653600000 | 64705.486 | 21-APR-14:00 | 28855.207 | 9104.397 | 9085.196 | 0 | 17660.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65299200000 | 81881.38 | 26-MAY-14:00 | 28855.207 | 9104.397 | 9085.196 | 0 | 34836.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 76250200000 | 83850.659 | 13-JUN-14:00 | 28855.207 | 9104.397 | 9085.196 | 0 | 36805.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 80866400000 | 84638.656 | 31-JUL-13:00 | 28855.207 | 9104.397 | 9085.196 | 0 | 37593.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 81642800000 | 84848.588 | 31-AUG-13:00 | 28855.207 | 9104.397 | 9085.196 | 0 | 37803.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 65406300000 | 82415.927 | 15-SEP-14:00 | 28855.207 | 9104.397 | 9085.196 | 0 | 35371.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59281900000 | 71177.032 | 06-OCT-15:00 | 28855.207 | 9104.397 | 9085.196 | 0 | 24132.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 55605400000 | 56840.312 | 03-NOV-14:50 | 28855.207 | 9104.397 | 9085.196 | 0 | 9795.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 57093200000 | 50740.181 | 19-DEC-15:20 | 28855.207 | 9104.397 | 9085.196 | 0 | 3695.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 764522000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 52008400000 | 50740.181 |  | 28855.207 | 9104.397 | 9085.196 | 0 | 3695.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 81642800000 | 84848.588 |  | 28855.207 | 9104.397 | 9085.196 | 0 | 37803.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26618.27 | 1937.6 | 0 | 28555.87
Cost per Total Building Area ($/m2) | 5.51 | 0.4 | 0 | 5.91
Cost per Net Conditioned Building Area ($/m2) | 5.51 | 0.4 | 0 | 5.91

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1039.69 | 215.03 | 215.03
Net Site Energy | 1039.69 | 215.03 | 215.03
Total Source Energy | 2959.4 | 612.06 | 612.06
Net Source Energy | 2959.4 | 612.06 | 612.06
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 158.93 | 0 | 0 | 0 | 0
Cooling | 182.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 159.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 880.76 | 158.93 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 29540.15 | 22245.02 | 7295.13 | 0.75 | 3.48
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 127611.2 | 86275.79 | 41335.41 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 37800.65 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21819.68 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 85022.96 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.56 | 1780.71 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.14 | 9640.53 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14223.187 | 22.2273 | 67.455 | 0 | 0.0002 | 498198.3606 | 5864.7972
February | 12809.8196 | 20.0005 | 60.6209 | 0 | 0.0002 | 447723.3072 | 5280.1769
March | 12633.5917 | 21.0134 | 69.1048 | 0 | 0.0002 | 510457.4648 | 5337.788
April | 11893.457 | 20.0599 | 67.0646 | 0 | 0.0002 | 495400.7913 | 5053.148
May | 14541.6041 | 24.5729 | 82.3336 | 0 | 0.0002 | 608193.9299 | 6182.967
June | 19399.6488 | 32.7885 | 109.8852 | 0 | 0.0003 | 811716.6441 | 8249.2053
July | 20757.393 | 35.0834 | 117.5761 | 0 | 0.0003 | 868528.6898 | 8826.5543
August | 20258.4617 | 34.2401 | 114.75 | 0 | 0.0003 | 847652.4584 | 8614.3965
September | 16244.4755 | 27.4558 | 92.0136 | 0 | 0.0002 | 679699.6634 | 6907.5507
October | 12567.6059 | 21.2188 | 71.0239 | 0 | 0.0002 | 524648.7913 | 5341.7796
November | 11693.3155 | 19.5237 | 64.4987 | 0 | 0.0002 | 476437.2225 | 4948.0226
December | 14943.6639 | 22.8908 | 67.5265 | 0 | 0.0002 | 498699.843 | 6115.1149
Annual Sum or Average | 181966.2239 | 301.075 | 983.853 | 0 | 0.0027 | 7267360 | 76721.5013
Minimum of Months | 11693.3155 | 19.5237 | 60.6209 | 0 | 0.0002 | 447723.3072 | 4948.0226
Maximum of Months | 20757.393 | 35.0834 | 117.5761 | 0 | 0.0003 | 868528.6898 | 8826.5543
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 60378700000 | 51345.965 | 26-JAN-15:50 | 28855.207 | 9104.397 | 11495.645 | 0 | 1890.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54261500000 | 53602.503 | 28-FEB-16:40 | 28855.207 | 9104.397 | 11495.645 | 0 | 4147.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61864500000 | 70611.817 | 17-MAR-15:39 | 28855.207 | 9104.397 | 11495.645 | 0 | 21156.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 60039700000 | 73363.036 | 26-APR-15:39 | 28855.207 | 9104.397 | 11495.645 | 0 | 23907.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 73709600000 | 88077.998 | 30-MAY-15:00 | 28855.207 | 9104.397 | 11495.645 | 0 | 38622.748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 98375300000 | 101316.215 | 28-JUN-15:00 | 28855.207 | 9104.397 | 11421.239 | 0 | 51935.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 105261000000 | 101587.161 | 11-JUL-15:00 | 28855.207 | 9104.397 | 11495.645 | 0 | 52131.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 102731000000 | 101205.091 | 01-AUG-15:00 | 28855.207 | 9104.397 | 11421.239 | 0 | 51824.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 82375600000 | 95853.749 | 08-SEP-15:00 | 28855.207 | 9104.397 | 11495.645 | 0 | 46398.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 63584400000 | 74083.492 | 02-OCT-15:39 | 28855.207 | 9104.397 | 11495.645 | 0 | 24628.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 57741400000 | 63458.26 | 13-NOV-15:39 | 28855.207 | 9104.397 | 11495.645 | 0 | 14003.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 60439500000 | 51170.175 | 11-DEC-15:39 | 28855.207 | 9104.397 | 11495.645 | 0 | 1714.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 880761000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 54261500000 | 51170.175 |  | 28855.207 | 9104.397 | 11421.239 | 0 | 1714.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 105261000000 | 101587.161 |  | 28855.207 | 9104.397 | 11495.645 | 0 | 52131.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27703.67 | 1279.11 | 0 | 28982.77
Cost per Total Building Area ($/m2) | 5.73 | 0.26 | 0 | 5.99
Cost per Net Conditioned Building Area ($/m2) | 5.73 | 0.26 | 0 | 5.99

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1285.22 | 265.81 | 265.81
Net Site Energy | 1285.22 | 265.81 | 265.81
Total Source Energy | 3093.73 | 639.84 | 639.84
Net Source Energy | 3093.73 | 639.84 | 639.84
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 541.26 | 0 | 0 | 0 | 0
Cooling | 50.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 154.86 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 743.96 | 541.26 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.691 | 2.265 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28968.35 | 20989.88 | 7978.47 | 0.72 | 3.41
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 131627.34 | 88991.03 | 42636.3 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 69523.61 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 32614.14 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 160114.26 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 1.44 | 133.51 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.4 | 1591.9 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.3 | 9943.93 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20709.5555 | 31.4014 | 61.8716 | 0 | 0.0002 | 109980.6021 | 8331.5636
February | 17414.9638 | 26.8701 | 54.3047 | 0 | 0.0002 | 96536.8538 | 7049.0094
March | 14234.1689 | 25.0852 | 59.6944 | 0 | 0.0002 | 106163.049 | 6049.9289
April | 11663.9321 | 21.5714 | 53.8951 | 0 | 0.0002 | 95860.2595 | 5051.3188
May | 11781.307 | 22.7252 | 59.0289 | 0 | 0.0002 | 105000.5782 | 5188.6515
June | 13024.9537 | 25.1507 | 65.3909 | 0 | 0.0002 | 116317.5992 | 5738.8366
July | 13693.1805 | 26.441 | 68.7456 | 0 | 0.0003 | 122284.8617 | 6033.2569
August | 13994.4257 | 27.0231 | 70.2599 | 0 | 0.0003 | 124978.592 | 6166.0235
September | 11802.3747 | 22.7885 | 59.246 | 0 | 0.0002 | 105386.9908 | 5200.0318
October | 11686.6698 | 22.0803 | 56.2885 | 0 | 0.0002 | 100121.75 | 5104.2766
November | 14301.3073 | 24.6137 | 57.0846 | 0 | 0.0002 | 101515.3714 | 6023.993
December | 18369.3015 | 28.8346 | 59.6924 | 0 | 0.0002 | 106121.7555 | 7480.7333
Annual Sum or Average | 172676.1406 | 304.5854 | 725.5026 | 0 | 0.0027 | 1290270 | 73417.6241
Minimum of Months | 11663.9321 | 21.5714 | 53.8951 | 0 | 0.0002 | 95860.2595 | 5051.3188
Maximum of Months | 20709.5555 | 31.4014 | 70.2599 | 0 | 0.0003 | 124978.592 | 8331.5636
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 63413800000 | 50198.152 | 23-JAN-15:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 628.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 55662200000 | 49893.35 | 27-FEB-15:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 323.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 61212600000 | 51575.688 | 28-MAR-14:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 2005.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 55272100000 | 61706.987 | 14-APR-15:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 12137.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 60542300000 | 73852.574 | 15-MAY-14:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 24282.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 67067600000 | 84724.694 | 19-JUN-14:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 35154.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 70508300000 | 95037.969 | 03-JUL-14:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 45468.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 72061500000 | 85688.369 | 17-AUG-13:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 36118.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 60765100000 | 77108.13 | 11-SEP-13:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 27538.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 57729300000 | 63683.16 | 12-OCT-15:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 14113.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58532800000 | 51029.744 | 22-NOV-14:00 | 28855.207 | 9104.397 | 11610.238 | 0 | 1459.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 61188800000 | 49945.045 | 01-DEC-15:30 | 28855.207 | 9104.397 | 11610.238 | 0 | 375.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 743956000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 55272100000 | 49893.35 |  | 28855.207 | 9104.397 | 11610.238 | 0 | 323.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 72061500000 | 95037.969 |  | 28855.207 | 9104.397 | 11610.238 | 0 | 45468.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 21559.02 | 5102.99 | 0 | 26662.01
Cost per Total Building Area ($/m2) | 4.46 | 1.06 | 0 | 5.51
Cost per Net Conditioned Building Area ($/m2) | 4.46 | 1.06 | 0 | 5.51

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 657.18 | 135.92 | 135.92
Net Site Energy | 657.18 | 135.92 | 135.92
Total Source Energy | 1879.99 | 388.82 | 388.82
Net Source Energy | 1879.99 | 388.82 | 388.82
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 76.88 | 0 | 0 | 0 | 0
Cooling | 5.19 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.47 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 36.4 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 580.3 | 76.88 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 16453.04 | 12390.4 | 4062.64 | 0.75 | 3.51
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 44142.22 | 29843.81 | 14298.4 | 0.68 | 3.1
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39207.88 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 17706.76 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 56072.99 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.54 | 622 | 0.87 | 1009.94 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.78 | 1944.04 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 5544.9855 | 4.8068 | 40.7026 | 0 | 0 | 245556.5839 | 2043.3109
February | 4782.6296 | 4.1393 | 36.2844 | 0 | 0 | 218906.737 | 1765.9785
March | 4926.4668 | 4.2421 | 41.2697 | 0 | 0 | 248999.0747 | 1830.9706
April | 4196.9646 | 3.6031 | 37.1007 | 0 | 0 | 223853.2755 | 1565.7694
May | 4251.1282 | 3.6419 | 38.9482 | 0 | 0 | 235004.8006 | 1590.152
June | 4136.2666 | 3.5418 | 38.2077 | 0 | 0 | 230537.9531 | 1548.139
July | 4014.4842 | 3.4357 | 37.4003 | 0 | 0 | 225667.1059 | 1503.5264
August | 4438.1629 | 3.7983 | 41.347 | 0 | 0 | 249480.9626 | 1662.2036
September | 4133.6751 | 3.5379 | 38.4843 | 0 | 0 | 232207.9162 | 1548.0859
October | 4317.2893 | 3.6967 | 39.8958 | 0 | 0 | 240723.8244 | 1615.9416
November | 4432.789 | 3.8035 | 39.5507 | 0 | 0 | 238636.6682 | 1654.8633
December | 5125.3995 | 4.4304 | 39.8891 | 0 | 0 | 240658.2096 | 1895.6095
Annual Sum or Average | 54300.2414 | 46.6774 | 469.0804 | 0 | 0.0002 | 2830230 | 20224.5507
Minimum of Months | 4014.4842 | 3.4357 | 36.2844 | 0 | 0 | 218906.737 | 1503.5264
Maximum of Months | 5544.9855 | 4.8068 | 41.347 | 0 | 0 | 249480.9626 | 2043.3109
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 50348300000 | 48336.991 | 02-JAN-16:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 44884100000 | 42775.651 | 13-FEB-11:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 1787.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 51054200000 | 42546.701 | 31-MAR-14:20 | 28855.207 | 9104.397 | 3028.387 | 0 | 1558.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 45898300000 | 43274.929 | 11-APR-15:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 2286.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 48184800000 | 42725.036 | 30-MAY-13:39 | 28855.207 | 9104.397 | 3028.387 | 0 | 1737.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 47268900000 | 42930.301 | 30-JUN-14:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 1942.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 46270200000 | 49167.264 | 10-JUL-15:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 8179.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 51153000000 | 53935.124 | 08-AUG-12:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 12947.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 47611300000 | 55152.045 | 25-SEP-12:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 14164.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 49357400000 | 43886.752 | 19-OCT-10:00 | 28855.207 | 9104.397 | 3028.387 | 0 | 2898.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 48929500000 | 48771.522 | 20-NOV-16:49 | 28855.207 | 9104.397 | 3028.387 | 0 | 434.531 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 49344000000 | 48621.101 | 18-DEC-16:49 | 28855.207 | 9104.397 | 3028.387 | 0 | 284.109 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 580304000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 44884100000 | 42546.701 |  | 28855.207 | 9104.397 | 3028.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 51153000000 | 55152.045 |  | 28855.207 | 9104.397 | 3028.387 | 0 | 14164.054 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22018.46 | 681.54 | 0 | 22700.01
Cost per Total Building Area ($/m2) | 4.55 | 0.14 | 0 | 4.69
Cost per Net Conditioned Building Area ($/m2) | 4.55 | 0.14 | 0 | 4.69

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1139.11 | 235.59 | 235.59
Net Site Energy | 1139.11 | 235.59 | 235.59
Total Source Energy | 3213.73 | 664.66 | 664.66
Net Source Energy | 3213.73 | 664.66 | 664.66
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 346.43 | 0 | 0 | 0 | 0
Cooling | 113.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.44 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 140.46 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 792.68 | 346.43 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.742 | 2.356 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24482.15 | 19470.25 | 5011.89 | 0.8 | 3.59
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 93299.88 | 66285.29 | 27014.59 | 0.71 | 3.47
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 36355.77 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 26690.19 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 117785.49 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.47 | 1669.38 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.28 | 8171.63 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 19789.7501 | 27.9373 | 93.82 | 0 | 0.0002 | 467747.6482 | 7885.9155
February | 13959.1166 | 21.1959 | 80.1803 | 0 | 0.0002 | 399821.6102 | 5717.3354
March | 15722.0539 | 24.0019 | 91.5206 | 0 | 0.0002 | 456375.8602 | 6452.8199
April | 12171.4053 | 19.8646 | 82.9134 | 0 | 0.0002 | 413508.5854 | 5128.9022
May | 13952.7504 | 22.8341 | 95.6333 | 0 | 0.0002 | 476947.5952 | 5886.0118
June | 18003.3677 | 29.5236 | 123.9651 | 0 | 0.0002 | 618248.14 | 7601.0655
July | 19537.5524 | 32.0402 | 134.5353 | 0 | 0.0003 | 670964.3635 | 8248.8713
August | 19875.3141 | 32.5941 | 136.8611 | 0 | 0.0003 | 682563.8761 | 8391.4763
September | 15357.2009 | 25.1844 | 105.7469 | 0 | 0.0002 | 527388.9065 | 6483.874
October | 12927.1336 | 21.1331 | 88.3913 | 0 | 0.0002 | 440829.4215 | 5451.0048
November | 14430.0124 | 22.307 | 86.6083 | 0 | 0.0002 | 431891.8179 | 5951.3752
December | 18219.4835 | 26.2268 | 91.1347 | 0 | 0.0002 | 454385.5586 | 7312.814
Annual Sum or Average | 193945.1409 | 304.843 | 1211.3103 | 0 | 0.0023 | 6040670 | 80511.4659
Minimum of Months | 12171.4053 | 19.8646 | 80.1803 | 0 | 0.0002 | 399821.6102 | 5128.9022
Maximum of Months | 19875.3141 | 32.5941 | 136.8611 | 0 | 0.0003 | 682563.8761 | 8391.4763
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 61379700000 | 55224.02 | 02-JAN-16:40 | 28855.207 | 9104.397 | 9915.415 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 52466200000 | 48142.251 | 08-FEB-15:00 | 28855.207 | 9104.397 | 9915.415 | 0 | 267.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 59887500000 | 49648.598 | 31-MAR-14:50 | 28855.207 | 9104.397 | 9915.415 | 0 | 1773.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 54262300000 | 68449.201 | 21-APR-15:20 | 28855.207 | 9104.397 | 9915.415 | 0 | 20574.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 62587000000 | 78435.218 | 31-MAY-15:00 | 28855.207 | 9104.397 | 9915.415 | 0 | 30560.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 81129000000 | 84280.605 | 27-JUN-15:39 | 28855.207 | 9104.397 | 9915.415 | 0 | 36405.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 88046700000 | 84197.746 | 25-JUL-15:00 | 28855.207 | 9104.397 | 9915.415 | 0 | 36322.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 89568800000 | 84013.747 | 04-AUG-15:30 | 28855.207 | 9104.397 | 9915.415 | 0 | 36138.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 69206100000 | 82845.176 | 01-SEP-14:00 | 28855.207 | 9104.397 | 9915.415 | 0 | 34970.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 57847400000 | 67327.406 | 03-OCT-14:00 | 28855.207 | 9104.397 | 9915.415 | 0 | 19452.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 56674600000 | 55766.596 | 10-NOV-16:40 | 28855.207 | 9104.397 | 9915.415 | 0 | 542.576 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 59626300000 | 55224.02 | 01-DEC-16:30 | 28855.207 | 9104.397 | 9915.415 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 792682000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 52466200000 | 48142.251 |  | 28855.207 | 9104.397 | 9915.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 89568800000 | 84280.605 |  | 28855.207 | 9104.397 | 9915.415 | 0 | 36405.585 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 22568.19 | 2623.34 | 0 | 25191.53
Cost per Total Building Area ($/m2) | 4.67 | 0.54 | 0 | 5.21
Cost per Net Conditioned Building Area ($/m2) | 4.67 | 0.54 | 0 | 5.21

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 915.02 | 189.24 | 189.24
Net Site Energy | 915.02 | 189.24 | 189.24
Total Source Energy | 2184.7 | 451.84 | 451.84
Net Source Energy | 2184.7 | 451.84 | 451.84
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 323.16 | 0 | 0 | 0 | 0
Cooling | 1.52 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.5 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 51.59 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 591.86 | 323.16 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.569 | 0.637 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.682 | 2.247 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 14613.79 | 11671.38 | 2942.41 | 0.8 | 3.61
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52075.65 | 38377.09 | 13698.56 | 0.74 | 3.22
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 39333.64 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 21368.25 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 82489.86 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 0.88 | 1005.7 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.62 | 2863 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 9071.6057 | 7.9986 | 42.5024 | 0 | 0 | 256312.4946 | 3269.3711
February | 5813.8129 | 5.0699 | 37.2902 | 0 | 0 | 224946.8205 | 2125.9414
March | 6921.5804 | 6.0462 | 42.5662 | 0 | 0 | 256764.2884 | 2525.4383
April | 5456.877 | 4.7418 | 38.02 | 0 | 0 | 229363.5859 | 2004.6317
May | 4896.2092 | 4.224 | 39.5863 | 0 | 0 | 238837.0199 | 1815.3623
June | 4427.7773 | 3.8039 | 38.6651 | 0 | 0 | 233290.0986 | 1650.4267
July | 4169.266 | 3.5747 | 37.6805 | 0 | 0 | 227354.492 | 1557.9518
August | 4534.7199 | 3.8884 | 40.9172 | 0 | 0 | 246883.4976 | 1694.311
September | 4254.2147 | 3.6468 | 38.5777 | 0 | 0 | 232768.3787 | 1590.09
October | 4683.8749 | 4.0265 | 40.4253 | 0 | 0 | 243908.852 | 1744.4329
November | 5691.4578 | 4.9403 | 40.6101 | 0 | 0 | 244993.2313 | 2093.7228
December | 8211.8844 | 7.2228 | 41.6462 | 0 | 0 | 251170.0523 | 2969.2078
Annual Sum or Average | 68133.2801 | 59.1838 | 478.487 | 0 | 0.0002 | 2886590 | 25040.8879
Minimum of Months | 4169.266 | 3.5747 | 37.2902 | 0 | 0 | 224946.8205 | 1557.9518
Maximum of Months | 9071.6057 | 7.9986 | 42.5662 | 0 | 0 | 256764.2884 | 3269.3711
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 52553700000 | 49251.708 | 02-JAN-16:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 46122500000 | 42762.584 | 15-FEB-15:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 859.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 52646300000 | 41902.708 | 01-MAR-09:09 | 28855.207 | 9104.397 | 3943.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 47028200000 | 42975.908 | 13-APR-14:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 1073.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 48970600000 | 43352.77 | 17-MAY-13:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 1450.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 47833200000 | 43473.727 | 16-JUN-14:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 1571.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 46616200000 | 52722.447 | 03-JUL-12:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 10819.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 50620400000 | 44052.127 | 15-AUG-12:09 | 28855.207 | 9104.397 | 3943.104 | 0 | 2149.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 47726300000 | 59255.592 | 28-SEP-14:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 17352.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 50010500000 | 43371.797 | 31-OCT-13:20 | 28855.207 | 9104.397 | 3943.104 | 0 | 1469.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 50232800000 | 49251.708 | 10-NOV-16:00 | 28855.207 | 9104.397 | 3943.104 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 51499300000 | 49251.708 | 01-DEC-16:49 | 28855.207 | 9104.397 | 3943.104 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 591860000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 46122500000 | 41902.708 |  | 28855.207 | 9104.397 | 3943.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 52646300000 | 59255.592 |  | 28855.207 | 9104.397 | 3943.104 | 0 | 17352.884 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25022.91 | 2812.33 | 0 | 27835.24
Cost per Total Building Area ($/m2) | 5.18 | 0.58 | 0 | 5.76
Cost per Net Conditioned Building Area ($/m2) | 5.18 | 0.58 | 0 | 5.76

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1752.3 | 362.41 | 362.41
Net Site Energy | 1752.3 | 362.41 | 362.41
Total Source Energy | 3798.35 | 785.57 | 785.57
Net Source Energy | 3798.35 | 785.57 | 785.57
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 993.51 | 0 | 0 | 0 | 0
Cooling | 38.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.43 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 181.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 758.79 | 993.51 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.489 | 0.539 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.489 | 0.539 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.253 | 1.543 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30827.95 | 21997.05 | 8830.9 | 0.71 | 3.38
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 146948.37 | 99349.33 | 47599.04 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 115523.34 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34669.83 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 184991.88 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 2.44 | 226.52 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.43 | 1630.4 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.92 | 11101.38 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26833.799 | 36.8306 | 68.9864 | 0 | 0.0003 | 4285.6972 | 10427.7728
February | 20964.7584 | 30.0141 | 60.7393 | 0 | 0.0003 | 3774.2066 | 8260.3234
March | 16514.4129 | 26.8159 | 65.366 | 0 | 0.0003 | 4063.6363 | 6796.9788
April | 11593.4492 | 20.8696 | 57.1763 | 0 | 0.0002 | 3555.4203 | 4958.5465
May | 10145.5904 | 19.8888 | 59.0109 | 0 | 0.0002 | 3670.084 | 4487.9215
June | 11096.3337 | 22.1775 | 66.8871 | 0 | 0.0003 | 4160.058 | 4947.3386
July | 11395.9845 | 22.7839 | 68.735 | 0 | 0.0003 | 4274.9911 | 5081.6287
August | 12303.2753 | 24.5949 | 74.1912 | 0 | 0.0003 | 4614.3379 | 5485.9346
September | 9896.4918 | 19.7352 | 59.4105 | 0 | 0.0002 | 3695.0381 | 4408.3427
October | 11681.4821 | 21.5814 | 60.6657 | 0 | 0.0002 | 3772.6022 | 5046.7933
November | 14716.1102 | 24.5942 | 62.1042 | 0 | 0.0003 | 3861.169 | 6120.6924
December | 22173.1715 | 32.1371 | 66.4098 | 0 | 0.0003 | 4126.8032 | 8772.3779
Annual Sum or Average | 179314.8591 | 302.0233 | 769.6824 | 0 | 0.0032 | 47854.0439 | 74794.6511
Minimum of Months | 9896.4918 | 19.7352 | 57.1763 | 0 | 0.0002 | 3555.4203 | 4408.3427
Maximum of Months | 26833.799 | 36.8306 | 74.1912 | 0 | 0.0003 | 4614.3379 | 10427.7728
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 67955700000 | 58114.788 | 02-JAN-16:49 | 28855.207 | 9104.397 | 12806.183 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 59845300000 | 50917.907 | 08-FEB-09:09 | 28855.207 | 9104.397 | 12958.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 64434700000 | 52702.434 | 09-MAR-15:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 1936.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 56376200000 | 52886.579 | 04-APR-15:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 2120.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 58194300000 | 61974.789 | 15-MAY-15:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 11209.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 65963600000 | 88864.561 | 30-JUN-15:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 38098.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 67786000000 | 94863.387 | 25-JUL-12:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 44097.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 73166800000 | 92431.133 | 17-AUG-14:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 41665.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 58590000000 | 76172.286 | 08-SEP-14:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 25406.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59819900000 | 59213.007 | 03-OCT-14:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 8447.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 61224300000 | 58114.788 | 06-NOV-16:00 | 28855.207 | 9104.397 | 12806.183 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 65436300000 | 58114.788 | 01-DEC-16:40 | 28855.207 | 9104.397 | 12806.183 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 758793000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 56376200000 | 50917.907 |  | 28855.207 | 9104.397 | 12806.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73166800000 | 94863.387 |  | 28855.207 | 9104.397 | 12958.302 | 0 | 44097.599 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 17352.76 | 9580.86 | 0 | 26933.62
Cost per Total Building Area ($/m2) | 3.59 | 1.98 | 0 | 5.57
Cost per Net Conditioned Building Area ($/m2) | 3.59 | 1.98 | 0 | 5.57

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1461.64 | 302.3 | 302.3
Net Site Energy | 1461.64 | 302.3 | 302.3
Total Source Energy | 3265.44 | 675.36 | 675.36
Net Source Energy | 3265.44 | 675.36 | 675.36
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 711.71 | 0 | 0 | 0 | 0
Cooling | 30.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.48 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 180.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 749.93 | 711.71 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.506 | 0.56 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.506 | 0.56 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.306 | 1.624 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 24954.34 | 19929.91 | 5024.42 | 0.8 | 3.6
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 124172.08 | 89266.9 | 34905.18 | 0.72 | 3.49
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 69319.65 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30012.9 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 151222 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 1.7 | 157.58 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.51 | 1717.33 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.87 | 11019.43 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 26417.9276 | 38.838 | 80.5333 | 0 | 0.0003 | 83694.7988 | 10600.7257
February | 21338.5534 | 32.3612 | 70.4106 | 0 | 0.0003 | 73184.1359 | 8659.6885
March | 21801.2258 | 34.2358 | 78.2857 | 0 | 0.0003 | 81379.7149 | 8962.5022
April | 16370.3035 | 27.4557 | 68.2471 | 0 | 0.0003 | 70958.479 | 6901.3449
May | 16007.853 | 27.9135 | 72.5044 | 0 | 0.0003 | 75392.2767 | 6853.0814
June | 16944.4691 | 29.7215 | 77.6925 | 0 | 0.0003 | 80788.1969 | 7271.1967
July | 17811.9381 | 31.2515 | 81.7154 | 0 | 0.0003 | 84971.4105 | 7644.2674
August | 17999.6355 | 31.5786 | 82.5644 | 0 | 0.0003 | 85854.2328 | 7724.6015
September | 15403.0366 | 27.0088 | 70.5765 | 0 | 0.0003 | 73388.5951 | 6608.8623
October | 17056.0322 | 28.7874 | 72.0892 | 0 | 0.0003 | 74954.4837 | 7208.253
November | 21443.4302 | 33.3606 | 75.3048 | 0 | 0.0003 | 78278.4407 | 8784.6737
December | 26766.3671 | 39.0423 | 79.9285 | 0 | 0.0003 | 83063.3009 | 10710.3331
Annual Sum or Average | 235360.7721 | 381.5551 | 909.8526 | 0 | 0.0036 | 945908.066 | 97929.5305
Minimum of Months | 15403.0366 | 27.0088 | 68.2471 | 0 | 0.0003 | 70958.479 | 6608.8623
Maximum of Months | 26766.3671 | 39.0423 | 82.5644 | 0 | 0.0003 | 85854.2328 | 10710.3331
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 66354200000 | 50770.767 | 02-JAN-09:09 | 28855.207 | 9104.397 | 12811.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 58021300000 | 50966.575 | 14-FEB-15:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 195.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 64518800000 | 51199.413 | 02-MAR-14:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 428.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 56256700000 | 56016.8 | 21-APR-15:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 5246.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 59771900000 | 67694.694 | 31-MAY-15:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 16923.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 64049900000 | 78800.761 | 29-JUN-14:39 | 28855.207 | 9104.397 | 12811.163 | 0 | 28029.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 67366400000 | 81030.831 | 31-JUL-14:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 30260.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 68066300000 | 81336.063 | 01-AUG-14:09 | 28855.207 | 9104.397 | 12811.163 | 0 | 30565.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 58183400000 | 64791.996 | 01-SEP-14:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 14021.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 59424800000 | 53118.196 | 13-OCT-14:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 2347.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 62060100000 | 58119.767 | 13-NOV-16:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 65853600000 | 58119.767 | 01-DEC-16:00 | 28855.207 | 9104.397 | 12811.163 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 749927000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 56256700000 | 50770.767 |  | 28855.207 | 9104.397 | 12811.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 68066300000 | 81336.063 |  | 28855.207 | 9104.397 | 12811.163 | 0 | 30565.295 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 7885.13 | 4869.99 | 0 | 12755.13
Cost per Total Building Area ($/m2) | 1.63 | 1.01 | 0 | 2.64
Cost per Net Conditioned Building Area ($/m2) | 1.63 | 1.01 | 0 | 2.64

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1407.41 | 291.08 | 291.08
Net Site Energy | 1407.41 | 291.08 | 291.08
Total Source Energy | 1975.34 | 408.54 | 408.54
Net Source Energy | 1975.34 | 408.54 | 408.54
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 732.87 | 0 | 0 | 0 | 0
Cooling | 1.76 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 134.29 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 674.54 | 732.87 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.483 | 0.532 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.483 | 0.532 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.227 | 1.503 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 5.835 | 0.54 | 0.384 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 19007.7 | 15180.6 | 3827.1 | 0.8 | 3.61
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 90840.57 | 65202.42 | 25638.14 | 0.72 | 3.5
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 43155 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27555.17 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 132962.3 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.8 | 74.41 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.15 | 1308.09 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.28 | 8164.45 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 10973.7839 | 12.0512 | 13.3907 | 0 | 0.0001 | 176461.6803 | 4021.8905
February | 7840.6624 | 8.9351 | 11.6402 | 0 | 0.0001 | 153508.6321 | 2908.3687
March | 8230.3039 | 9.5188 | 13.1104 | 0 | 0.0001 | 172938.9299 | 3067.8591
April | 5629.7153 | 6.9052 | 11.4844 | 0 | 0.0001 | 151597.6941 | 2140.6992
May | 3633.806 | 5.1232 | 11.6659 | 0 | 0 | 154135.1397 | 1453.0966
June | 2821.9887 | 4.329 | 11.2964 | 0 | 0 | 149300.4533 | 1165.9844
July | 2521.4127 | 4.0074 | 10.9842 | 0 | 0 | 145189.4432 | 1056.7389
August | 2755.1043 | 4.3901 | 12.0742 | 0 | 0 | 159598.8264 | 1155.8882
September | 2955.3933 | 4.4683 | 11.413 | 0 | 0 | 150835.4084 | 1214.1037
October | 4455.5729 | 5.946 | 12.1599 | 0 | 0.0001 | 160616.9646 | 1745.7405
November | 8003.7106 | 9.2425 | 12.6587 | 0 | 0.0001 | 166976.1534 | 2981.8732
December | 10779.3722 | 11.836 | 13.1428 | 0 | 0.0001 | 173194.2554 | 3950.4596
Annual Sum or Average | 70600.8263 | 86.7528 | 145.0208 | 0 | 0.0006 | 1914350 | 26862.7026
Minimum of Months | 2521.4127 | 4.0074 | 10.9842 | 0 | 0 | 145189.4432 | 1056.7389
Maximum of Months | 10973.7839 | 12.0512 | 13.3907 | 0 | 0.0001 | 176461.6803 | 4021.8905
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 62178200000 | 54855.546 | 02-JAN-16:30 | 28855.207 | 9104.397 | 9546.942 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 54090400000 | 47506.546 | 01-FEB-09:09 | 28855.207 | 9104.397 | 9546.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 60936900000 | 47955.141 | 29-MAR-15:30 | 28855.207 | 9104.397 | 9546.942 | 0 | 448.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 53417100000 | 47506.546 | 03-APR-08:09 | 28855.207 | 9104.397 | 9546.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 54311200000 | 49025.87 | 04-MAY-14:00 | 28855.207 | 9104.397 | 9546.942 | 0 | 1519.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 52607600000 | 52219.629 | 28-JUN-14:00 | 28855.207 | 9104.397 | 9546.942 | 0 | 4713.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 51159100000 | 61444.761 | 24-JUL-14:00 | 28855.207 | 9104.397 | 9546.942 | 0 | 13938.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 56236400000 | 56484.221 | 07-AUG-15:39 | 28855.207 | 9104.397 | 9546.942 | 0 | 8977.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 53148500000 | 55347.008 | 01-SEP-15:00 | 28855.207 | 9104.397 | 9546.942 | 0 | 7840.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 56595100000 | 48414.426 | 17-OCT-14:00 | 28855.207 | 9104.397 | 9546.942 | 0 | 907.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 58835900000 | 54855.546 | 06-NOV-16:49 | 28855.207 | 9104.397 | 9546.942 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 61026900000 | 54855.546 | 01-DEC-16:19 | 28855.207 | 9104.397 | 9546.942 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 674543000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 51159100000 | 47506.546 |  | 28855.207 | 9104.397 | 9546.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 62178200000 | 61444.761 |  | 28855.207 | 9104.397 | 9546.942 | 0 | 13938.215 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 13579.05 | 6197.56 | 0 | 19776.61
Cost per Total Building Area ($/m2) | 2.81 | 1.28 | 0 | 4.09
Cost per Net Conditioned Building Area ($/m2) | 2.81 | 1.28 | 0 | 4.09

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2303.29 | 476.37 | 476.37
Net Site Energy | 2303.29 | 476.37 | 476.37
Total Source Energy | 4504.87 | 931.7 | 931.7
Net Source Energy | 4504.87 | 931.7 | 931.7
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1492.5 | 0 | 0 | 0 | 0
Cooling | 23.71 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.45 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 248.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 810.79 | 1492.5 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.4 | 0.433 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.4 | 0.433 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.067 | 1.269 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39276.66 | 27757.93 | 11518.74 | 0.71 | 3.34
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 203674.07 | 137700.62 | 65973.45 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 232871.02 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42491.99 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 251838.7 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 5.23 | 485.97 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.78 | 1946.04 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.2 | 15386.78 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47983.8116 | 67.1486 | 141.636 | 0 | 0.0005 | 32579.9769 | 18863.063
February | 36999.7488 | 54.0893 | 123.0726 | 0 | 0.0004 | 28315.4806 | 14766.1197
March | 34669.1685 | 53.9632 | 134.9888 | 0 | 0.0004 | 31064.0663 | 14149.7094
April | 24670.5499 | 41.6848 | 115.7483 | 0 | 0.0004 | 26642.365 | 10382.9645
May | 22204.7104 | 39.8212 | 117.9841 | 0 | 0.0004 | 27160.4738 | 9565.3556
June | 22881.7762 | 41.6464 | 125.2442 | 0 | 0.0004 | 28832.6034 | 9915.4368
July | 23659.6665 | 43.0794 | 129.6049 | 0 | 0.0004 | 29836.5169 | 10254.1642
August | 23870.3631 | 43.4595 | 130.7378 | 0 | 0.0004 | 30097.3046 | 10345.1405
September | 21069.6772 | 38.2841 | 114.941 | 0 | 0.0003 | 26460.6119 | 9124.0598
October | 24211.9351 | 42.1107 | 120.7953 | 0 | 0.0004 | 27805.8881 | 10304.7635
November | 30072.9333 | 48.2625 | 125.8054 | 0 | 0.0004 | 28953.3996 | 12412.7822
December | 42511.9938 | 61.5192 | 137.6408 | 0 | 0.0005 | 31665.8628 | 16905.9011
Annual Sum or Average | 354806.3344 | 575.069 | 1518.1991 | 0 | 0.0047 | 349414.5499 | 146989.4601
Minimum of Months | 21069.6772 | 38.2841 | 114.941 | 0 | 0.0003 | 26460.6119 | 9124.0598
Maximum of Months | 47983.8116 | 67.1486 | 141.636 | 0 | 0.0005 | 32579.9769 | 18863.063
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 75599400000 | 63127.408 | 06-JAN-16:30 | 28855.207 | 9104.397 | 17818.804 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 65703900000 | 62715.84 | 01-FEB-16:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 72081800000 | 55914.812 | 31-MAR-14:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 547.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 61821600000 | 56316.03 | 07-APR-14:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 949.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63023800000 | 68772.712 | 30-MAY-15:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 13405.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 66903900000 | 91934.548 | 08-JUN-12:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 36567.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 69233400000 | 94716.752 | 13-JUL-14:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 39349.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 69838500000 | 90362.86 | 04-AUG-15:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 34996.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 61399900000 | 74990.276 | 05-SEP-13:00 | 28855.207 | 9104.397 | 17407.235 | 0 | 19623.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 64521500000 | 57610.733 | 31-OCT-13:30 | 28855.207 | 9104.397 | 17407.235 | 0 | 2243.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 67184200000 | 62715.84 | 06-NOV-16:40 | 28855.207 | 9104.397 | 17407.235 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73478200000 | 62715.84 | 01-DEC-16:19 | 28855.207 | 9104.397 | 17407.235 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 810790000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61399900000 | 55914.812 |  | 28855.207 | 9104.397 | 17407.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 75599400000 | 94716.752 |  | 28855.207 | 9104.397 | 17818.804 | 0 | 39349.912 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 12043.73 | 12315.8 | 0 | 24359.53
Cost per Total Building Area ($/m2) | 2.49 | 2.55 | 0 | 5.04
Cost per Net Conditioned Building Area ($/m2) | 2.49 | 2.55 | 0 | 5.04

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1955.1 | 404.35 | 404.35
Net Site Energy | 1955.1 | 404.35 | 404.35
Total Source Energy | 3924.28 | 811.62 | 811.62
Net Source Energy | 3924.28 | 811.62 | 811.62
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1151.28 | 0 | 0 | 0 | 0
Cooling | 16.65 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 248.55 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 803.82 | 1151.28 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.422 | 0.459 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.422 | 0.459 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 1.108 | 1.329 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30615.95 | 24451.59 | 6164.36 | 0.8 | 3.56
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 189885.63 | 131770.48 | 58115.15 | 0.69 | 3.38
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 172147.06 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 36898.37 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 210796.41 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 4.58 | 424.89 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.85 | 2022.67 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.2 | 15390.69 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 33389.2762 | 46.8256 | 89.5455 | 0 | 0.0004 | 93039.2837 | 13176.3064
February | 26815.2572 | 38.8083 | 78.4218 | 0 | 0.0003 | 81494.5498 | 10699.9448
March | 26408.7485 | 40.0543 | 87.1611 | 0 | 0.0004 | 90594.458 | 10717.6631
April | 19499.3303 | 31.5703 | 75.1578 | 0 | 0.0003 | 78135.7947 | 8109.3036
May | 17996.5273 | 30.5325 | 76.9178 | 0 | 0.0003 | 79976.0666 | 7621.1942
June | 16916.801 | 29.5132 | 76.7005 | 0 | 0.0003 | 79755.6833 | 7243.6456
July | 17480.5019 | 30.6676 | 80.182 | 0 | 0.0003 | 83376.8523 | 7501.7923
August | 18593.2612 | 32.612 | 85.2436 | 0 | 0.0003 | 88640.0852 | 7978.5639
September | 16771.9885 | 29.0742 | 75.0356 | 0 | 0.0003 | 78023.2126 | 7163.3633
October | 19736.7353 | 32.506 | 79.0573 | 0 | 0.0003 | 82193.9913 | 8262.1217
November | 25231.858 | 38.2609 | 83.2316 | 0 | 0.0003 | 86510.0568 | 10239.2165
December | 33672.1068 | 46.9242 | 88.6909 | 0 | 0.0004 | 92148.0605 | 13258.6839
Annual Sum or Average | 272512.3923 | 427.3489 | 975.3455 | 0 | 0.0039 | 1013890 | 111971.7993
Minimum of Months | 16771.9885 | 29.0742 | 75.0356 | 0 | 0.0003 | 78023.2126 | 7163.3633
Maximum of Months | 33672.1068 | 46.9242 | 89.5455 | 0 | 0.0004 | 93039.2837 | 13258.6839
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 73762700000 | 63146.861 | 05-JAN-16:49 | 28855.207 | 9104.397 | 17838.256 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 64609900000 | 55797.861 | 14-FEB-09:09 | 28855.207 | 9104.397 | 17838.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 71824400000 | 56244.487 | 30-MAR-15:00 | 28855.207 | 9104.397 | 17487.771 | 0 | 797.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 61947000000 | 57134.735 | 25-APR-14:00 | 28855.207 | 9104.397 | 17487.771 | 0 | 1687.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 63406000000 | 67446.119 | 23-MAY-15:00 | 28855.207 | 9104.397 | 17487.771 | 0 | 11998.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63231300000 | 78632.545 | 28-JUN-13:00 | 28855.207 | 9104.397 | 17487.771 | 0 | 23185.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 66102200000 | 85167.586 | 17-JUL-15:50 | 28855.207 | 9104.397 | 17487.771 | 0 | 29720.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 70274900000 | 85792.064 | 30-AUG-13:00 | 28855.207 | 9104.397 | 17487.771 | 0 | 30344.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 61857700000 | 71863.418 | 06-SEP-15:00 | 28855.207 | 9104.397 | 17487.771 | 0 | 16416.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 65164400000 | 61401.7 | 05-OCT-15:00 | 28855.207 | 9104.397 | 17487.771 | 0 | 5954.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 68586200000 | 62796.375 | 06-NOV-16:49 | 28855.207 | 9104.397 | 17487.771 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 73056100000 | 63146.861 | 01-DEC-16:40 | 28855.207 | 9104.397 | 17838.256 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 803823000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61857700000 | 55797.861 |  | 28855.207 | 9104.397 | 17487.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 73762700000 | 85792.064 |  | 28855.207 | 9104.397 | 17838.256 | 0 | 30344.689 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 8437.98 | 7902.05 | 0 | 16340.03
Cost per Total Building Area ($/m2) | 1.75 | 1.63 | 0 | 3.38
Cost per Net Conditioned Building Area ($/m2) | 1.75 | 1.63 | 0 | 3.38

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3186.85 | 659.1 | 659.1
Net Site Energy | 3186.85 | 659.1 | 659.1
Total Source Energy | 5419.82 | 1120.92 | 1120.92
Net Source Energy | 5419.82 | 1120.92 | 1120.92
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2359.65 | 0 | 0 | 0 | 0
Cooling | 16.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 271.92 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 827.2 | 2359.65 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.335 | 0.357 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.335 | 0.357 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42793.45 | 30536.72 | 12256.73 | 0.71 | 3.17
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 234747.02 | 158708.52 | 76038.5 | 0.68 | 3.1
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 297631.02 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 47116.17 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 287985.86 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 6.8 | 631.83 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.99 | 2173.01 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1017.59 | 9.45 | 16263 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 56243.2172 | 67.2302 | 52.9373 | 0 | 0.0005 | 34667.5117 | 21012.2689
February | 40315.9082 | 50.5648 | 45.6739 | 0 | 0.0004 | 29938.7031 | 15288.7352
March | 28277.2369 | 40.4542 | 48.2784 | 0 | 0.0004 | 31694.4846 | 11200.2164
April | 17361.6103 | 28.3189 | 40.9763 | 0 | 0.0003 | 26923.1683 | 7209.418
May | 14741.6801 | 26.3376 | 42.2563 | 0 | 0.0003 | 27774.9047 | 6340.5859
June | 14584.9337 | 26.5954 | 43.5584 | 0 | 0.0003 | 28632.8708 | 6324.5823
July | 14304.4388 | 26.098 | 42.7665 | 0 | 0.0003 | 28112.3332 | 6204.292
August | 15386.29 | 28.0737 | 46.0071 | 0 | 0.0003 | 30242.5524 | 6673.7069
September | 13688.2872 | 24.7563 | 40.2162 | 0 | 0.0003 | 26435.0844 | 5916.2577
October | 18067.6816 | 29.7203 | 43.4559 | 0 | 0.0003 | 28553.5568 | 7526.486
November | 26302.8663 | 37.9356 | 45.9041 | 0 | 0.0004 | 30137.7585 | 10447.4519
December | 44985.2554 | 56.4052 | 50.9118 | 0 | 0.0004 | 33371.9473 | 17057.935
Annual Sum or Average | 304259.4058 | 442.4902 | 542.9423 | 0 | 0.0042 | 356484.8757 | 121201.9361
Minimum of Months | 13688.2872 | 24.7563 | 40.2162 | 0 | 0.0003 | 26435.0844 | 5916.2577
Maximum of Months | 56243.2172 | 67.2302 | 52.9373 | 0 | 0.0005 | 34667.5117 | 21012.2689
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 80443300000 | 64376.44 | 02-JAN-16:40 | 28855.207 | 9104.397 | 19067.835 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 69470500000 | 57027.44 | 01-FEB-09:09 | 28855.207 | 9104.397 | 19067.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 73544700000 | 57027.44 | 06-MAR-09:09 | 28855.207 | 9104.397 | 19067.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 62473200000 | 56470.021 | 03-APR-08:09 | 28855.207 | 9104.397 | 18510.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 64449600000 | 69479.782 | 31-MAY-12:09 | 28855.207 | 9104.397 | 18510.416 | 0 | 13009.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 66440400000 | 91944.526 | 29-JUN-14:00 | 28855.207 | 9104.397 | 18510.416 | 0 | 35474.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 65232600000 | 89431.595 | 13-JUL-14:00 | 28855.207 | 9104.397 | 18510.416 | 0 | 32961.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 70175600000 | 87429.434 | 25-AUG-15:00 | 28855.207 | 9104.397 | 18510.416 | 0 | 30959.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 61340600000 | 70442.662 | 14-SEP-14:00 | 28855.207 | 9104.397 | 18510.416 | 0 | 13972.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 66256400000 | 57475.084 | 06-OCT-14:00 | 28855.207 | 9104.397 | 18510.416 | 0 | 1005.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 69932400000 | 64376.44 | 27-NOV-16:40 | 28855.207 | 9104.397 | 19067.835 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 77437100000 | 64376.44 | 05-DEC-16:30 | 28855.207 | 9104.397 | 19067.835 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 827196000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 61340600000 | 56470.021 |  | 28855.207 | 9104.397 | 18510.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 80443300000 | 91944.526 |  | 28855.207 | 9104.397 | 19067.835 | 0 | 35474.506 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 15097.2 | 18699.87 | 0 | 33797.07
Cost per Total Building Area ($/m2) | 3.12 | 3.87 | 0 | 6.99
Cost per Net Conditioned Building Area ($/m2) | 3.12 | 3.87 | 0 | 6.99

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2602.69 | 538.29 | 538.29
Net Site Energy | 2602.69 | 538.29 | 538.29
Total Source Energy | 4814.89 | 995.81 | 995.81
Net Source Energy | 4814.89 | 995.81 | 995.81
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1775.2 | 0 | 0 | 0 | 0
Cooling | 6.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 282.43 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 827.5 | 1775.2 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.335 | 0.357 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.335 | 0.357 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.977 | 1.145 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35369.02 | 28247.66 | 7121.37 | 0.8 | 3.56
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 196527.99 | 146230.48 | 50297.51 | 0.74 | 3.48
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 282340.69 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 45157.98 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 274643.18 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 7.24 | 672.38 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.14 | 2336.69 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1017.59 | 10.11 | 17392.1 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 43181.2196 | 55.4203 | 58.8723 | 0 | 0.0005 | 1393660 | 16513.4047
February | 34257.662 | 45.291 | 51.4926 | 0 | 0.0004 | 1219390 | 13228.785
March | 26915.4844 | 39.6225 | 55.0614 | 0 | 0.0004 | 1305090 | 10783.928
April | 19904.5515 | 31.2721 | 47.845 | 0 | 0.0003 | 1134470 | 8165.4025
May | 17122.9243 | 28.8941 | 48.3635 | 0 | 0.0003 | 1147130 | 7216.8743
June | 15832.891 | 27.7134 | 48.3226 | 0 | 0.0003 | 1146320 | 6769.4548
July | 15031.1344 | 26.6676 | 47.1687 | 0 | 0.0003 | 1119000 | 6461.2204
August | 16093.8059 | 28.5226 | 50.3939 | 0 | 0.0003 | 1195500 | 6915.0872
September | 15534.6755 | 26.9444 | 46.5193 | 0 | 0.0003 | 1103500 | 6618.0772
October | 19669.0674 | 31.7602 | 50.3824 | 0 | 0.0004 | 1194790 | 8151.7488
November | 25722.8564 | 37.9386 | 52.8813 | 0 | 0.0004 | 1253430 | 10313.0298
December | 38593.2473 | 50.7234 | 56.9262 | 0 | 0.0004 | 1347980 | 14874.0414
Annual Sum or Average | 287859.5196 | 430.7703 | 614.2293 | 0 | 0.0044 | 14560300 | 116011.054
Minimum of Months | 15031.1344 | 26.6676 | 46.5193 | 0 | 0.0003 | 1103500 | 6461.2204
Maximum of Months | 43181.2196 | 55.4203 | 58.8723 | 0 | 0.0005 | 1393660 | 16513.4047
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 79205100000 | 65709.779 | 03-JAN-16:49 | 28855.207 | 9104.397 | 20401.175 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 69301000000 | 58360.779 | 06-FEB-09:09 | 28855.207 | 9104.397 | 20401.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 74171600000 | 58360.779 | 02-MAR-09:09 | 28855.207 | 9104.397 | 20401.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 64474800000 | 57762.804 | 03-APR-08:09 | 28855.207 | 9104.397 | 19803.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 65194300000 | 59324.768 | 16-MAY-15:00 | 28855.207 | 9104.397 | 19803.199 | 0 | 1561.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 65148000000 | 82219.681 | 30-JUN-14:00 | 28855.207 | 9104.397 | 19803.199 | 0 | 24456.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 63595300000 | 81515.318 | 21-JUL-15:00 | 28855.207 | 9104.397 | 19803.199 | 0 | 23752.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67943400000 | 76412.016 | 09-AUG-15:00 | 28855.207 | 9104.397 | 19803.199 | 0 | 18649.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 62714700000 | 63517.1 | 01-SEP-15:00 | 28855.207 | 9104.397 | 19803.199 | 0 | 5754.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 67903000000 | 58938.792 | 06-OCT-15:00 | 28855.207 | 9104.397 | 19803.199 | 0 | 1175.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 71235600000 | 65111.804 | 08-NOV-16:00 | 28855.207 | 9104.397 | 19803.199 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 76608800000 | 65709.779 | 08-DEC-16:40 | 28855.207 | 9104.397 | 20401.175 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 827496000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 62714700000 | 57762.804 |  | 28855.207 | 9104.397 | 19803.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 79205100000 | 82219.681 |  | 28855.207 | 9104.397 | 20401.175 | 0 | 24456.878 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18320.37 | 14155.13 | 0 | 32475.5
Cost per Total Building Area ($/m2) | 3.79 | 2.93 | 0 | 6.72
Cost per Net Conditioned Building Area ($/m2) | 3.79 | 2.93 | 0 | 6.72

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3920.32 | 810.8 | 810.8
Net Site Energy | 3920.32 | 810.8 | 810.8
Total Source Energy | 6272.99 | 1297.38 | 1297.38
Net Source Energy | 6272.99 | 1297.38 | 1297.38
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3070.85 | 0 | 0 | 0 | 0
Cooling | 3.79 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 115.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 307.15 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 849.47 | 3070.85 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.341 | 0.365 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.341 | 0.365 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.906 | 1.048 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 44263.3 | 31920.52 | 12342.79 | 0.72 | 3.19
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 255427.52 | 172690.26 | 82737.26 | 0.68 | 3.1
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 331105.88 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 48998.01 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 306540.68 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 7.77 | 721.34 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.11 | 2307.83 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1017.59 | 10.29 | 17695.72 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 57922.2716 | 69.2866 | 54.6783 | 0 | 0.0005 | 35808.2571 | 21644.2744
February | 48083.776 | 58.3611 | 48.1368 | 0 | 0.0004 | 31534.1583 | 18048.4563
March | 37977.4412 | 50.291 | 51.6834 | 0 | 0.0004 | 33903.7159 | 14656.1155
April | 22097.0926 | 33.3868 | 43.5036 | 0 | 0.0003 | 28571.322 | 8921.9271
May | 17278.3334 | 28.9546 | 43.2919 | 0 | 0.0003 | 28448.2522 | 7248.5842
June | 14201.9421 | 25.6561 | 41.6303 | 0 | 0.0003 | 27364.5128 | 6135.4775
July | 13925.2199 | 25.3511 | 41.4537 | 0 | 0.0003 | 27249.1613 | 6034.5566
August | 15151.7669 | 27.4015 | 44.5105 | 0 | 0.0003 | 29257.8606 | 6548.6358
September | 15309.7674 | 26.6237 | 41.5115 | 0 | 0.0003 | 27282.5306 | 6515.2602
October | 20344.7559 | 32.3322 | 45.241 | 0 | 0.0003 | 29721.3074 | 8366.6805
November | 32555.9819 | 44.4617 | 48.701 | 0 | 0.0004 | 31958.24 | 12692.9228
December | 51346.5251 | 62.9325 | 53.3934 | 0 | 0.0005 | 34984.4673 | 19331.5688
Annual Sum or Average | 346194.8739 | 485.039 | 557.7354 | 0 | 0.0044 | 366083.7855 | 136144.4599
Minimum of Months | 13925.2199 | 25.3511 | 41.4537 | 0 | 0.0003 | 27249.1613 | 6034.5566
Maximum of Months | 57922.2716 | 69.2866 | 54.6783 | 0 | 0.0005 | 35808.2571 | 21644.2744
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 83090400000 | 66033.503 | 02-JAN-16:30 | 28855.207 | 9104.397 | 20724.899 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 73172600000 | 58684.503 | 01-FEB-09:09 | 28855.207 | 9104.397 | 20724.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 78671000000 | 58684.503 | 01-MAR-09:09 | 28855.207 | 9104.397 | 20724.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 66297600000 | 58684.503 | 03-APR-08:09 | 28855.207 | 9104.397 | 20724.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 66012000000 | 59508.699 | 31-MAY-15:00 | 28855.207 | 9104.397 | 20077.961 | 0 | 1471.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 63497300000 | 69959.668 | 14-JUN-15:00 | 28855.207 | 9104.397 | 20077.961 | 0 | 11922.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 63229600000 | 84198.674 | 06-JUL-15:00 | 28855.207 | 9104.397 | 20077.961 | 0 | 26161.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 67890700000 | 75792.969 | 11-AUG-15:30 | 28855.207 | 9104.397 | 20077.961 | 0 | 17755.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 63307100000 | 60654.171 | 07-SEP-14:00 | 28855.207 | 9104.397 | 20077.961 | 0 | 2616.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 68966100000 | 58037.565 | 02-OCT-08:09 | 28855.207 | 9104.397 | 20077.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 74156700000 | 66033.503 | 21-NOV-16:30 | 28855.207 | 9104.397 | 20724.899 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 81178800000 | 66033.503 | 04-DEC-16:19 | 28855.207 | 9104.397 | 20724.899 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 849470000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 63229600000 | 58037.565 |  | 28855.207 | 9104.397 | 20077.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 83090400000 | 84198.674 |  | 28855.207 | 9104.397 | 20724.899 | 0 | 26161.109 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 14853 | 24228.78 | 0 | 39081.78
Cost per Total Building Area ($/m2) | 3.07 | 5.01 | 0 | 8.08
Cost per Net Conditioned Building Area ($/m2) | 3.07 | 5.01 | 0 | 8.08

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 7403.03 | 1531.09 | 1531.09
Net Site Energy | 7403.03 | 1531.09 | 1531.09
Total Source Energy | 10483.39 | 2168.17 | 2168.17
Net Source Energy | 10483.39 | 2168.17 | 2168.17
Area [m2]
Total Building Area | 4835.13
Net Conditioned Building Area | 4835.13
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6435.57 | 0 | 0 | 0 | 0
Cooling | 0.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 318.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 114.58 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 104.42 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 429.34 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 967.45 | 6435.57 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BULKSTORAGE | 3204.84 | Yes | 31313.82 | 1 | 1586.63 | 0 | 3.34 |  | 2.56
FINESTORAGE | 1393.41 | Yes | 11554.41 | 1 | 1150.96 | 0 | 11.64 |  | 0
OFFICE | 236.88 | Yes | 1010.76 | 1 | 299.12 | 17.66 | 21.69 | 47.38 | 8.07
Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Conditioned Total | 4835.13 |  | 43879 |  | 3036.71 | 17.66 | 6.6309 | 967.03 | 2.0922
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BULKSTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 598.24 | 90 | 90 | E
BULKSTORAGE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 390.16 | 0 | 90 | N
BULKSTORAGE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 598.24 | 270 | 90 | W
BULKSTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 3204.84 | 0 | 180
BULKSTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.335 | 0.357 | 3204.84 | 180 | 0
FINE STORAGE OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 110.54 | 180 | 90 | S
FINE STORAGE OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 39.02 | 270 | 90 | W
FINESTORAGE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 260.1 | 90 | 90 | E
FINESTORAGE_WALL_NORTH | INT-WALLS | 0.08 | 3.242 | 6.299 | 390.16 | 0 | 90 | N
FINESTORAGE_WALL_SOUTH_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 169.07 | 180 | 90 | S
FINESTORAGE_WALL_WEST_1 | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 182.07 | 270 | 90 | W
FINESTORAGE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 1156.53 | 0 | 180
FINESTORAGE_CEILING | ROOF-IEAD-SEMI | 0.3 | 0.335 | 0.357 | 1393.41 | 0 | 0
OFFICE_WALL_EAST | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 39.02 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 110.54 | 0 | 90 | N
OFFICE_WALL_SOUTH | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 110.54 | 180 | 90 | S
OFFICE_WALL_WEST | EXT-WALLS-METAL-SEMI | 0.8 | 0.821 | 0.937 | 39.02 | 270 | 90 | W
OFFICE_FLOOR | EXT-SLAB | 0.3 | 2.512 | 6.452 | 236.88 | 0 | 180
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
OFFICE_WALL_SOUTH WINDOW 1 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_SOUTH WINDOW2 | WINDOW-SEMI-OPER | 5.58 | 5.58 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_SOUTH | 180 | S
OFFICE_WALL_WEST WINDOW1 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
OFFICE_WALL_WEST WINDOW2 | WINDOW-SEMI-OPER | 3.25 | 3.25 | 3.525 | 0.407 | 0.316 | No | OFFICE_WALL_WEST | 270 | W
Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 17.66 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 43975.17 | 35121 | 8854.17 | 0.8 | 3.35
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 229345.61 | 183168.08 | 46177.53 | 0.8 | 3.53
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BULKSTORAGE UNIT HEATER COIL | Coil:Heating:Gas | 549716.01 | 0.78
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 63923.53 | 0.78
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 426862.63 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BULKSTORAGE UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 12.65 | 1175.05 | 1 | Unit Heater Fans
FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.66 | 2905.26 | 1 | Unitary Fans
FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.6 | 1017.59 | 13.85 | 23474.03 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 95392.5608 | 93.3543 | 141.7143 | 0 | 0.0006 | 28364.8077 | 34055.8026
February | 79493.1067 | 78.0726 | 123.9111 | 0 | 0.0006 | 24805.4425 | 28422.3737
March | 59609.1786 | 60.3199 | 130.0715 | 0 | 0.0005 | 26063.3063 | 21586.2662
April | 30864.3447 | 33.0689 | 105.771 | 0 | 0.0004 | 21212.2516 | 11459.5237
May | 16311.8275 | 19.5041 | 98.3107 | 0 | 0.0003 | 19728.884 | 6368.3204
June | 13402.0388 | 16.6089 | 92.9923 | 0 | 0.0003 | 18663.6811 | 5322.182
July | 12578.9027 | 15.7099 | 89.8151 | 0 | 0.0003 | 18026.3893 | 5013.9413
August | 14866.7534 | 18.3634 | 101.8856 | 0 | 0.0003 | 20448.3819 | 5894.5047
September | 18180.1565 | 21.2698 | 99.7747 | 0 | 0.0003 | 20020.9889 | 7025.6791
October | 34768.8357 | 37.1072 | 116.1157 | 0 | 0.0004 | 23285.9501 | 12886.8791
November | 66491.6435 | 66.591 | 130.5814 | 0 | 0.0005 | 26158.6074 | 23971.897
December | 82761.5185 | 81.7489 | 138.7617 | 0 | 0.0006 | 27784.8138 | 29662.7387
Annual Sum or Average | 524720.8674 | 541.7191 | 1369.705 | 0 | 0.0053 | 274563.5046 | 191670.1084
Minimum of Months | 12578.9027 | 15.7099 | 89.8151 | 0 | 0.0003 | 18026.3893 | 5013.9413
Maximum of Months | 95392.5608 | 93.3543 | 141.7143 | 0 | 0.0006 | 28364.8077 | 34055.8026
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 99946500000 | 72862.945 | 02-JAN-09:09 | 28855.207 | 9104.397 | 27554.34 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 87404700000 | 72862.945 | 01-FEB-09:09 | 28855.207 | 9104.397 | 27554.34 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 91836900000 | 65513.945 | 01-MAR-09:09 | 28855.207 | 9104.397 | 27554.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 74743700000 | 65513.945 | 03-APR-08:09 | 28855.207 | 9104.397 | 27554.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 69516900000 | 64413.301 | 01-MAY-08:09 | 28855.207 | 9104.397 | 26453.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 65763500000 | 69942.379 | 20-JUN-15:00 | 28855.207 | 9104.397 | 26453.697 | 0 | 5529.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 63517900000 | 70773.991 | 21-JUL-15:00 | 28855.207 | 9104.397 | 26453.697 | 0 | 6360.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 72052100000 | 68486.929 | 15-AUG-15:00 | 28855.207 | 9104.397 | 26453.697 | 0 | 4073.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 70546100000 | 64413.301 | 01-SEP-08:09 | 28855.207 | 9104.397 | 26453.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 82050600000 | 72862.945 | 23-OCT-08:09 | 28855.207 | 9104.397 | 27554.34 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 92172700000 | 72862.945 | 01-NOV-08:09 | 28855.207 | 9104.397 | 27554.34 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 97902800000 | 72862.945 | 01-DEC-09:09 | 28855.207 | 9104.397 | 27554.34 | 0 | 0 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 967454000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 63517900000 | 64413.301 |  | 28855.207 | 9104.397 | 26453.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 99946500000 | 72862.945 |  | 28855.207 | 9104.397 | 27554.34 | 0 | 6360.69 | 7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27260.36 | 26421.12 | 0 | 53681.48
Cost per Total Building Area ($/m2) | 5.64 | 5.46 | 0 | 11.1
Cost per Net Conditioned Building Area ($/m2) | 5.64 | 5.46 | 0 | 11.1

## Picture
DOE Commercial Building Benchmark - Warehouse

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 3.5 | 182.5
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Sat | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.07 | 0.1 | 0.3 | 0.36 | 0.36 | 0.46 | 0.57 | 0.43 | 0.38 | 0.4 | 0.3 | 0.18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 4.29 | 22.88 | 1193.03
|  |  | Sat, WinterDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.12 | 0.12 | 0.17 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.91
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.52
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2956 | 154134.29
|  |  | SummerDesign | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
|  |  | Sun, Hol, Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
HTGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372 | 2604 | 135780
HTGSETP_BulkStorage_SCH | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 4692 | 244654.29
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
CLGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8 | 4485.6 | 233892
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58 | 3024.29
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Through 9/30 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -240 | -1680 | -87600
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600